## Order
Scenario 3
Local Supply Rates + Installation Rates
|  | UNIQUE IDENTIFIERS | [8 empty] | UOM | QTY | RATE (can be entered directly or summed up for totals)
Sr. No. | Item Range Code | Description | Area | Make | Model No./ Product Code | Tag/ Item No. | ITC HS Code | Country of Origin | Port of Loading | User defined column |  |  | Local supply rate | [5 empty] | Installation Rate |  |  |  | Amount
[13 empty] | Basic Rate | Excise | Subtotal = Basic + Excise | VAT/CST on Subtotal | Others | Supply Rate Total (sum or direct entry) | Basic Rate | Service Tax | Other | Installation Rate Total (sum or direct entry) | LOCAL SUPPLY AMOUNT | INSTALLATION AMOUNT | TOTAL AMOUNT
A | 501020000 | SANITARY FIXTURES & FITTINGS: (INSTALLATION) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 501020000 | Fixing, testing and commissioning of white vitreous China wall mounting type European water closet including Providing & fixing of C.P. bolts, nuts, C.I. chair (painted with two coats of enamel paint over a coat of primer) & Fixing, testing & commissioning of hanging arrangements, bakelite / poly propylene seat & cover (fixing only) with C.P. hinges & rubber buffers, C.P. brass screw, washer with all accessories. Including cutting & making good the walls, floors, slab wherever required. (Material cost of required hinges, screws etc to be included in the item) | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1024 | 126.5664 | 0 | 1150.5664 | 0 | 0 | 0
2 | 501020000 | Fixing, testing and commissioning of white vitreous china floor mounting type European water closet including Providing & Fixing of C.P. bolts, nuts, supporting arrangements, bakelite / poly propylene seat & cover(fixing only) with C.P. hinges & rubber buffers, complete with all accessories. Including cutting & making good the walls & floors wherever required. The item also includes Fixing, testing and commissioning of exposed viterious china low level cistern for WC, with dual flush facility complete with all necessary fittings, CP / GI flush pipes & accessories including all supports & making good. (Material cost of required hinges, screws etc to be included in the item) | [8 empty] | No. | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 893 | 110.3748 | 0 | 1003.3748 | 0 | 270911.196 | 270911.196
3 | 501020000 | Fixing of white viterous china wall mounting / floor mounting type bidet with Providing & Fixing single tap hole and CP bolts, nuts and including providing & fixing hanging arrangements, 32 mm dia CP brass waste, 32 mm dia CP cast brass bottle flange and rubber adapter for waste connection complete including cutting and making good the walls, floors wherever required. | [8 empty] | No. | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 683 | 84.4188 | 0 | 767.4188 | 0 | 1534.8376 | 1534.8376
4 | 501020000 | Fixing, testing and commissioning of mixer fitting for bidet complete with connection to spray outlet including cutting and making good the walls, floor wherever required. | [8 empty] | No. | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 368 | 45.4848 | 0 | 413.4848 | 0 | 826.9696 | 826.9696
5 | 501020000 | Fixing, testing & commissioning of dual type Concealed type flush valve (suitable for shaft / wall) fittings push button arrangement, 32 mm dia C.P. flush pipe with clamp and adapter, rubber joint, C.P. brass wall flange, elbow complete with all other accessories. Including connection to water closet & cutting and making good the walls wherever required. | [8 empty] | No. | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 473 | 58.4628 | 0 | 531.4628 | 0 | 7971.942 | 7971.942
6 | 501020000 | Fixing, testing & commissioning of ABS Rinsing spray with regulator of approved quality with plastic flexible pipe 1.5 m long, wall hook complete as required. | [8 empty] | No. | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 12.978 | 0 | 117.978 | 0 | 31854.06 | 31854.06
7 | 501020000 | Fixing first quality white vitreous china oval / round / square wash basin (size as per architectural drawing) for under counter mounting, including providing & fixing of specially fabricated CI / MS brackets, painted with two or three coats of enamel paint of approved shade over a coat of primer, 32 mm CP brass waste and CP brass cast bottle trap and pipe to wall with CP brass flange and rubber adopter for waste connection complete including filling gap between counter and wash basin with approved type poly sulphide sealant, cutting and making good the walls wherever required. | [8 empty] | No. | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 630 | 77.868 | 0 | 707.868 | 0 | 212360.4 | 212360.4
8 | 501020000 | Fixing first quality white vitreous china wall mounting wash basin (size as per architectural drawing) including providing & fixing specially fabricated CI / MS brackets, painted with two or three coats of enamel paint of approved shade over a coat of primer, 32 mm CP brass waste and CP brass cast bottle trap and pipe to wall with CP brass flange and rubber adopter for waste connection complete including and wash basin with approved type poly sulphide sealant, cutting and making good the walls wherever required. | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 683 | 84.4188 | 0 | 767.4188 | 0 | 0 | 0
9 | 501020000 | Fixing, testing and commissioning of vitreous china pedestal for wash basin complete recessed at the back for the reception of pipes and fittings. | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 263 | 32.5068 | 0 | 295.5068 | 0 | 0 | 0
10 | 501020000 | Fixing, testing and commissioning of C.P. brass single hole basin mixer with pop-up waste and brass nuts complete as required. | [8 empty] | No. | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 236 | 29.1696 | 0 | 265.1696 | 0 | 79550.88 | 79550.88
11 | 501020000 | Fixing, testing and commissioning of three hole basin mixer with popup waste and brass nuts complete as required. | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 263 | 32.5068 | 0 | 295.5068 | 0 | 0 | 0
12 | 501020000 | Fixing sensor based automatic battery operated hot & cold water tap with solenoid valve at inlet, Doppler based sensor, control box complete with all flexible pipes & accessories. | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 263 | 32.5068 | 0 | 295.5068 | 0 | 0 | 0
13 | 501020000 | Fixing, testing & commissioning of C.P. brass eurometic self closing pillar tap. | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210 | 25.956 | 0 | 235.956 | 0 | 0 | 0
14 | 501020000 | Fixing, testing, and commissioning of bath tub completely leveled, including waste overflow set, chain plug, cast brass P/S trap with overflow arrangement, legs, grouting of legs etc with cement concrete all complete as required. | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14.1 | 501020000 | ( Cost of grouting material shall be included in the rate) | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14.2 | 501020000 | Apron type bath tub | [8 empty] | No. | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 1575 | 194.67 | 0 | 1769.67 | 0 | 44241.75 | 44241.75
14.3 | 501020000 | Free standing bath tub | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1575 | 194.67 | 0 | 1769.67 | 0 | 0 | 0
14.4 | 501020000 | Bath Tub Spout / Spout | [8 empty] | No. | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 473 | 58.4628 | 0 | 531.4628 | 0 | 13286.57 | 13286.57
14.5 | 501020000 | Deck mount bath tub mixer with spout and telephonic hand shower. | [8 empty] | No. | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 578 | 71.4408 | 0 | 649.4408 | 0 | 16236.02 | 16236.02
15 | 501020000 | Fixing, testing and commissioning of bathing facucets including necessary wall chases and making good. | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15.1 | 501020000 | Concealed bath shower divertor, faucet, 115 mm long bend pipe, overhead shower and wall flanges complete. | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 263 | 32.5068 | 0 | 295.5068 | 0 | 0 | 0
15.2 | 501020000 | Single lever wall divertor assembly with non-return valves | [8 empty] | No. | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 236 | 29.1696 | 0 | 265.1696 | 0 | 58337.312 | 58337.312
15.3 | 501020000 | Concealed stop valves with wall flanges | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 19.5288 | 0 | 177.5288 | 0 | 0 | 0
15.4 | 501020000 | Overhead shower with short / long arm and wall flange | [8 empty] | No. | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 19.5288 | 0 | 177.5288 | 0 | 4438.22 | 4438.22
15.5 | 501020000 | Overhead drencher shower, ceiling mounted | [8 empty] | No. | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 19.5288 | 0 | 177.5288 | 0 | 37281.048 | 37281.048
16 | 501020000 | Fixing of SS 304 SS shower channel with grating (polished surface), socket type outlet (50 mm dia), slope towards socket, effective tray depth 20 mm, width 70 mm approximate 900 following length. | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16.1 | 501020000 | 900 mm Length | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 473 | 58.4628 | 0 | 531.4628 | 0 | 0 | 0
16.2 | 501020000 | 1000 mm Length | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578 | 71.4408 | 0 | 649.4408 | 0 | 0 | 0
17 | 501020000 | Fixing, testing and commissioning of white viterous china large flat back / half stall urinal including providing & fixing CI / MS bracket (duly painted with 2 coats of paints over a coat of primer), including CP brass waste with dome type grating, CP cast brass bottle trap with extension piece, wall flanges complete with all accessories. | [8 empty] | No. | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 788 | 97.3968 | 0 | 885.3968 | 0 | 22134.92 | 22134.92
18 | 501020000 | Fixing, testing and commissioning of white vitreous china large urinal partition including providing & fixing concealed CI bracket, cutting and making good. | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 263 | 32.5068 | 0 | 295.5068 | 0 | 0 | 0
19 | 501020000 | Fixing, testing and commissioning of automatic flushing systems for urinal to ensure pre-flush & flushing only immediately after use, comprising of all plumbing, electronic and electrical items. CP brass flush pipe with CP brass elbow, CP brass spreader, CP wall flange, infrared photo cells, eyes electrically operated solenoid valve, step down transformer / equipment and any other item required to provide satisfactory functioning. Including necessary wall cutting / chasing and making good, as required. | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578 | 71.4408 | 0 | 649.4408 | 0 | 0 | 0
20 | 501020000 | Fixing battery operated automatic urinal flushing systems for urinal flushing complete as mentioned above. | [8 empty] | No. | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 394 | 48.6984 | 0 | 442.6984 | 0 | 11067.46 | 11067.46
21 | 501020000 | Fixing, testing & commissioning of white acrylic shower tray of size 780x780x125 mm deep with C.P. brass waste, C.I lugs and all other accessories complete as required. | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 473 | 58.4628 | 0 | 531.4628 | 0 | 0 | 0
22 | 501020000 | Fixing, testing and commissioning of sink including providing & fixing C.I./M.S. Brackets (duly painted with 2 coats of paint over a coat of primer) C.P. cast brass bottle trap with extension piece, rubber adaptor, wall flange, union, C.P. brass chainrubber plug & making good. | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22.1 | 501020000 | Stainless Steel sink w/o drain board | [8 empty] | No. | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 604 | 74.6544 | 0 | 678.6544 | 0 | 10179.816 | 10179.816
22.2 | 501020000 | Stainless steel sink with drain board. | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 788 | 97.3968 | 0 | 885.3968 | 0 | 0 | 0
22.3 | 501020000 | Sainless sink with double drain board | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 840 | 103.824 | 0 | 943.824 | 0 | 0 | 0
23 | 501020000 | Providing, fixing, testing and commissioning of C.P. brass wall / counter mounted sink mixer with C.P. wall flange, overhead swinging spout complete as required and making good. | [8 empty] | No. | 20 | 4344 | 0 | 4344 | 217.2 | 0 | 4561.2 | 210 | 25.956 | 0 | 235.956 | 91224 | 4719.12 | 95943.12
24 | 501020000 | Providing, fixing of white viterous china Janitor sink of size 470 x 370 x 180mm deep including providing & fixing CI/MS brackets (duly painted with 2 coats of paint over a coat of primer) C.P. cast brass bottle trap with extension piece, rubber adopter, wall flange, union, C.P. brass chain rubber plug complete as required. | [8 empty] | No. | 5 | 5322 | 0 | 5322 | 266.1 | 0 | 5588.1 | 420 | 51.912 | 0 | 471.912 | 27940.5 | 2359.56 | 30300.06
25 | 501020000 | Fixing storage type water heater of approved shade with copper container, glasswool insulation,stove enamelled M.S jacket, thermostatically controlled inner heater with pilot neon lamps, angle valve on inlet connection, 15mm dia C.P flexible connection pipe in inlet & outlet suitable for working pressure of 5 kg/sqcm complete as required. | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25.1 | 501020000 | Capacity 15 litres | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 263 | 32.5068 | 0 | 295.5068 | 0 | 0 | 0
25.2 | 501020000 | Capacity 25 litres | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 368 | 45.4848 | 0 | 413.4848 | 0 | 0 | 0
26 | 501020000 | Fixing storage type water cooler of the following capacity, I.S.I marked, stainless steel front panel, C.P brass push cock, inlet float valve with all plumbing and electrical accessories, inlet, outlet, overflow and PVC drain out connection to F.D complete as required. | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26.1 | 501020000 | Cooling capacity 15 Lts./hr Storage capacity 40 Lts. | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 525 | 64.89 | 0 | 589.89 | 0 | 0 | 0
26.2 | 501020000 | Cooling capacity 40Lts./hr Storage capacity 80 Lts. | [8 empty] | No. | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 683 | 84.4188 | 0 | 767.4188 | 0 | 1534.8376 | 1534.8376
27 | 501020000 | Providing , fixing commercial water purifier of water flow rate 2.0 Lit/min. Including all components as per manufacture specifications, including connection from water supply line, and final connection to water cooler electric wiring & plug top etc. with all accessories. | [8 empty] | No. | 7 | 15250 | 0 | 15250 | 762.5 | 0 | 16012.5 | 473 | 58.4628 | 0 | 531.4628 | 112087.5 | 3720.2396 | 115807.7396
28 | 501020000 | Fixing solid state, no touch operting, fully hygienic hand drier of approved shade with single blower, with time delay, summer & winter control, volume ON/OFF controls including providing necessary brackets, cable from drier to Plug, Plug top key and lock etc, complete as required. | [8 empty] | No. | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 38.934 | 0 | 353.934 | 0 | 5309.01 | 5309.01
29 | 501020000 | Fixing solid state, no touch operating, fully hygienic hand drier of approved shade with double blower, continous repeat usage,time delay, summer & winter control including providing necessary brackets, cable from drier to Plug, Plug to key and lock etc. complete as required. | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 51.912 | 0 | 471.912 | 0 | 0 | 0
30 | 501020000 | Fixing S.S. toilet paper holder with PVC rawl plug & C.P. brass screw complete as required. | [8 empty] | No. | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 9.7644 | 0 | 88.7644 | 0 | 23966.388 | 23966.388
31 | 501020000 | Fixing S.S. reserve toilet paper holder with PVC rawl plug & C.P. brass screw complete as required. | [8 empty] | No. | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 9.7644 | 0 | 88.7644 | 0 | 18640.524 | 18640.524
32 | 501020000 | Fixing Recessed type S.S. soap dish with PVC rawl plug & C.P. brass screw complete as required. | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 12.978 | 0 | 117.978 | 0 | 0 | 0
33 | 501020000 | Fixing C.P. brass liquid soap container with PVC rawl plug & C.P. brass screw complete as required. | [8 empty] | No. | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 12.978 | 0 | 117.978 | 0 | 1179.78 | 1179.78
34 | 501020000 | Fixing push type liquid soap dispenser with PVC rawl plug & C.P. brass screw complete as required. | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 12.978 | 0 | 117.978 | 0 | 0 | 0
35 | 501020000 | Fixing C.P. brass twin coat hook with PVC rawl plug & C.P. brass screw complete as required. | [8 empty] | No. | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 6.5508 | 0 | 59.5508 | 0 | 16078.716 | 16078.716
36 | 501020000 | Fixing C.P brass deodourizer. | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131 | 16.1916 | 0 | 147.1916 | 0 | 0 | 0
37 | 501020000 | Fixing deodoriser system with turbo fan, battery & cartridge including wall mounting arrangement complete as required. | [8 empty] | No. | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 263 | 32.5068 | 0 | 295.5068 | 0 | 7387.67 | 7387.67
38 | 501020000 | Fixing towel rack deluxe with PVC rawl plug & C.P. brass screw complete as required of size Size 230 x 600 mm | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 19.5288 | 0 | 177.5288 | 0 | 0 | 0
39 | 501020000 | Fixing, testing and commissioning of 15 mm dia C.P. brass 2 way angle valve with C.P. wall flange of approved quality and making good. | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 12.978 | 0 | 117.978 | 0 | 0 | 0
40 | 501020000 | Fixing, testing and commissioning of 15 mm dia C.P. brass bib cock with C.P. wall flange of approved quality and making good as required. | [8 empty] | No. | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 12.978 | 0 | 117.978 | 0 | 1179.78 | 1179.78
41 | 501020000 | Fixing, testing and commissioning of C.P. brass angle valve with C.P. wall flange, Nut and Washer etc. complete as required. | [8 empty] | No. | 1170 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 10.3824 | 0 | 94.3824 | 0 | 110427.408 | 110427.408
42 | 501020000 | Fixing, testing and commissioning of C.P Copper connection 375 mm long including nuts and washers and making connection to fixtures and fittings complete as required. | [8 empty] | No. | 870 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 12.978 | 0 | 117.978 | 0 | 102640.86 | 102640.86
43 | 501020000 | Fixing, testing and commissioning of pillar cock for sinks and making good as required. | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 12.978 | 0 | 117.978 | 0 | 0 | 0
44 | 501020000 | Fixing Jacuzzi-whirl pool bath system consist the following items. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
45 | 501020000 | 1 No. Acrylic bath tub of 1780 mm dia with bottom supports.6 Nos CP brass venturi jets with revolving outlet.ON/OFF switch, ELCB, control wiring & cabling.2 HP motor pump set with electronic device to prevent the motor from running dry.Air controller, suction outlet.Automatic waste cum over flow with cast brass P/S trap and all necessary fittings and final connection to F.D.PVC pipe connecting to the system.C.P brass bath mixer (bath tub mounted) with telephonic shower, stand & crutch. Bath System as described above | [8 empty] | Set | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46 | 501020000 | Fixing adjustable type wash basin for handicap toilet complete with brackets, tracks, waste pipes and other accessories complete as required. | [8 empty] | No. | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 998 | 123.3528 | 0 | 1121.3528 | 0 | 4485.4112 | 4485.4112
47 | 501020000 | Fixing 2 Nos. support arms and backrest to mounted on the track (vertically and laterally) for handicap toilet complete as required. | [8 empty] | No. | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 38.934 | 0 | 353.934 | 0 | 1415.736 | 1415.736
48 | 501020000 | Fixing raised toilet seat with cover for handicap toilet | [8 empty] | No. | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 263 | 32.5068 | 0 | 295.5068 | 0 | 1182.0272 | 1182.0272
49 | 501020000 | Fixing 35 mm dia powder coated steel grab bar. | [8 empty] | No. | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 210 | 25.956 | 0 | 235.956 | 0 | 943.824 | 943.824
50 | 501020000 | Fixing shower chair comprising of individual seat & bank completely adjustable, counter balanced fold & hold mechanisum | [8 empty] | No. | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 368 | 45.4848 | 0 | 413.4848 | 0 | 1653.9392 | 1653.9392
B | 501030000 | COLD WATER SUPPLY : (INTERNAL / EXTERNAL) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 501030000 | Providing, fixing,commissioning & testing ( at required pressure) CPVC (Chlorinated Poly Vinyl Chloride) water supply pipes with pipe as per CTS SDR 11 (operating pressure - 7 Bar @ 82 Deg C and 28 Bar @ 23 Deg C)for pipes from 1/2 Inch to 2 Inch. Schedule 40 Pipe to be used from 2-1/2 Inch to 6 Inch. Pipes shall be joined using solvent welded CPVC fittings i.e. Tees, Elbows, Couplers, Unions, Reducers, brushings etc. including transition fittings (connection between CPVC & metal pipe/GI) i.e. Brass Adaptors (both Male & Female threaded) conforming to ASTM D-2846. ASTM F441 with only CPVC solvent cement conforming to ASTM F-493. All termination points for installation of faucets shall have brass termination fittings. Installation shall be to as per Technical Manual of manufacturer of pipes & fittings.Cost shall be inclusive of (a)Making maximum of 7.5 x 7.5 cm chase in wall and floors for the pipe, making good the same by using 1:2 cement mortar over the wire mesh complete as required or (b) Fixing/supporting the pipes (& fittings) at wall/ceiling level supported by galvanized clamps, fastener, hangers etc, as per specification. Exposed pipes to be painted of legends with direction arrow. M.S. pipe sleeves suitable higher size shall be provided wherever the pipes are crossing the fire rated walls / floors slab and sealing the sleeves with glass wool in between and fire sealant compound at either end all as per Project Managers / Consultant requirement. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.1 | 501030000 | 1/2" dia (15 mm) | [8 empty] | RM | 5500 | 102 | 0 | 102 | 5.1 | 0 | 107.1 | 41 | 5.0676 | 0 | 46.0676 | 589050 | 253371.8 | 842421.8
1.2 | 501030000 | 3/4" dia (20 mm | [8 empty] | RM | 3500 | 163 | 0 | 163 | 8.15 | 0 | 171.15 | 41 | 5.0676 | 0 | 46.0676 | 599025 | 161236.6 | 760261.6
1.3 | 501030000 | 1" dia (25 mm) a | [8 empty] | RM | 2000 | 228 | 0 | 228 | 11.4 | 0 | 239.4 | 51 | 6.3036 | 0 | 57.3036 | 478800 | 114607.2 | 593407.2
1.4 | 501030000 | 1.1/4" dia (32 mm) | [8 empty] | RM | 1200 | 327 | 0 | 327 | 16.35 | 0 | 343.35 | 56 | 6.9216 | 0 | 62.9216 | 412020 | 75505.92 | 487525.92
1.5 | 501030000 | 1.1/2: dia (40 mm | [8 empty] | RM | 700 | 425 | 0 | 425 | 21.25 | 0 | 446.25 | 77 | 9.5172 | 0 | 86.5172 | 312375 | 60562.04 | 372937.04
1.6 | 501030000 | 2" dia (50 mm | [8 empty] | RM | 350 | 660 | 0 | 660 | 33 | 0 | 693 | 92 | 11.3712 | 0 | 103.3712 | 242550 | 36179.92 | 278729.92
1.7 | 501030000 | 2.1/2" dia (65 mm) | [8 empty] | RM | 200 | 1300 | 0 | 1300 | 65 | 0 | 1365 | 128 | 15.8208 | 0 | 143.8208 | 273000 | 28764.16 | 301764.16
1.8 | 501030000 | 3" dia (80 mm | [8 empty] | RM | 200 | 1980 | 0 | 1980 | 99 | 0 | 2079 | 154 | 19.0344 | 0 | 173.0344 | 415800 | 34606.88 | 450406.88
1.9 | 501030000 | 4" dia (100 mm | [8 empty] | RM | 250 | 2870 | 0 | 2870 | 143.5 | 0 | 3013.5 | 200 | 24.72 | 0 | 224.72 | 753375 | 56180 | 809555
1.1 | 501030000 | 6" dia (150 mm | [8 empty] | RM | 0 | 4700 | 0 | 4700 | 235 | 0 | 4935 | 315 | 38.934 | 0 | 353.934 | 0 | 0 | 0
2 | 501030000 | Providing, fixing, commissioning & testing male/ female screwed end full way lever operated forged brass ball valve of brass body with forged brass hard chromeplated ball & teflon seat tested to a pressure 30 Kg / sqcm with (threaded joints) complete as required. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.1 | 501030000 | 15 mm di | [8 empty] | No. | 250 | 266 | 0 | 266 | 13.3 | 0 | 279.3 | 72 | 8.8992 | 0 | 80.8992 | 69825 | 20224.8 | 90049.8
2.2 | 501030000 | 20 mm di | [8 empty] | No. | 15 | 382 | 0 | 382 | 19.1 | 0 | 401.1 | 72 | 8.8992 | 0 | 80.8992 | 6016.5 | 1213.488 | 7229.988
2.3 | 501030000 | 25 mm di | [8 empty] | No. | 240 | 594 | 0 | 594 | 29.7 | 0 | 623.7 | 103 | 12.7308 | 0 | 115.7308 | 149688 | 27775.392 | 177463.392
2.4 | 501030000 | 32 mm di | [8 empty] | No. | 15 | 1055 | 0 | 1055 | 52.75 | 0 | 1107.75 | 128 | 15.8208 | 0 | 143.8208 | 16616.25 | 2157.312 | 18773.562
2.5 | 501030000 | 40 mm d | [8 empty] | No. | 35 | 1528 | 0 | 1528 | 76.4 | 0 | 1604.4 | 158 | 19.5288 | 0 | 177.5288 | 56154 | 6213.508 | 62367.508
2.6 | 501030000 | 50 mm a | [8 empty] | No. | 25 | 2321 | 0 | 2321 | 116.05 | 0 | 2437.05 | 210 | 25.956 | 0 | 235.956 | 60926.25 | 5898.9 | 66825.15
3 | 501030000 | Providing, fixing & commissioning C.I. Butterfly valve (Body : Grey Cast Iron, shaft : SS, Disc : SG Iron (nickel plated), Liner : HT - EPDM) of approved make with flange, washer, nuts & bolts and PN 10 pressure rating including rubber gasket & painting complete. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.1 | 501030000 | 50 mm | [8 empty] | No. | 0 | 3360 | 0 | 3360 | 168 | 0 | 3528 | 263 | 32.5068 | 0 | 295.5068 | 0 | 0 | 0
3.2 | 501030000 | 65 mm di | [8 empty] | No. | 0 | 3732 | 0 | 3732 | 186.6 | 0 | 3918.6 | 341 | 42.1476 | 0 | 383.1476 | 0 | 0 | 0
3.3 | 501030000 | 80mm | [8 empty] | No. | 0 | 4440 | 0 | 4440 | 222 | 0 | 4662 | 420 | 51.912 | 0 | 471.912 | 0 | 0 | 0
3.4 | 501030000 | 100 mm di | [8 empty] | No. | 0 | 5820 | 0 | 5820 | 291 | 0 | 6111 | 525 | 64.89 | 0 | 589.89 | 0 | 0 | 0
3.5 | 501030000 | 150 mm d | [8 empty] | No. | 0 | 8640 | 0 | 8640 | 432 | 0 | 9072 | 788 | 97.3968 | 0 | 885.3968 | 0 | 0 | 0
4 | 501030000 | Providing & fixing C.I. wafer type check valve of rating PN 10 including rubber gasket, flanges, union, nuts, bolts, washers & painting complete as required. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4.1 | 501030000 | 50 mm d | [8 empty] | No. | 9 | 3136 | 0 | 3136 | 156.8 | 0 | 3292.8 | 258 | 31.8888 | 0 | 289.8888 | 29635.2 | 2608.9992 | 32244.1992
4.2 | 501030000 | 65 mm d | [8 empty] | No. | 6 | 3626 | 0 | 3626 | 181.3 | 0 | 3807.3 | 334 | 41.2824 | 0 | 375.2824 | 22843.8 | 2251.6944 | 25095.4944
4.3 | 501030000 | 80 mm d | [8 empty] | No. | 5 | 4331 | 0 | 4331 | 216.55 | 0 | 4547.55 | 412 | 50.9232 | 0 | 462.9232 | 22737.75 | 2314.616 | 25052.366
4.4 | 501030000 | 100 mm d | [8 empty] | No. | 4 | 5635 | 0 | 5635 | 281.75 | 0 | 5916.75 | 515 | 63.654 | 0 | 578.654 | 23667 | 2314.616 | 25981.616
4.5 | 501030000 | 150 mm | [8 empty] | No. | 0 | 8200 | 0 | 8200 | 410 | 0 | 8610 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 501030000 | Providing & fixing dual flanged C.I. Y Strainer with stainless steel fine wire mesh perforated sheet basket with necessary flange/ unions nuts, bolts and washers complete as required. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.1 | 501030000 | 65 mm di | [8 empty] | No. | 0 | 3732 | 0 | 3732 | 186.6 | 0 | 3918.6 | 341 | 42.1476 | 0 | 383.1476 | 0 | 0 | 0
5.2 | 501030000 | 80 mm | [8 empty] | No. | 0 | 4542 | 0 | 4542 | 227.1 | 0 | 4769.1 | 420 | 51.912 | 0 | 471.912 | 0 | 0 | 0
5.3 | 501030000 | 100 mm di | [8 empty] | No. | 0 | 6936 | 0 | 6936 | 346.8 | 0 | 7282.8 | 525 | 64.89 | 0 | 589.89 | 0 | 0 | 0
5.4 | 501030000 | 150 mm d | [8 empty] | No. | 0 | 12816 | 0 | 12816 | 640.8 | 0 | 13456.8 | 788 | 97.3968 | 0 | 885.3968 | 0 | 0 | 0
6 | 501030000 | Providing & fixing of gun metal screwed ended Y type strainer with SS fine wire mash/ perforated sheet with necessary fitting complete as required. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6.1 | 501030000 | 40 mm di | [8 empty] | No | 0 | 3725 | 0 | 3725 | 186.25 | 0 | 3911.25 | 210 | 25.956 | 0 | 235.956 | 0 | 0 | 0
6.2 | 501030000 | 50 mm di | [8 empty] | No | 0 | 4800 | 0 | 4800 | 240 | 0 | 5040 | 263 | 32.5068 | 0 | 295.5068 | 0 | 0 | 0
7 | 501030000 | Providing and fixing in position of approved quality high pressure rated Gun Metal Float Valve with copper ball float and brass rods of required length suitable for test pressure of not less than 15 Kg/sqcm of the following sizes: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7.1 | 501030000 | 40 mm diaa | [8 empty] | No. | 2 | 3273 | 0 | 3273 | 163.65 | 0 | 3436.65 | 206 | 25.4616 | 0 | 231.4616 | 6873.3 | 462.9232 | 7336.2232
7.2 | 501030000 | 50 mm dia b | [8 empty] | No. | 2 | 5791 | 0 | 5791 | 289.55 | 0 | 6080.55 | 258 | 31.8888 | 0 | 289.8888 | 12161.1 | 579.7776 | 12740.8776
7.3 | 501030000 | 80 mm di | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7.4 | 501030000 | 100 mm dia | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 501030000 | Providing and fixing heavy duty floating flange EPDM rubber expansion joint with unit control (tie rod & gusset plate) as per manufacturers specifications of standard length complete with all accessories tested to a pressure not less than 15 Kg./sqcm including rubber gaskets, flanges, nuts, bolts & washers complete as required. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8.1 | 501030000 | 50 mm dia | [8 empty] | No. | 0 | 3715 | 0 | 3715 | 185.75 | 0 | 3900.75 | 158 | 19.5288 | 0 | 177.5288 | 0 | 0 | 0
8.2 | 501030000 | 65 mm dia | [8 empty] | No. | 0 | 4100 | 0 | 4100 | 205 | 0 | 4305 | 210 | 25.956 | 0 | 235.956 | 0 | 0 | 0
8.3 | 501030000 | 80 mm dia | [8 empty] | No. | 0 | 4465 | 0 | 4465 | 223.25 | 0 | 4688.25 | 252 | 31.1472 | 0 | 283.1472 | 0 | 0 | 0
8.4 | 501030000 | 100 mm dia | [8 empty] | No. | 0 | 5805 | 0 | 5805 | 290.25 | 0 | 6095.25 | 315 | 38.934 | 0 | 353.934 | 0 | 0 | 0
8.5 | 501030000 | 150 mm dia | [8 empty] | No. | 0 | 7530 | 0 | 7530 | 376.5 | 0 | 7906.5 | 473 | 58.4628 | 0 | 531.4628 | 0 | 0 | 0
9 | 501030000 | Providing and fixing pressure reducing station for cold water supply comprising of 2 Nos PRV,4Nos Gun Metal ball valves on inlet & outlet & Screwed connection, 2 No. Y strainer, 2 Nos Pressure gauge on inlet & outlet, and 1 No. 15 mm dia safety valve. The complete system is tested to a pressure not less than 15 Kg/Sq.cm and suitable to reduce the pressure upto 2 Kg/Sq.cm) Including necessary pipe & fittings; i.e. flanges/ unions, nuts, bolts and washers complete as required. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.1 | 501030000 | 25 mm dia (Brass Housing - PRV) | [8 empty] | No. | 0 | 12810 | 0 | 12810 | 640.5 | 0 | 13450.5 | 525 | 64.89 | 0 | 589.89 | 0 | 0 | 0
9.2 | 501030000 | 32 mm dia (Brass Housing - PRV) a | [8 empty] | No. | 5 | 15648 | 0 | 15648 | 782.4 | 0 | 16430.4 | 658 | 81.3288 | 0 | 739.3288 | 82152 | 3696.644 | 85848.644
9.3 | 501030000 | 40 mm dia (CI Housing - PRV) | [8 empty] | No. | 10 | 19400 | 0 | 19400 | 970 | 0 | 20370 | 823.2 | 101.7475 | 0 | 924.9475 | 203700 | 9249.4752 | 212949.4752
9.4 | 501030000 | 50 mm dia (CI Housing - PRV) | [8 empty] | No. | 2 | 27165 | 0 | 27165 | 1358.25 | 0 | 28523.25 | 1029 | 127.1844 | 0 | 1156.1844 | 57046.5 | 2312.3688 | 59358.8688
9.5 | 501030000 | 65 mm dia (CI Housing - PRV) | [8 empty] | No. | 0 | 46335 | 0 | 46335 | 2316.75 | 0 | 48651.75 | 1365 | 168.714 | 0 | 1533.714 | 0 | 0 | 0
10 | 501030000 | Providing, fixing , testing and commissioning water meter with direct reading dial in KL with all necessary fitting such as threaded pieces, unions pressure gauge, isolation cock, flanges piece for future removal, flanges / unions complete with all necessary testing charges and obtaining test certificates from municipal authorities, on following size pipe lines (1 no. strainer shall be provided at inlet & outlet and cost shall be inclusive for the same). | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10.1 | 501030000 | 50 mm dia (CI) | [8 empty] | No. | 2 | 8584 | 0 | 8584 | 429.2 | 0 | 9013.2 | 1235 | 152.646 | 0 | 1387.646 | 18026.4 | 2775.292 | 20801.692
10.2 | 501030000 | 65 mm dia (CI) | [8 empty] | No. | 3 | 11387 | 0 | 11387 | 569.35 | 0 | 11956.35 | 1544 | 190.8384 | 0 | 1734.8384 | 35869.05 | 5204.5152 | 41073.5652
10.3 | 501030000 | 80 mm dia (CI) | [8 empty] | No. | 2 | 14327 | 0 | 14327 | 716.35 | 0 | 15043.35 | 2573 | 318.0228 | 0 | 2891.0228 | 30086.7 | 5782.0456 | 35868.7456
11 | 501030000 | Making water supply connection to kitchen / laundry equipment, appliances, coolers etc. including necessary fittings, (pipes and valves to be paid separately). | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11.1 | 501030000 | 15 mm to 25 mm dia | [8 empty] | No. | 40 | 400 | 0 | 400 | 20 | 0 | 420 | 77 | 9.5172 | 0 | 86.5172 | 16800 | 3460.688 | 20260.688
11.2 | 501030000 | 32 mm to 50 mm dia | [8 empty] | No. | 15 | 550 | 0 | 550 | 27.5 | 0 | 577.5 | 103 | 12.7308 | 0 | 115.7308 | 8662.5 | 1735.962 | 10398.462
12 | 501030000 | Providing and fixing stainless steel hose connection with flange / union connection. | [8 empty] | No. | 3 | 2940 | 0 | 2940 | 147 | 0 | 3087 | 257 | 31.7652 | 0 | 288.7652 | 9261 | 866.2956 | 10127.2956
13 | 501030000 | Providing & fixing Auto Air vent with isolation valve for cold water supply risers, suitable for pressure not less than 10 Kg/Sq.cm. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13.1 | 501030000 | 15 mm dia a | [8 empty] | No. | 10 | 1421 | 0 | 1421 | 71.05 | 0 | 1492.05 | 103 | 12.7308 | 0 | 115.7308 | 14920.5 | 1157.308 | 16077.808
13.2 | 501030000 | 20 mmdia | [8 empty] | No. | 15 | 1764 | 0 | 1764 | 88.2 | 0 | 1852.2 | 103 | 12.7308 | 0 | 115.7308 | 27783 | 1735.962 | 29518.962
13.3 | 501030000 | 25 mm dia a | [8 empty] | No. | 12 | 2156 | 0 | 2156 | 107.8 | 0 | 2263.8 | 128 | 15.8208 | 0 | 143.8208 | 27165.6 | 1725.8496 | 28891.4496
14 | 501030000 | Providing, laying, jointing and testing in position the following Upvc pipes for under ground piping conforming to IS:13592 (Type B 6 kg/sq.cm) including all necessary fittings such as elbow, coupler & tee etc. Cost shall be inclusive of excavation, dewatering, backfilling, ramming surrounding the pipe all round with minimum 150 mm thick all round compacted silver sand and providing thrust block. All work complete as per specification and satisfaction of the Project Manager. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14.1 | 501030000 | 25 mm d | [8 empty] | RM | 20 | 45 | 0 | 45 | 2.25 | 0 | 47.25 | 25 | 3.09 | 0 | 28.09 | 945 | 561.8 | 1506.8
14.2 | 501030000 | 32 mm dia a | [8 empty] | RM | 10 | 55 | 0 | 55 | 2.75 | 0 | 57.75 | 30 | 3.708 | 0 | 33.708 | 577.5 | 337.08 | 914.58
14.3 | 501030000 | 40 mm dia a | [8 empty] | RM | 5 | 59 | 0 | 59 | 2.95 | 0 | 61.95 | 41 | 5.0676 | 0 | 46.0676 | 309.75 | 230.338 | 540.088
14.4 | 501030000 | 50 mm dia a | [8 empty] | RM | 20 | 88 | 0 | 88 | 4.4 | 0 | 92.4 | 52 | 6.4272 | 0 | 58.4272 | 1848 | 1168.544 | 3016.544
14.5 | 501030000 | 65 mm dia a | [8 empty] | RM | 50 | 135 | 0 | 135 | 6.75 | 0 | 141.75 | 72 | 8.8992 | 0 | 80.8992 | 7087.5 | 4044.96 | 11132.46
14.6 | 501030000 | 80 mm da | [8 empty] | RM | 100 | 323 | 0 | 323 | 16.15 | 0 | 339.15 | 93 | 11.4948 | 0 | 104.4948 | 33915 | 10449.48 | 44364.48
14.7 | 501030000 | 100 mm di a | [8 empty] | RM | 50 | 424 | 0 | 424 | 21.2 | 0 | 445.2 | 112 | 13.8432 | 0 | 125.8432 | 22260 | 6292.16 | 28552.16
15 | 501030000 | Providing & fixing in position 25 mm dia lawn hydrants consisting of 25 mm dia Ball valve, GI nipple and quick release coupling / threaded hose receiver complete as required. | [8 empty] | No. | 5 | 2205 | 0 | 2205 | 110.25 | 0 | 2315.25 | 257 | 31.7652 | 0 | 288.7652 | 11576.25 | 1443.826 | 13020.076
16 | 501030000 | Constructing brick masonary chamber (for housing valves, Meters etc.) of brick work with bricks of class 75 with cement mortar 1:5 (1 cement:5 fine sand) plastering internal face & (with a floating coat of neat cement) cement mortar 1:3 (1 cement: 3 fine sand and rough plaster on outer face. R.C.C top slab with medium duty D.I. manhole cover and frame of 600 mm dia (weight : 60 KG). Including excavation, dewatering, refilling, watering, ramming and removing the surplus excavated material complete as required. (All sizes are clear internal sizes). | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16.1 | 501030000 | Size 1000 x 800 x 1200 mm deep | [8 empty] | No. | 1 | 16660 | 0 | 16660 | 833 | 0 | 17493 | 4631 | 572.3916 | 0 | 5203.3916 | 17493 | 5203.3916 | 22696.3916
17 | 501030000 | Constructing brick masonary chamber (for housing lawn hydrant) of brick work with bricks of class 75 in cement mortar 1:5 (1 cement:5 fine sand) plastering internal face with cement 1:3 (1 cement mortar: 3 fine sand) and a rough plaster on outer face with a floating coat of neat cement. R.C.C. top slab with manhole cover & frame. Including excavation, dewatering, refilling, watering, ramming & removing the surplus excavated material complete as required. (All sizes are clear internal sizes). | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17.1 | 501030000 | Size 300 x 300 x 450 mm deep (with 300 x 300 LD : DI cover (Wt: 8 kg)) | [8 empty] | No. | 5 | 3234 | 0 | 3234 | 161.7 | 0 | 3395.7 | 1235 | 152.646 | 0 | 1387.646 | 16978.5 | 6938.23 | 23916.73
18 | 501030000 | Effecting connection from Existing/ Municipal Water Supply line including necessary excavation & making good the same including cutting, boring and tapping the Existing line by providing and installing ferrule / Tee connections with necessary fittings as required and making good the same. The rate for this item also includes complete services from the contractor for liasoning works such as filing necessary applications, submission of forms for approval to the municipal authorities, depositing the fees / other amounts as required for getting the premises / installations, inspected and approved and all other formalities required till the water connection is obtained. All the expenses incurred in this regard shall be borne by the Contractor except for the official payments to be made for any security deposit etc. which will be reimbursed on production of original voucher. | [8 empty] | LS | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 135000 | 16686 | 0 | 151686 | 0 | 151686 | 151686
C | 501030000 | HOT WATER SUPPLY: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 501030000 | Providing, fixing,commissioning & testing(at required pressure) CPVC (Chlorinated Poly Vinyl Chloride) water supply pipes with pipe as per CTS SDR 11 (operating pressure - 7 Bar @ 82 Deg C and 28 Bar @ 23 Deg C)for pipes from 1/2 Inch to 2 Inch. Schedule 80 Pipe to be used from 2-1/2 Inch to 6 Inch. Pipes shall be joined using solvent welded CPVC fittings i.e. Tees, Elbows, Couplers, Unions, Reducers, brushings etc. including transition fittings (connection between CPVC & metal pipe/GI) i.e. Brass Adaptors (both Male & Female threaded) conforming to ASTM D-2846. ASTM F441 with only CPVC solvent cement conforming to ASTM F-493. Cost shall be inclusive of (a) Making maximum of 7.5 x 7.5 cm chase in wall and floors for the pipe, making good the same by using 1:2 cement mortar wire mesh and providing insulation (seprate item) or (b) Fixing/supporting the pipes & fittings at wall/ceiling level supported by galvanized clamps, fastener, puff blocks, hangers etc, as per specification. Exposed pipes to be insulated (seprate item) and painting of legends with direction arrow on insulation. All termination points for installation of faucets shall have brass termination fittings. Installation shall be to as per Technical Manual of manufacturer of pipes & fittings. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 501030000 | M.S. pipe sleeves suitable higher size shall be provided wherever the pipes are crossing the fire rated wall / floor slab and sealing the sleeves with glass wool in between and fire sealant compound at either end all as per Project Managers / Consultant requirement. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.1 | 501030000 | 1/2" dia (15 mm) | [8 empty] | RM | 8000 | 102 | 0 | 102 | 5.1 | 0 | 107.1 | 41 | 5.0676 | 0 | 46.0676 | 856800 | 368540.8 | 1225340.8
2.2 | 501030000 | 3/4" dia (20 mm) | [8 empty] | RM | 4000 | 163 | 0 | 163 | 8.15 | 0 | 171.15 | 41 | 5.0676 | 0 | 46.0676 | 684600 | 184270.4 | 868870.4
2.3 | 501030000 | 1" dia (25 mm) | [8 empty] | RM | 1500 | 228 | 0 | 228 | 11.4 | 0 | 239.4 | 52 | 6.4272 | 0 | 58.4272 | 359100 | 87640.8 | 446740.8
2.4 | 501030000 | 1.1/4" dia (32 mm ) | [8 empty] | RM | 1200 | 327 | 0 | 327 | 16.35 | 0 | 343.35 | 56 | 6.9216 | 0 | 62.9216 | 412020 | 75505.92 | 487525.92
2.5 | 501030000 | 1.1/2: dia (40 mm) | [8 empty] | RM | 700 | 425 | 0 | 425 | 21.25 | 0 | 446.25 | 77 | 9.5172 | 0 | 86.5172 | 312375 | 60562.04 | 372937.04
2.6 | 501030000 | 2" dia (50 mm) | [8 empty] | RM | 450 | 660 | 0 | 660 | 33 | 0 | 693 | 92 | 11.3712 | 0 | 103.3712 | 311850 | 46517.04 | 358367.04
2.7 | 501030000 | 2.1/2" dia | [8 empty] | RM | 200 | 1300 | 0 | 1300 | 65 | 0 | 1365 | 128 | 15.8208 | 0 | 143.8208 | 273000 | 28764.16 | 301764.16
2.8 | 501030000 | 3" dia (80 mm) | [8 empty] | RM | 250 | 1980 | 0 | 1980 | 99 | 0 | 2079 | 155 | 19.158 | 0 | 174.158 | 519750 | 43539.5 | 563289.5
2.9 | 501030000 | 4" dia (100 mm) | [8 empty] | RM | 150 | 2870 | 0 | 2870 | 143.5 | 0 | 3013.5 | 200 | 24.72 | 0 | 224.72 | 452025 | 33708 | 485733
2.1 | 501030000 | 6" dia (150 mm) | [8 empty] | RM | 0 | 4700 | 0 | 4700 | 235 | 0 | 4935 | 315 | 38.934 | 0 | 353.934 | 0 | 0 | 0
3 | 501030000 | Providing and fixing 6 mm thick supercera rope insulation with SS304 brading for return, hot water supply / return, pipes & fittings (in chases) for the following diameter of pipes. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.1 | 501030000 | 15 mm dia to 32 mm dia | [8 empty] | RM | 0 | 180 | 0 | 180 | 9 | 0 | 189 | 53 | 6.5508 | 0 | 59.5508 | 0 | 0 | 0
4 | 501030000 | Providing and fixing nitrle rubber insulation on hot water supply / return pipes. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
4.1 | 501030000 | 15 mm dia (9 mm thickness) | [8 empty] | RM | 8000 | 38 | 0 | 38 | 1.9 | 0 | 39.9 | 15 | 1.854 | 0 | 16.854 | 319200 | 134832 | 454032
4.2 | 501030000 | 20 mm dia (9 mm thickness) | [8 empty] | RM | 4000 | 41 | 0 | 41 | 2.05 | 0 | 43.05 | 20 | 2.472 | 0 | 22.472 | 172200 | 89888 | 262088
4.3 | 501030000 | 25 mm dia (9 mm thickness) | [8 empty] | RM | 1500 | 43 | 0 | 43 | 2.15 | 0 | 45.15 | 25 | 3.09 | 0 | 28.09 | 67725 | 42135 | 109860
4.4 | 501030000 | 32 mm dia (13 mm thickness) | [8 empty] | RM | 1200 | 63 | 0 | 63 | 3.15 | 0 | 66.15 | 31 | 3.8316 | 0 | 34.8316 | 79380 | 41797.92 | 121177.92
4.5 | 501030000 | 40 mm dia (13 mm thickness) | [8 empty] | RM | 700 | 110 | 0 | 110 | 5.5 | 0 | 115.5 | 41 | 5.0676 | 0 | 46.0676 | 80850 | 32247.32 | 113097.32
4.6 | 501030000 | 50 mm dia (13 mm thickness) | [8 empty] | RM | 450 | 132 | 0 | 132 | 6.6 | 0 | 138.6 | 52 | 6.4272 | 0 | 58.4272 | 62370 | 26292.24 | 88662.24
4.7 | 501030000 | 65mm dia (19 mm thickness) | [8 empty] | RM | 200 | 161 | 0 | 161 | 8.05 | 0 | 169.05 | 66 | 8.1576 | 0 | 74.1576 | 33810 | 14831.52 | 48641.52
4.8 | 501030000 | 80mm dia (19 mm thickness) | [8 empty] | RM | 250 | 199 | 0 | 199 | 9.95 | 0 | 208.95 | 82 | 10.1352 | 0 | 92.1352 | 52237.5 | 23033.8 | 75271.3
4.9 | 501030000 | 100 mm dia (19 mm thickness) | [8 empty] | RM | 150 | 233 | 0 | 233 | 11.65 | 0 | 244.65 | 103 | 12.7308 | 0 | 115.7308 | 36697.5 | 17359.62 | 54057.12
4.1 | 501030000 | 150 mm dia (19 mm thickness) | [8 empty] | RM | 0 | 370 | 0 | 370 | 18.5 | 0 | 388.5 | 131 | 16.1916 | 0 | 147.1916 | 0 | 0 | 0
5 | 501030000 | Providing and fixing proprietary polyshield outer mechanical protection ON nitrile rubber insulation comprising of wrapping with poly glass tape helically wound and subsequently applying 2 coats of polyshield material (resin & hardner) as per manufacturers specification and approved by Project Manager / Consultnats. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.1 | 501030000 | 15 mm dia | [8 empty] | RM | 0 | 105 | 0 | 105 | 5.25 | 0 | 110.25 | 21 | 2.5956 | 0 | 23.5956 | 0 | 0 | 0
5.2 | 501030000 | 20 mm dia | [8 empty] | RM | 0 | 120 | 0 | 120 | 6 | 0 | 126 | 26 | 3.2136 | 0 | 29.2136 | 0 | 0 | 0
5.3 | 501030000 | 25 mm dia | [8 empty] | RM | 0 | 140 | 0 | 140 | 7 | 0 | 147 | 37 | 4.5732 | 0 | 41.5732 | 0 | 0 | 0
5.4 | 501030000 | 32 mm dia | [8 empty] | RM | 0 | 178 | 0 | 178 | 8.9 | 0 | 186.9 | 42 | 5.1912 | 0 | 47.1912 | 0 | 0 | 0
5.5 | 501030000 | 40 mm dia | [8 empty] | RM | 0 | 250 | 0 | 250 | 12.5 | 0 | 262.5 | 58 | 7.1688 | 0 | 65.1688 | 0 | 0 | 0
5.6 | 501030000 | 50mm dia | [8 empty] | RM | 0 | 266 | 0 | 266 | 13.3 | 0 | 279.3 | 74 | 9.1464 | 0 | 83.1464 | 0 | 0 | 0
5.7 | 501030000 | 65 mm dia | [8 empty] | RM | 0 | 336 | 0 | 336 | 16.8 | 0 | 352.8 | 89 | 11.0004 | 0 | 100.0004 | 0 | 0 | 0
5.8 | 501030000 | 80mm dia | [8 empty] | RM | 0 | 390 | 0 | 390 | 19.5 | 0 | 409.5 | 110 | 13.596 | 0 | 123.596 | 0 | 0 | 0
5.9 | 501030000 | 100 mm dia | [8 empty] | RM | 0 | 425 | 0 | 425 | 21.25 | 0 | 446.25 | 142 | 17.5512 | 0 | 159.5512 | 0 | 0 | 0
5.1 | 501030000 | 150mm dia | [8 empty] | RM | 0 | 620 | 0 | 620 | 31 | 0 | 651 | 210 | 25.956 | 0 | 235.956 | 0 | 0 | 0
6 | 501030000 | Providing and fixing 22 SWG GI sheet cladding over nitrile rubber insulation on hot water pipe work for the following size pipes. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6.1 | 501030000 | 40 mm dia | [8 empty] | RM | 0 | 259 | 0 | 259 | 12.95 | 0 | 271.95 | 58 | 7.1688 | 0 | 65.1688 | 0 | 0 | 0
6.2 | 501030000 | 50 mm dia | [8 empty] | RM | 0 | 301 | 0 | 301 | 15.05 | 0 | 316.05 | 73 | 9.0228 | 0 | 82.0228 | 0 | 0 | 0
6.3 | 501030000 | 65 mm dia | [8 empty] | RM | 0 | 415 | 0 | 415 | 20.75 | 0 | 435.75 | 89 | 11.0004 | 0 | 100.0004 | 0 | 0 | 0
6.4 | 501030000 | 80mm dia | [8 empty] | RM | 0 | 427 | 0 | 427 | 21.35 | 0 | 448.35 | 110 | 13.596 | 0 | 123.596 | 0 | 0 | 0
6.5 | 501030000 | 100 mm dia | [8 empty] | RM | 0 | 483 | 0 | 483 | 24.15 | 0 | 507.15 | 142 | 17.5512 | 0 | 159.5512 | 0 | 0 | 0
7 | 501030000 | Providing and fixing male/ female screw ended full way lever operated forged brass ball valves with brass body with forged brass hard chrome plated ball / stem, union. Rated to temperature of 85 Deg C and tested to a pressure not less than 30 Kg/Sq.cm. Including covering with nitrile rubber insulation having protective coating against mechanical damage as per manufacturers specification (GI boxing to be provided). | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7.1 | 501030000 | 15 mm di a | [8 empty] | No. | 10 | 266 | 0 | 266 | 13.3 | 0 | 279.3 | 72 | 8.8992 | 0 | 80.8992 | 2793 | 808.992 | 3601.992
7.2 | 501030000 | 20 mm dia a | [8 empty] | No. | 230 | 382 | 0 | 382 | 19.1 | 0 | 401.1 | 72 | 8.8992 | 0 | 80.8992 | 92253 | 18606.816 | 110859.816
7.3 | 501030000 | 25 mm dia b | [8 empty] | No. | 230 | 594 | 0 | 594 | 29.7 | 0 | 623.7 | 103 | 12.7308 | 0 | 115.7308 | 143451 | 26618.084 | 170069.084
7.4 | 501030000 | 32 mm dia b | [8 empty] | No. | 15 | 1055 | 0 | 1055 | 52.75 | 0 | 1107.75 | 128 | 15.8208 | 0 | 143.8208 | 16616.25 | 2157.312 | 18773.562
7.5 | 501030000 | 40 mm dia b | [8 empty] | No. | 15 | 1528 | 0 | 1528 | 76.4 | 0 | 1604.4 | 155 | 19.158 | 0 | 174.158 | 24066 | 2612.37 | 26678.37
7.6 | 501030000 | 50 mm dia c | [8 empty] | No. | 10 | 2321 | 0 | 2321 | 116.05 | 0 | 2437.05 | 206 | 25.4616 | 0 | 231.4616 | 24370.5 | 2314.616 | 26685.116
8 | 501030000 | Providing and fixing C.I. Butterfly valve (Body : Grey Cast Iron, shaft : SS, Disc : SG Iron (nickel plated coated), Liner : HT - EPDM) of approved make with union / flange, washer, nuts & bolts. Rated to temperature of 85 Deg C and PN 10/16 pressure rating including nitrile rubber insulation with proprietary fire proof protective coating against mechanical damage as per manufacturers specification (GI boxing to be provided). | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8.1 | 501030000 | 65 mm dia b | [8 empty] | No. | 10 | 3732 | 0 | 3732 | 186.6 | 0 | 3918.6 | 334 | 41.2824 | 0 | 375.2824 | 39186 | 3752.824 | 42938.824
8.2 | 501030000 | 80 mm dia a | [8 empty] | No. | 10 | 4440 | 0 | 4440 | 222 | 0 | 4662 | 412 | 50.9232 | 0 | 462.9232 | 46620 | 4629.232 | 51249.232
8.3 | 501030000 | 100 mm dia a | [8 empty] | No. | 5 | 5820 | 0 | 5820 | 291 | 0 | 6111 | 515 | 63.654 | 0 | 578.654 | 30555 | 2893.27 | 33448.27
9 | 501030000 | Providing & fixing C.I. Wafer type Check Valve of PN 16 rating of approved make with union / flange, washer, nuts & bolts. Rated to temperature of 85 Deg C and including nitrile rubber insulation with proprietary fire proof protective coating against mechanical damage as per manufacturers specification. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.1 | 501030000 | 65 mm dia | [8 empty] | No. | 0 | 5106 | 0 | 5106 | 255.3 | 0 | 5361.3 | 341 | 42.1476 | 0 | 383.1476 | 0 | 0 | 0
9.2 | 501030000 | 80 mm dia | [8 empty] | No. | 0 | 6144 | 0 | 6144 | 307.2 | 0 | 6451.2 | 420 | 51.912 | 0 | 471.912 | 0 | 0 | 0
9.3 | 501030000 | 100 mm dia | [8 empty] | No. | 0 | 7938 | 0 | 7938 | 396.9 | 0 | 8334.9 | 525 | 64.89 | 0 | 589.89 | 0 | 0 | 0
10 | 501030000 | Providing & fixing C.I. Y (flange type) with stainless steel fine wire mesh and perforated sheet basket with necessary flange/unions, nuts, bolts, washers suitable for test pressure not less than 10 Kg/Sq.cm. Including nitrile rubber insulation with proprietory fire proof protective coating against mechanical damage as per manufacturers specification and approved by Project Manager.Suitable for operation at 85 deg. C. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10.1 | 501030000 | 50 mm dia | [8 empty] | No. | 0 | 4682 | 0 | 4682 | 234.1 | 0 | 4916.1 | 263 | 32.5068 | 0 | 295.5068 | 0 | 0 | 0
10.2 | 501030000 | 65 mm dia | [8 empty] | No. | 0 | 5256 | 0 | 5256 | 262.8 | 0 | 5518.8 | 341 | 42.1476 | 0 | 383.1476 | 0 | 0 | 0
10.3 | 501030000 | 80 mm dia | [8 empty] | No. | 0 | 6696 | 0 | 6696 | 334.8 | 0 | 7030.8 | 420 | 51.912 | 0 | 471.912 | 0 | 0 | 0
10.4 | 501030000 | 100 mm dia | [8 empty] | No. | 0 | 9720 | 0 | 9720 | 486 | 0 | 10206 | 525 | 64.89 | 0 | 589.89 | 0 | 0 | 0
11 | 501030000 | Providing and fixing heavy duty floating flange EPDM rubber expansion joint with unit control (tie rod & gusset plate) as per manufacturers specifications of standard length complete with all accessories testing to a pressure not less than 15 KG / sqcm including rubber gaskets, flanges nuts, bolts & washers complete as required suitable for operation at 85 deg. C. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11.1 | 501030000 | 80 mm dia | [8 empty] | No. | 0 | 5358 | 0 | 5358 | 267.9 | 0 | 5625.9 | 252 | 31.1472 | 0 | 283.1472 | 0 | 0 | 0
11.2 | 501030000 | 100 mm dia | [8 empty] | No. | 0 | 6966 | 0 | 6966 | 348.3 | 0 | 7314.3 | 315 | 38.934 | 0 | 353.934 | 0 | 0 | 0
12 | 501030000 | Providing and fixing auto air vent with isolation valve for Hot water supply system suitable for pressure not less than 10 Kg / Sqcm. suitable for operation at 85 deg. C. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12.1 | 501030000 | 15 mm dia | [8 empty] | No. | 5 | 1294 | 0 | 1294 | 64.7 | 0 | 1358.7 | 103 | 12.7308 | 0 | 115.7308 | 6793.5 | 578.654 | 7372.154
12.2 | 501030000 | 20 mm dia | [8 empty] | No. | 30 | 1680 | 0 | 1680 | 84 | 0 | 1764 | 105 | 12.978 | 0 | 117.978 | 52920 | 3539.34 | 56459.34
12.3 | 501030000 | 25 mm dia | [8 empty] | No. | 0 | 2640 | 0 | 2640 | 132 | 0 | 2772 | 131 | 16.1916 | 0 | 147.1916 | 0 | 0 | 0
13 | 501030000 | Providing and fixing insulated pressure reducing station for hot water supply comprising of 2 nos Gun Metal ball valves on inlet, outlet & 1 nos. globe valve for by pass, 1 No pressure reducing valve with flanged/ screwed connection, 1 No. Y strainer, 2 Nos Pressure gauge on inlet & outlet, and 1 No. 15 mm dia safety valve. The complete system is tested to a pressure not less than 15 Kg/Sq.cm and suitable to reduce the pressure upto 2 Kg/Sq.cm. Including necessary pipes & fittings i.e. flanges/ unions, nuts, bolts and washers complete as required (GI boxing to be provided on the installation).PRV should be operable at 85 deg C. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13.1 | 501030000 | 32 mm dia (Brass Housing - PRV) | [8 empty] | No. | 5 | 16224 | 0 | 16224 | 811.2 | 0 | 17035.2 | 672 | 83.0592 | 0 | 755.0592 | 85176 | 3775.296 | 88951.296
13.2 | 501030000 | 40 mm dia (Brass Housing - PRV) | [8 empty] | No. | 10 | 20161 | 0 | 20161 | 1008.05 | 0 | 21169.05 | 840 | 103.824 | 0 | 943.824 | 211690.5 | 9438.24 | 221128.74
13.3 | 501030000 | 50 mm dia (Brass Housing - PRV) | [8 empty] | No. | 2 | 28184 | 0 | 28184 | 1409.2 | 0 | 29593.2 | 1050 | 129.78 | 0 | 1179.78 | 59186.4 | 2359.56 | 61545.96
14 | 501030000 | Making water supply connection to laundry / kitchen equipment, appliances etc., including necessary fittings, (pipes & valves to paid separately). | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14.1 | 501030000 | Size 15 mm to 25 mm dia | [8 empty] | No. | 40 | 563 | 0 | 563 | 28.15 | 0 | 591.15 | 77 | 9.5172 | 0 | 86.5172 | 23646 | 3460.688 | 27106.688
14.2 | 501030000 | Size 32 mm to 50 mm dia | [8 empty] | No. | 15 | 637 | 0 | 637 | 31.85 | 0 | 668.85 | 103 | 12.7308 | 0 | 115.7308 | 10032.75 | 1735.962 | 11768.712
D | 501040000 | INTERNAL DRAINAGE : (SOIL, WASTE & VENT) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
1 | 501040000 | Providing, fixing, jointing, testing and commissioning spun/centri C.I. pipe for soil, waste & vent pipes installation conforming to IS:3989 cut to required lengths including all necessary fittings and specials such as Bends, junctions, offsets, access pieces (plain or door) & vent cowl. Fixing at wall/ceiling level supported by galvanized steel clamps & hangers etc. duly epoxy coated. Making proper connection with drip seal PJS joint of required depth as per manufacturer. Cutting, chases/holes in floors / walls / slab. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 501040000 | Providing MS pipe sleeves of suitable higher size wherever pipes crossing a fire rated wall / floor slab and sealing of space around pipe and pipe sleeve with glass wool in between and fire proof sealent at either end to the satisfaction of the Project Manager / Consultants and making good the same after pipes have been duly laid and testing complete | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 501040000 | Cost shall also be inclusive of painting the pipes & fittings with two coats of synthetic enamel paint of approved shade over a coat of primer. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.1 | 501040000 | 75 mm di | [8 empty] | RM | 1400 | 1065 | 0 | 1065 | 53.25 | 0 | 1118.25 | 215 | 26.574 | 0 | 241.574 | 1565550 | 338203.6 | 1903753.6
3.2 | 501040000 | 100 mm dia b | [8 empty] | RM | 3500 | 1300 | 0 | 1300 | 65 | 0 | 1365 | 288 | 35.5968 | 0 | 323.5968 | 4777500 | 1132588.8 | 5910088.8
3.3 | 501040000 | 150 mm dia a | [8 empty] | RM | 200 | 2295 | 0 | 2295 | 114.75 | 0 | 2409.75 | 426 | 52.6536 | 0 | 478.6536 | 481950 | 95730.72 | 577680.72
4 | 501040000 | Providing, fixing, jointing, testing and commissioning UPVC (Class III) 6 Kg/cm sq. Rain water down take pipe conforming to IS:4985 cut to required lengths including all necessary fittings and specials. Fixing at wall/ceiling level supported by galvanized steel clamps & hangers etc. Making proper connection with cement solvent joint as per BIS / manufacturer. Cutting, chases / holes in floors / walls / slab. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4.1 | 501040000 | 75 mm dia | [8 empty] | RM | 20 | 144 | 0 | 144 | 7.2 | 0 | 151.2 | 93 | 11.4948 | 0 | 104.4948 | 3024 | 2089.896 | 5113.896
4.2 | 501040000 | 110 mm dia a | [8 empty] | RM | 25 | 363 | 0 | 363 | 18.15 | 0 | 381.15 | 112 | 13.8432 | 0 | 125.8432 | 9528.75 | 3146.08 | 12674.83
4.3 | 501040000 | 160 mm dia a | [8 empty] | RM | 400 | 830 | 0 | 830 | 41.5 | 0 | 871.5 | 185 | 22.866 | 0 | 207.866 | 348600 | 83146.4 | 431746.4
4.4 | 501040000 | 200 mm dia a | [8 empty] | RM | 50 | 1514 | 0 | 1514 | 75.7 | 0 | 1589.7 | 247 | 30.5292 | 0 | 277.5292 | 79485 | 13876.46 | 93361.46
4.5 | 501040000 | 250 mm dia a | [8 empty] | RM | 150 | 1750 | 0 | 1750 | 87.5 | 0 | 1837.5 | 309 | 38.1924 | 0 | 347.1924 | 275625 | 52078.86 | 327703.86
5 | 501040000 | Providing, fixing, jointing and testing in position the C.I. class LA pipe for soil & waste installation conforming to IS:1536. Cut to required lengths including all necessary fittings & specials such as bends, junctions, offsets, access pieces (plain or door). Fixing at wall / ceiling level supported by galvanized steel clamps & hangers etc. duly epoxy coated. Making proper connection. Cuting, chases/holes in floors / walls / slab. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 501040000 | Providing MS pipe sleeves of suitable higher size wherever pipes crossing a fire rated wall or floor slab & sealing of space around pipe and pipe sleeve with glass wool inbetween and fire proof sealant at either end to the satisfaction of the Project Manager / Consultant and making good the same after pipe have been duly laid and testing complete The piping shall have proper connection with dripsed of required depth as per BIS / manufacturer, | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 501040000 | Cost shall also be inclusive of painting the pipes & fittings with two coats of synthetic enamel paint of approved shade over a coat of primer. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7.1 | 501040000 | 100 mm dia | [8 empty] | RM | 0 | 2202 | 0 | 2202 | 110.1 | 0 | 2312.1 | 294 | 36.3384 | 0 | 330.3384 | 0 | 0 | 0
7.2 | 501040000 | 150 mm dia | [8 empty] | RM | 0 | 3524 | 0 | 3524 | 176.2 | 0 | 3700.2 | 446 | 55.1256 | 0 | 501.1256 | 0 | 0 | 0
7.3 | 501040000 | 200 mm dia a | [8 empty] | RM | 300 | 4047 | 0 | 4047 | 202.35 | 0 | 4249.35 | 575 | 71.07 | 0 | 646.07 | 1274805 | 193821 | 1468626
7.4 | 501040000 | 250 mm dia | [8 empty] | RM | 0 | 6325 | 0 | 6325 | 316.25 | 0 | 6641.25 | 720 | 88.992 | 0 | 808.992 | 0 | 0 | 0
8 | 501040000 | Providing, fixing, jointing, testing and commissioning of UPVC pipe (for Planter / landscape drain) confirming to IS : 13592 (Type B 6kg/sq.cm.), cut to required lengths including all necessary fittings and specials such as bends, junctions offsets, access pieces (plain or door) & vent cowl. Fixing at wall / ceiling level supported by G.I. clamps, hangers etc. duly epoxy coated. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8.1 | 501040000 | 110 mm dia | [8 empty] | RM | 25 | 351 | 0 | 351 | 17.55 | 0 | 368.55 | 113 | 13.9668 | 0 | 126.9668 | 9213.75 | 3174.17 | 12387.92
8.2 | 501040000 | 160 mm dia | [8 empty] | RM | 25 | 695 | 0 | 695 | 34.75 | 0 | 729.75 | 185 | 22.866 | 0 | 207.866 | 18243.75 | 5196.65 | 23440.4
9 | 501040000 | Providing and fixing in position G.I. pipe and fittings of heavy class (c) conforming to IS:1239 (for waste pipe from individual fixtures to floor trap / floor drain & vent pipe) Including fixing at wall / ceiling level supported by galvanized clamps and hangers providing two coats of synthetic enamel paint of approved shade as per pipe colour code over a coat of primer or cutting & chasing in wall & floors, providing protection to embedded GI pipes & fittings by wrapping of 400 microne polythene sheet over two coats of bitumen including proper overlaps in joints complete as required and making good the chase by using 1:1 cement mortar. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.1 | 501040000 | 32 mm dia c | [8 empty] | RM | 330 | 352 | 0 | 352 | 17.6 | 0 | 369.6 | 134 | 16.5624 | 0 | 150.5624 | 121968 | 49685.592 | 171653.592
9.2 | 501040000 | 40 mm dia c | [8 empty] | RM | 320 | 396 | 0 | 396 | 19.8 | 0 | 415.8 | 164 | 20.2704 | 0 | 184.2704 | 133056 | 58966.528 | 192022.528
9.3 | 501040000 | 50 mmdia | [8 empty] | RM | 825 | 558 | 0 | 558 | 27.9 | 0 | 585.9 | 206 | 25.4616 | 0 | 231.4616 | 483367.5 | 190955.82 | 674323.32
10 | 501040000 | Providing and fixing in position 75 mm N.B. C.I. Nahni traps of self cleaning design including 125 mm dia CP grating, joining, embedding in concrete etc. complete rate to include making of opening in floor, marble / tiles, for fixing grating. | [8 empty] | Nos. | 25 | 488 | 0 | 488 | 24.4 | 0 | 512.4 | 52 | 6.4272 | 0 | 58.4272 | 12810 | 1460.68 | 14270.68
11 | 501040000 | Providing and fixing in position CI full bore P trap of the following sizes for underslab location including providing necessary galvanized steel support and as per Specification and duly epoxy coated. Making proper connection with refined pig lead / drip seal joints, cutting chase / hole in floors / slabs and bringing the same in proper condition and shape after placing the trap in right position complete by supporting by GI clamps / hangers as required. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11.1 | 501040000 | 100 mm inlet and 80 mm outlet. | [8 empty] | No. | 780 | 588 | 0 | 588 | 29.4 | 0 | 617.4 | 155 | 19.158 | 0 | 174.158 | 481572 | 135843.24 | 617415.24
11.2 | 501040000 | 100 mm inlet and 100 mm outlet. | [8 empty] | No. | 230 | 759 | 0 | 759 | 37.95 | 0 | 796.95 | 155 | 19.158 | 0 | 174.158 | 183298.5 | 40056.34 | 223354.84
12 | 501040000 | Providing & fixing 80mm x 50mm GI waste with reducing elbow & nipple cutting chases, the floor / slab, repairs complete as required and connection to waste pipe. | [8 empty] | No. | 0 | 2040 | 0 | 2040 | 102 | 0 | 2142 | 53 | 6.5508 | 0 | 59.5508 | 0 | 0 | 0
13 | 501040000 | Providing and fixing uPVC boss pipe with three inlet fittings to receive waste pipes from fixtures waste. | [8 empty] | No. | 0 | 1680 | 0 | 1680 | 84 | 0 | 1764 | 53 | 6.5508 | 0 | 59.5508 | 0 | 0 | 0
14 | 501040000 | Providing and fixing Heavy class SS grating with Cockroach proof SS strainer of approved design including setting in floor with cement mortar to match with floor finish as per architect requirement & suitable for waste and FD. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14.1 | 501040000 | Size 100 mm x 100 mm or 100 mm dia | [8 empty] | No. | 0 | 790 | 0 | 790 | 39.5 | 0 | 829.5 | 79 | 9.7644 | 0 | 88.7644 | 0 | 0 | 0
14.2 | 501040000 | Size 150 mm x 150 mm or 125 mm di | [8 empty] | No. | 500 | 793 | 0 | 793 | 39.65 | 0 | 832.65 | 103 | 12.7308 | 0 | 115.7308 | 416325 | 57865.4 | 474190.4
15 | 501040000 | Providing and fixing heavy duty S.S. Floor grating with frame of approved design including setting in floor with cement mortar to match with floor finish as per architect requirement. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15.1 | 501040000 | Size 100 mm x 100 mm or 100 mm dia | [8 empty] | No. | 0 | 540 | 0 | 540 | 27 | 0 | 567 | 79 | 9.7644 | 0 | 88.7644 | 0 | 0 | 0
15.2 | 501040000 | Size 150 mm x 150 mm or 125 mm dia | [8 empty] | No. | 0 | 810 | 0 | 810 | 40.5 | 0 | 850.5 | 105 | 12.978 | 0 | 117.978 | 0 | 0 | 0
16 | 501040000 | Providing and fixing CP brass heavy duty grating with frame of approved design including setting in floor with cement mortar to match with floor finish as per architect requirement. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16.1 | 501040000 | Size 100 mm x 100 mm or 100 mm dia | [8 empty] | No. | 0 | 185 | 0 | 185 | 9.25 | 0 | 194.25 | 53 | 6.5508 | 0 | 59.5508 | 0 | 0 | 0
16.2 | 501040000 | Size 150 mm x 150 mm or 125 mm dia | [8 empty] | No. | 0 | 290 | 0 | 290 | 14.5 | 0 | 304.5 | 79 | 9.7644 | 0 | 88.7644 | 0 | 0 | 0
17 | 501040000 | Providing and fixing 6 mm thick CP brass hinged grating with rim of approved design including setting floor with cement mortar (as per approved by Project Manager design). | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17.1 | 501040000 | For 75 mm dia pipe | [8 empty] | No. | 0 | 360 | 0 | 360 | 18 | 0 | 378 | 53 | 6.5508 | 0 | 59.5508 | 0 | 0 | 0
17.2 | 501040000 | For 100 mm dia pipes | [8 empty] | No. | 200 | 235 | 0 | 235 | 11.75 | 0 | 246.75 | 77 | 9.5172 | 0 | 86.5172 | 49350 | 17303.44 | 66653.44
18 | 501040000 | Providing and fixing ABS heavy duty grating with frame of approved design including setting in floor with cement mortar to match with floor finish as per architect requirement. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18.1 | 501040000 | Size 100 mm x 100 mm | [8 empty] | No. | 0 | 480 | 0 | 480 | 24 | 0 | 504 | 53 | 6.5508 | 0 | 59.5508 | 0 | 0 | 0
18.2 | 501040000 | Size 150 mm x 150 mm | [8 empty] | No. | 0 | 600 | 0 | 600 | 30 | 0 | 630 | 79 | 9.7644 | 0 | 88.7644 | 0 | 0 | 0
19 | 501040000 | Providing and fixing Brass floor clean out plug comprising of GI pipe, socket, elbow, extension piece caulked to pipe and cast brass plug with suitable inlet key for opening male threaded joint with GI class C pipe & socket. Including drip seal caulked to CI pipes or CI class LA pipes complete as required. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19.1 | 501040000 | For 75 mm dia pip | [8 empty] | No. | 5 | 999 | 0 | 999 | 49.95 | 0 | 1048.95 | 103 | 12.7308 | 0 | 115.7308 | 5244.75 | 578.654 | 5823.404
19.2 | 501040000 | For 100 mm dia pip | [8 empty] | No. | 10 | 1470 | 0 | 1470 | 73.5 | 0 | 1543.5 | 103 | 12.7308 | 0 | 115.7308 | 15435 | 1157.308 | 16592.308
19.3 | 501040000 | For 150 mm dia pip | [8 empty] | No. | 5 | 2117 | 0 | 2117 | 105.85 | 0 | 2222.85 | 154 | 19.0344 | 0 | 173.0344 | 11114.25 | 865.172 | 11979.422
19.4 | 501040000 | For 200 mm dia pipe | [8 empty] | No. | 0 | 2940 | 0 | 2940 | 147 | 0 | 3087 | 210 | 25.956 | 0 | 235.956 | 0 | 0 | 0
20 | 501040000 | Providing and fixing cleaning eye on horizontal CI soil & waste pipes, for med of 300 mm long GI pipe with one plain end lead / drip seal caulked in to the collar of CI pipe and the other end with flange which in covered by neoprene rubber gasket and blank flange, complete with nuts, bolts etc and hot dip galvanization after fabrication to the satisfaction of the Project Manager / Consultants. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20.1 | 501040000 | For 75 mm dia pipw | [8 empty] | No. | 5 | 490 | 0 | 490 | 24.5 | 0 | 514.5 | 52 | 6.4272 | 0 | 58.4272 | 2572.5 | 292.136 | 2864.636
20.2 | 501040000 | For 100 mm dia pi | [8 empty] | No. | 8 | 588 | 0 | 588 | 29.4 | 0 | 617.4 | 77 | 9.5172 | 0 | 86.5172 | 4939.2 | 692.1376 | 5631.3376
20.3 | 501040000 | For 150 mm dia pipe | [8 empty] | No. | 10 | 769 | 0 | 769 | 38.45 | 0 | 807.45 | 103 | 12.7308 | 0 | 115.7308 | 8074.5 | 1157.308 | 9231.808
20.4 | 501040000 | For 200 mm dia pie | [8 empty] | No. | 10 | 970 | 0 | 970 | 48.5 | 0 | 1018.5 | 128 | 15.8208 | 0 | 143.8208 | 10185 | 1438.208 | 11623.208
20.5 | 501040000 | For 250 mm dia pipe | [8 empty] | No. | 5 | 1215 | 0 | 1215 | 60.75 | 0 | 1275.75 | 155 | 19.158 | 0 | 174.158 | 6378.75 | 870.79 | 7249.54
21 | 501040000 | Providing and fixing P.V.C. WC connector (straight or bend type) with rubber lip ring. Including 110 mm dia PVC pipe / bend of required length and proper connection with M seal to C.I. pipe complete as required | [8 empty] | No. | 270 | 196 | 0 | 196 | 9.8 | 0 | 205.8 | 52 | 6.4272 | 0 | 58.4272 | 55566 | 15775.344 | 71341.344
22 | 501040000 | Making drainage connection to kitchen / laundry equipment, appliances etc. including necessary GI pipes / fittings & Flexiable pipes complete as required. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22.1 | 501040000 | 32 mm dia to 50 mm dia | [8 empty] | No. | 40 | 392 | 0 | 392 | 19.6 | 0 | 411.6 | 52 | 6.4272 | 0 | 58.4272 | 16464 | 2337.088 | 18801.088
23 | 501040000 | Providing and fixing 25 mm thick CI grating with 30 x 30 x 5 mm angle frame with hold fasts welded at intervals of 600 mm with frame, setting with cement mortar 1:3 (1 cement : 3 sand) true to levels as required (for plant room). All M.S. Angles etc. must be hot dip galvanized. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23.1 | 501040000 | 300 mm wide x 600 mm length | [8 empty] | No. | 0 | 3000 | 0 | 3000 | 150 | 0 | 3150 | 263 | 32.5068 | 0 | 295.5068 | 0 | 0 | 0
23.2 | 501040000 | 200 mm wide x 600 mm length | [8 empty] | No. | 0 | 2500 | 0 | 2500 | 125 | 0 | 2625 | 210 | 25.956 | 0 | 235.956 | 0 | 0 | 0
24 | 501040000 | Providing & fixing rain water Khurras size 450x450 mm required depth with lead flashing around the pipe with one piece lead sheet of 3 mm thick set on a layer of cold bitumen. Including Heavy duty CI/MS grating as per drawing complete as required. | [8 empty] | No. | 10 | 2842 | 0 | 2842 | 142.1 | 0 | 2984.1 | 926 | 114.4536 | 0 | 1040.4536 | 29841 | 10404.536 | 40245.536
25 | 501040000 | Constructing Grease Trap of size as mentioned below of 1200 liquid depth in brick work of class 75 with cement mortar (1:6), inside plastering 16 mm thick with cement mortar 1:3 with floating coat of neat cement and rough plaster on outside. Including aluminium bucket as per detail to collect the grease. RCC top slab with 2 nos. 600 x 600 mm dia medium duty, double seal manhole covers with frame (weight of covers & weight of frame 75 Kg), necessary 150 mm thick foundation concrete (1:2:4). | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25.1 | 501040000 | 2500 x 1200 mm | [8 empty] | No. | 0 | 131250 | 0 | 131250 | 6562.5 | 0 | 137812.5 | 21000 | 2595.6 | 0 | 23595.6 | 0 | 0 | 0
E | 501040000 | EXTERNAL SEWAGE / STORM WATER DRAINAGE: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 501040000 | Providing, laying, jointing and testing in position the following C.I. pipes class (LA) conforming to IS: 1536 for drainage cut to required lengths making proper connections with drip seal of required depths. Pipe to be laid below ground level in trenches upto required depth including excavation in all kind of soil (hard rock), dewatering, refilling, watering, ramming & removing the surplus excavated material and making good the same complete as required. Cost shall be inclusive of providing protection to pipe all round / haunches as per specification. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.1 | 501040000 | 100mm d | [8 empty] | RM | 50 | 1827 | 0 | 1827 | 91.35 | 0 | 1918.35 | 412 | 50.9232 | 0 | 462.9232 | 95917.5 | 23146.16 | 119063.66
1.2 | 501040000 | 150 mm diaaa | [8 empty] | RM | 10 | 2941 | 0 | 2941 | 147.05 | 0 | 3088.05 | 618 | 76.3848 | 0 | 694.3848 | 30880.5 | 6943.848 | 37824.348
2 | 501040000 | Providing, fixing, jointing and testing in position the following UPVC pipes confirming to IS:4985 of 6 Kg / Sq.cm for drainage system cut to required length. Pipe to be laid below ground level in trenches upto required depth including excavation in all kind of soil (hard rock), dewatering, refilling, watering, ramming and removing the surplus excavated material and making good the same complete as required. Cost shall be inclusive of providing protection to pipe all round / haunches as per specification. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.1 | 501040000 | 110 mm diaaa | [8 empty] | RM | 10 | 496 | 0 | 496 | 24.8 | 0 | 520.8 | 180 | 22.248 | 0 | 202.248 | 5208 | 2022.48 | 7230.48
2.2 | 501040000 | 160 mm diaaa | [8 empty] | RM | 25 | 1208 | 0 | 1208 | 60.4 | 0 | 1268.4 | 262 | 32.3832 | 0 | 294.3832 | 31710 | 7359.58 | 39069.58
2.3 | 501040000 | 200 mm dia | [8 empty] | RM | 0 | 1986 | 0 | 1986 | 99.3 | 0 | 2085.3 | 329 | 40.6644 | 0 | 369.6644 | 0 | 0 | 0
2.4 | 501040000 | 250 mm dia | [8 empty] | RM | 0 | 3340 | 0 | 3340 | 167 | 0 | 3507 | 412 | 50.9232 | 0 | 462.9232 | 0 | 0 | 0
3 | 501040000 | Providing,laying, jointing and testing socketed and spigotted RCC pipes (NP2 class) conforming to IS:458 collars jointed with stiff mixture of cement mortar in the proporation of 1:2 (1 cement : 2 find sand) laid to correct levels below ground in trenches upto required depth including excavation in all kind of soil (hard / soft), dewatering, refilling, watering, ramming and removing the surplus excavated material and making good the same complete as required. Cost shall be inclusive of providing protection to pipe all round / haunches as per specification. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.1 | 501040000 | 150 mm dia | [8 empty] | RM | 0 | 465 | 0 | 465 | 23.25 | 0 | 488.25 | 189 | 23.3604 | 0 | 212.3604 | 0 | 0 | 0
3.2 | 501040000 | 200 mm diaaa | [8 empty] | RM | 20 | 560 | 0 | 560 | 28 | 0 | 588 | 247 | 30.5292 | 0 | 277.5292 | 11760 | 5550.584 | 17310.584
3.3 | 501040000 | 250 mm diaaa | [8 empty] | RM | 10 | 563 | 0 | 563 | 28.15 | 0 | 591.15 | 309 | 38.1924 | 0 | 347.1924 | 5911.5 | 3471.924 | 9383.424
3.4 | 501040000 | 300 mm diaa | [8 empty] | RM | 10 | 382 | 0 | 382 | 19.1 | 0 | 401.1 | 370 | 45.732 | 0 | 415.732 | 4011 | 4157.32 | 8168.32
3.5 | 501040000 | 350 mm diaa | [8 empty] | RM | 5 | 996 | 0 | 996 | 49.8 | 0 | 1045.8 | 432 | 53.3952 | 0 | 485.3952 | 5229 | 2426.976 | 7655.976
3.6 | 501040000 | 400 mm dia | [8 empty] | RM | 5 | 1122 | 0 | 1122 | 56.1 | 0 | 1178.1 | 494 | 61.0584 | 0 | 555.0584 | 5890.5 | 2775.292 | 8665.792
3.7 | 501040000 | 450 mm dia | [8 empty] | RM | 0 | 1668 | 0 | 1668 | 83.4 | 0 | 1751.4 | 567 | 70.0812 | 0 | 637.0812 | 0 | 0 | 0
3.8 | 501040000 | 600 mm dia | [8 empty] | RM | 0 | 3006 | 0 | 3006 | 150.3 | 0 | 3156.3 | 756 | 93.4416 | 0 | 849.4416 | 0 | 0 | 0
4 | 501040000 | Construction of road gully chamber of the following sizes in brick work with bricks of class 75 in cement mortar 1 : 5 (1 cement : 5 find sand) necessary foundation concrete(1 : 4 : 8). Inside & outside plastering 12 mm thick with cement mortar 1 : 3 with a floating a coat of neat cement. Including the RCC top slab for fixing the grating including necessary excavation, dewatering, refilling, watering, ramming, removing, the surplus excavated material and making good the same complete as required. Cost shall be inclusive of providing, DI grating with frame. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4.1 | 501040000 | Internal size 450 x 500 x 450 - 600 mm deep; Pre Cast /SFRC Grating with frame 450 x 450 mm | [8 empty] | No. | 5 | 4900 | 0 | 4900 | 245 | 0 | 5145 | 2573 | 318.0228 | 0 | 2891.0228 | 25725 | 14455.114 | 40180.114
4.2 | 501040000 | Internal size 450 x 500 x 600 - 750 mm deep; DI Grating with frame 600 x 600 mm (B-125; 70 kg) | [8 empty] | No. | 0 | 11800 | 0 | 11800 | 590 | 0 | 12390 | 3675 | 454.23 | 0 | 4129.23 | 0 | 0 | 0
5 | 501040000 | Designing and constructing brick masonry inspection chamber of the following sizes in brick work of class 75 in cement mortar 1:5 (1 cement:5 fine sand), R.C.C. top slab with 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm. nominal size) embeded with frame for manhole, RCC foundation slab. 1:2:4 mix (1 cement : 2 coarse sand:4 graded stone aggregate 40 mm nominal size) both inside and outside of plastering 12 mm thick with cement motar 1:3 (1 cement : 3 coarse sand) with a floating coat of neat cement on inside face, proper water proofing to ensure no ground water seepage in the manhole, Poly propylene (conforming to ASTMD - 4101) foot rests (meeting the 224 kg load requirement as per IS 5455) at 300 mm spacing, benching and making channels with 1:2:4 cement concrete neatly finished, including necessary centering and shuttering, reinforcement, excavation, in all kind of soil, dewatering, refilling, watering, ramming and removing the surplus excavated earth, making good the same complete as required. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.1 | 501040000 | Contractor shall submit the structural design and drawings for the approval of Project Manager prior to execution. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.2 | 501040000 | 450 x 450 mm x 600mm | [8 empty] | No. | 0 | 6600 | 0 | 6600 | 330 | 0 | 6930 | 2888 | 356.9568 | 0 | 3244.9568 | 0 | 0 | 0
5.3 | 501040000 | 900 x 600 mm ( 600 to 900 mm deep) | [8 empty] | Nos. | 3 | 9310 | 0 | 9310 | 465.5 | 0 | 9775.5 | 3087 | 381.5532 | 0 | 3468.5532 | 29326.5 | 10405.6596 | 39732.1596
5.4 | 501040000 | Extra depth for (5.2) above 90 cm to 120 cm | [8 empty] | RM | 3 | 1470 | 0 | 1470 | 73.5 | 0 | 1543.5 | 515 | 63.654 | 0 | 578.654 | 4630.5 | 1735.962 | 6366.462
5.5 | 501040000 | Extra depth for (5.2) above 120cm to 180 cm | [8 empty] | RM | 3 | 2450 | 0 | 2450 | 122.5 | 0 | 2572.5 | 1029 | 127.1844 | 0 | 1156.1844 | 7717.5 | 3468.5532 | 11186.0532
5.6 | 501040000 | 1500 mm dia circular type (2300 mm deep) | [8 empty] | No. | 1 | 15680 | 0 | 15680 | 784 | 0 | 16464 | 4631 | 572.3916 | 0 | 5203.3916 | 16464 | 5203.3916 | 21667.3916
5.7 | 501040000 | Extra depth for (5.3) above 150cm & above | [8 empty] | RM | 3 | 3185 | 0 | 3185 | 159.25 | 0 | 3344.25 | 1029 | 127.1844 | 0 | 1156.1844 | 10032.75 | 3468.5532 | 13501.3032
6 | 501040000 | Providing & fixing Ductile Iron Manhole cover with frame: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6.1 | 501040000 | For 600 x 900 mm MH | [8 empty] | No. | 1 | 11270 | 0 | 11270 | 563.5 | 0 | 11833.5 | 515 | 63.654 | 0 | 578.654 | 11833.5 | 578.654 | 12412.154
6.1.1 | 501040000 | 500 x 450 mm, Medium Duty (B-125) Wt - 45 kg | [8 empty] | No. | 5 | 4165 | 0 | 4165 | 208.25 | 0 | 4373.25 | 515 | 63.654 | 0 | 578.654 | 21866.25 | 2893.27 | 24759.52
6.2 | 501040000 | For 1500 mm Circular MH | [8 empty] | No. | 1 | 15680 | 0 | 15680 | 784 | 0 | 16464 | 1029 | 127.1844 | 0 | 1156.1844 | 16464 | 1156.1844 | 17620.1844
6.2.1 | 501040000 | 600 mm dia, Heavy Duty (C-250), Wt : 85 kg | [8 empty] | No. | 1 | 8034 | 0 | 8034 | 401.7 | 0 | 8435.7 | 515 | 63.654 | 0 | 578.654 | 8435.7 | 578.654 | 9014.354
7 | 501040000 | Supply and installing Rain Water Percolation pits - 1500 mm in diameter up to 3200 mm deep, bottom 500 mm filled with boulders 150 - 230 mm size, over which one no. UPVC 160 mm dia (4.0 kg/cm2) perforated pipe with 8 mm dia perforations protected by a cowl on upper end 2100 mm long, surrounding filled with broken bricks up to 1000 mm, pebbles 40 to 50 mm up to 400 mm, Gravel 15 to 25 mm up to 400 mm and upper most layer of 300 mm with coarse sand of 3 to 5 mm. The top 600 mm shall be left open, with RCC grated cover on top. | [8 empty] | No. | 9 | 62040 | 0 | 62040 | 3102 | 0 | 65142 | 24300 | 3003.48 | 0 | 27303.48 | 586278 | 245731.32 | 832009.32
8 | 501040000 | Providing and excuting reverse bore for rain water recharing comprising of rain water harvesting pit as per plumbing site plan drawing complete with PVC (6 kg / sqcm) 160 mm dia slotted pipehaving 3 mm slot, adequate size of bore filled with 3 - 6 mm gravels, complete with bail plug at bottom. The reverse bore shall be 30 meter in depth from the natural ground level and the execution of some shall be in accordance to RWH & conservation manual of CPWD, Govt. of India. | [8 empty] | Job | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5145000 | 635922 | 0 | 5780922 | 0 | 0 | 0
9 | 501040000 | Providing and fixing SEWER TRAP with vent cum Air inlet with MICA flap valve complete with inspection cover with frame for Municipal connection. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.1 | 501040000 | Size 150 mm | [8 empty] | No. | 1 | 2205 | 0 | 2205 | 110.25 | 0 | 2315.25 | 257.25 | 31.7961 | 0 | 289.0461 | 2315.25 | 289.0461 | 2604.2961
10 | 501040000 | Making connection to existing or new Municipal sewer / storm water drain including necessary excavation and breaking the wall of municipal manhole and making good the same with Cement mortar 1:3, finished with a floating coat of neat cement and making drains etc. complete. Removing the excavated surplus material. This also includes the contractor for liasoning work such as filling necessary applications, submission of forms for approval to the municipal authorities, depositing and making channels for the necessary fees and other amounts as required for getting the premises / installations inspected and approved and all other formalities required till the sewer / storm water connection is obtained. All the expenses incurred in this regard shall be borne by the Contractor, except for the payments to be made for any security deposits which will be reimbursed on production of original voucher. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10.1 | 501040000 | For Sewer Connection | [8 empty] | Job | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 147000 | 18169.2 | 0 | 165169.2 | 0 | 165169.2 | 165169.2
10.2 | 501040000 | For Storm Water Connection | [8 empty] | Job | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 122500 | 15141 | 0 | 137641 | 0 | 137641 | 137641
F | 501060000 | CIVIL WORKS / MISCELLANEOUS ITEMS: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 501060000 | Providing and fixing 600 mm long MS hot dip galvanized PUDDLE FLANGES fabricated out of 6 mm thick MS plates of suitable size and IS:1239 heavy class pipes properly fixed in walls & top slab of tanks. The entire fittings shall be hot dipped galvanized after fabrication. Length shall be minimum 600 mm or wall thickness plus 200 mm on either side (which ever is more). | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.1 | 501060000 | 20 mm dia (screwed ends) | [8 empty] | Nos. | 0 | 552 | 0 | 552 | 27.6 | 0 | 579.6 | 84 | 10.3824 | 0 | 94.3824 | 0 | 0 | 0
1.2 | 501060000 | 25 mm dia (screwed ends) | [8 empty] | Nos. | 0 | 619 | 0 | 619 | 30.95 | 0 | 649.95 | 84 | 10.3824 | 0 | 94.3824 | 0 | 0 | 0
1.3 | 501060000 | 32 mm dia (screwed ends) | [8 empty] | Nos. | 0 | 706 | 0 | 706 | 35.3 | 0 | 741.3 | 109 | 13.4724 | 0 | 122.4724 | 0 | 0 | 0
1.4 | 501060000 | 40 mm dia (screwed ends) | [8 empty] | Nos. | 0 | 1065 | 0 | 1065 | 53.25 | 0 | 1118.25 | 134 | 16.5624 | 0 | 150.5624 | 0 | 0 | 0
1.5 | 501060000 | 50 mm dia (flanged ends) | [8 empty] | Nos. | 0 | 1195 | 0 | 1195 | 59.75 | 0 | 1254.75 | 168 | 20.7648 | 0 | 188.7648 | 0 | 0 | 0
1.6 | 501060000 | 80 mm dia (flanged ends) | [8 empty] | Nos. | 0 | 1838 | 0 | 1838 | 91.9 | 0 | 1929.9 | 269 | 33.2484 | 0 | 302.2484 | 0 | 0 | 0
1.7 | 501060000 | 100 mm dia (flanged ends) | [8 empty] | Nos. | 0 | 2659 | 0 | 2659 | 132.95 | 0 | 2791.95 | 336 | 41.5296 | 0 | 377.5296 | 0 | 0 | 0
1.8 | 501060000 | 150 mm dia (flanged ends) | [8 empty] | Nos. | 0 | 3528 | 0 | 3528 | 176.4 | 0 | 3704.4 | 504 | 62.2944 | 0 | 566.2944 | 0 | 0 | 0
1.9 | 501060000 | 200 mm dia (flanged ends) | [8 empty] | Nos. | 0 | 5218 | 0 | 5218 | 260.9 | 0 | 5478.9 | 672 | 83.0592 | 0 | 755.0592 | 0 | 0 | 0
1.1 | 501060000 | 250 mm dia (flanged ends) | [8 empty] | Nos. | 0 | 6500 | 0 | 6500 | 325 | 0 | 6825 | 840 | 103.824 | 0 | 943.824 | 0 | 0 | 0
1.11 | 501060000 | 300 mm dia (flanged ends) | [8 empty] | Nos. | 0 | 8719 | 0 | 8719 | 435.95 | 0 | 9154.95 | 1008 | 124.5888 | 0 | 1132.5888 | 0 | 0 | 0
2 | 501060000 | Providing and fixing blank flanges, making flanged joints with bolts, nuts, washers and rubber insertion 3 mm thick, testing the flange and joints etc. complete for pipes of following diameter. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.1 | 501060000 | 50 mm diaa | [8 empty] | Pair | 1 | 666 | 0 | 666 | 33.3 | 0 | 699.3 | 123 | 15.2028 | 0 | 138.2028 | 699.3 | 138.2028 | 837.5028
2.2 | 501060000 | 80 mm dia | [8 empty] | Pair | 3 | 1421 | 0 | 1421 | 71.05 | 0 | 1492.05 | 195 | 24.102 | 0 | 219.102 | 4476.15 | 657.306 | 5133.456
2.3 | 501060000 | 100 mm diaaa | [8 empty] | Pair | 5 | 2038 | 0 | 2038 | 101.9 | 0 | 2139.9 | 247 | 30.5292 | 0 | 277.5292 | 10699.5 | 1387.646 | 12087.146
2.4 | 501060000 | 150 mm diam | [8 empty] | Pair | 2 | 3361 | 0 | 3361 | 168.05 | 0 | 3529.05 | 370 | 45.732 | 0 | 415.732 | 7058.1 | 831.464 | 7889.564
3 | 501060000 | Providing and fixing in position the UPVC SLEEVES each to be embedded in RCC walls / beams. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.1 | 501060000 | 250 mm dia (600 mm long) | [8 empty] | No. | 1 | 3626 | 0 | 3626 | 181.3 | 0 | 3807.3 | 206 | 25.4616 | 0 | 231.4616 | 3807.3 | 231.4616 | 4038.7616
3.2 | 501060000 | 150 mm dia (600 mm long) | [8 empty] | No. | 5 | 1979 | 0 | 1979 | 98.95 | 0 | 2077.95 | 128 | 15.8208 | 0 | 143.8208 | 10389.75 | 719.104 | 11108.854
3.3 | 501060000 | 100 mm dia (600 mm long) | [8 empty] | No. | 5 | 1176 | 0 | 1176 | 58.8 | 0 | 1234.8 | 103 | 12.7308 | 0 | 115.7308 | 6174 | 578.654 | 6752.654
4 | 501060000 | Providing and fixing DI Grating (Grade A-15) with 40 x 40 mm angle frame with hold fasts welded at intervals of 600 mm setting with cement mortar 1:3 (1 cement : 3 sand) true to levels as required (for Plant Room & Car Parking Areas) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4.1 | 501060000 | 300 mm wide x 600 mm length (wt : 12 Kg) | [8 empty] | No. | 0 | 1876 | 0 | 1876 | 93.8 | 0 | 1969.8 | 210 | 25.956 | 0 | 235.956 | 0 | 0 | 0
4.2 | 501060000 | 450 mm wide x 600 mm length (wt : 16 kg) | [8 empty] | No. | 0 | 3125 | 0 | 3125 | 156.25 | 0 | 3281.25 | 315 | 38.934 | 0 | 353.934 | 0 | 0 | 0
4.3 | 501060000 | Internal size 600 x 600 Pre Cast/ SFRC Grating with frame | [8 empty] | No. | 0 | 5500 | 0 | 5500 | 275 | 0 | 5775 | 473 | 58.4628 | 0 | 531.4628 | 0 | 0 | 0
5 | 501060000 | Providing & fixing GI Waste pipe for upper basement drainage. Cost shall be inclusive of providing, jointing & fixing GI heavy class pipe, including all necessary fittings and especial such as bends, elbows, unions, socket, connection with waste puddle flange at ceiling slabs etc. Fixing at wall / ceiling / clamping at color with galvanized steel clamps & hangers etc. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.1 | 501060000 | 100 mm dia | [8 empty] | RM. | 0 | 1750 | 0 | 1750 | 87.5 | 0 | 1837.5 | 420 | 51.912 | 0 | 471.912 | 0 | 0 | 0
5.2 | 501060000 | 80 mm diam | [8 empty] | RM. | 250 | 764 | 0 | 764 | 38.2 | 0 | 802.2 | 329 | 40.6644 | 0 | 369.6644 | 200550 | 92416.1 | 292966.1
6 | 501060000 | Providing and fixing 6 mm thick CP brass hinged grating with rim of approved design including setting floor with cement mortar (as per approved by Project Manager design). | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6.1 | 501060000 | For 100 mm dia pipe | [8 empty] | Nos. | 25 | 465 | 0 | 465 | 23.25 | 0 | 488.25 | 103 | 12.7308 | 0 | 115.7308 | 12206.25 | 2893.27 | 15099.52
7 | 501060000 | Providing & fixing Planter Top / Bottom grating including GI hopper. Cost shall be inclusive of providing SS / Bronze grating with connection to GI socket / waste pipe. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7.1 | 501060000 | 50 mm diam | [8 empty] | Nos. | 15 | 1225 | 0 | 1225 | 61.25 | 0 | 1286.25 | 154 | 19.0344 | 0 | 173.0344 | 19293.75 | 2595.516 | 21889.266
7.2 | 501060000 | 65 mm dia | [8 empty] | Nos. | 0 | 1772 | 0 | 1772 | 88.6 | 0 | 1860.6 | 158 | 19.5288 | 0 | 177.5288 | 0 | 0 | 0
7.3 | 501060000 | 80 asas diaaa | [8 empty] | Nos. | 10 | 1842 | 0 | 1842 | 92.1 | 0 | 1934.1 | 206 | 25.4616 | 0 | 231.4616 | 19341 | 2314.616 | 21655.616
7.4 | 501060000 | 100 mm dia | [8 empty] | Nos. | 10 | 2303 | 0 | 2303 | 115.15 | 0 | 2418.15 | 257 | 31.7652 | 0 | 288.7652 | 24181.5 | 2887.652 | 27069.152
8 | 501060000 | Providing and fixing 600 mm dia ductile iron (heavy duty) water tank circular cover with frame (as per EN-124) with lockable arrangement complete in all regards (Total WT of cover and frame tobe not less than 85 kg). | [8 empty] | No. | 0 | 15000 | 0 | 15000 | 750 | 0 | 15750 | 525 | 64.89 | 0 | 589.89 | 0 | 0 | 0
8.1 | 501060000 | Providing laying, jointing & testing perforated PVC (class III) pipes with 6 to 8 mm holes on the ¾ circumference of the pipe for sub soil drainage of the courtyard. Provision of geo textile wrapping on the pipe & 10 to 15 mm pebble to prevent ingress of fine particles, shall also be made & the installation shall be to the direction of the landscape consultant & made good to the satisfaction of the Project Manager. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8.2 | 501060000 | 110 mm dia | [8 empty] | RM | 25 | 499 | 0 | 499 | 24.95 | 0 | 523.95 | 123 | 15.2028 | 0 | 138.2028 | 13098.75 | 3455.07 | 16553.82
8.3 | 501060000 | 160 mm dia | [8 empty] | RM | 25 | 1357 | 0 | 1357 | 67.85 | 0 | 1424.85 | 206 | 25.4616 | 0 | 231.4616 | 35621.25 | 5786.54 | 41407.79
9 | 501060000 | Providing and fixing electronic type level indicator for water tanks mounting in panel with the following features, level display, alarm when water level is low or high, full range from one level to four level display and manual reset for alarm etc. with electrical wiring conduit supports from wall & ceiling probs and all other accessories complete as required.(6 Tanks) | [8 empty] | Set | 1 | 22050 | 0 | 22050 | 1102.5 | 0 | 23152.5 | 1544 | 190.8384 | 0 | 1734.8384 | 23152.5 | 1734.8384 | 24887.3384
9.1 | 501060000 | Providing and fixing in position G.I. vent with brass mosquito proof coupling and air filter including return bend, complete as required. The entire fitting shall be hot dip galvanised. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.2 | 501060000 | 50 asas dia | [8 empty] | No. | 6 | 1666 | 0 | 1666 | 83.3 | 0 | 1749.3 | 206 | 25.4616 | 0 | 231.4616 | 10495.8 | 1388.7696 | 11884.5696
9.3 | 501060000 | 80 mm dia | [8 empty] | No. | 0 | 2700 | 0 | 2700 | 135 | 0 | 2835 | 315 | 38.934 | 0 | 353.934 | 0 | 0 | 0
9.4 | 501060000 | 100 mm dia | [8 empty] | No. | 12 | 2940 | 0 | 2940 | 147 | 0 | 3087 | 360 | 44.496 | 0 | 404.496 | 37044 | 4853.952 | 41897.952
10 | 501060000 | Providing and fixing M.S. structural work fabricated from structural steel sections M.S. rounds, angles, channels, tees, square bars, plates including cutting to size, drilling, welding fixing and welding to insert plates in RCC structural works, as directed by Architects. M.S. ladders and tank covers & frame etc. cutting and making good the wall and floor where ever required including two coats of synthetic enamel paint/epoxy paint over a coat of primer. | [8 empty] | Kg | 600 | 75 | 0 | 75 | 3.75 | 0 | 78.75 | 20 | 2.472 | 0 | 22.472 | 47250 | 13483.2 | 60733.2
11 | 501060000 | Providing and fixing 22 gauge GI tray (drip tray) of standard design with necessary fabrication, hanger and support under the horizontal suspended soil / waste header. Tray shall be installed in slop with drain connection at end. The installation shall be to the satisfaction / approval of Project Manager | [8 empty] | Sqm | 0 | 1500 | 0 | 1500 | 75 | 0 | 1575 | 53 | 6.5508 | 0 | 59.5508 | 0 | 0 | 0
12 | 501060000 | Providing and fixing truck fill point consisting of 100 mm dia water filling point having 100 mm dia brass plug (Truck fill point shall be housed in suitable lockable chamber) | [8 empty] | No. | 1 | 11760 | 0 | 11760 | 588 | 0 | 12348 | 515 | 63.654 | 0 | 578.654 | 12348 | 578.654 | 12926.654
13 | 501060000 | Providing and fixing sump pump covers of G.I. Chequered plate 7 mm thick with openable handles on to M.S. Hot Dip Galvanized angle frame. | [8 empty] | Sq.m | 10 | 6321 | 0 | 6321 | 316.05 | 0 | 6637.05 | 360 | 44.496 | 0 | 404.496 | 66370.5 | 4044.96 | 70415.46
14 | 501060000 | Providing and fixing Mosquito proff S.S. netting & Aluminium frame with double leaf door for water tank side manholes with pad lock arrangement | [8 empty] | Sq.m | 5 | 1470 | 0 | 1470 | 73.5 | 0 | 1543.5 | 103 | 12.7308 | 0 | 115.7308 | 7717.5 | 578.654 | 8296.154
15 | 501060000 | Making core cuts in RCC slab for drainage pipe in Guest room & public area as per qty. mention below.(Please refer structural drawing for exact slab thickness) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15.1 | 501060000 | 80 mm Dias | [8 empty] | Nos | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 1183 | 146.2188 | 0 | 1329.2188 | 0 | 33230.47 | 33230.47
15.2 | 501060000 | 100 mm Dia. | [8 empty] | Nos. | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 1311 | 162.0396 | 0 | 1473.0396 | 0 | 331433.91 | 331433.91
15.3 | 501060000 | 150 mm Dia. | [8 empty] | Nos. | 425 | 0 | 0 | 0 | 0 | 0 | 0 | 1646 | 203.4456 | 0 | 1849.4456 | 0 | 786014.38 | 786014.38
G | 501050000 | WATER SUPPLY, DRAINAGE, PUMPS & EQUIPMENT: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 501050000 | Hydropneumatic System:Supply, Installation, Testing And Commissioning Of Compact Self Contained Skid Mounted Hydropneumatic System As Follows:In-Line, Multisage, centrifugal pumps with SS-304 casing and impeller and SS-316 shaft, CI base & head TEFC motor (with mechanical seal)(Vendor to submit performance curves and technical catalog of the proposed model for review & information)The pump shall be selected for performance at best efficiency point. However, the pump selection shall be suitable for performance with set point @ + 20% of the rated head. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.1 | 501050000 | Hydropneumatic systems: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.1.1 | 501050000 | Lower zone- Domestic water supplyNos. of Pumps : 3 (2 Working + 1 Stand by)Water Flow Rate : 3.5 LPS Each pumpHead : 60 M | [8 empty] | Set | 1 | 741760 | 0 | 741760 | 37088 | 0 | 778848 | 46305 | 5723.298 | 0 | 52028.298 | 778848 | 52028.298 | 830876.298
1.1.2 | 501050000 | Upper zone- Domestic water supplyNos. of Pumps : 3 (2 Working + 1 Standby)Water Flow Rate : 6.0 LPS Each pumpHead : 110 M | [8 empty] | Set | 1 | 1134770 | 0 | 1134770 | 56738.5 | 0 | 1191508.5 | 46305 | 5723.298 | 0 | 52028.298 | 1191508.5 | 52028.298 | 1243536.798
1.1.3 | 501050000 | Lower & Upper zone Flushing water supplyNos. of Pumps : 3 (2 Working +1 Standby)Water Flow Rate : 6 LPS Each pumpHead : 110M | [8 empty] | Set | 1 | 1134770 | 0 | 1134770 | 56738.5 | 0 | 1191508.5 | 46305 | 5723.298 | 0 | 52028.298 | 1191508.5 | 52028.298 | 1243536.798
2 | 501050000 | Submersiable Pumps: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.1 | 501050000 | Submersiable Centrifugal Non-clog Drainage Pumps | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.2 | 501050000 | Supply, installation, testing and commissioning of continuous duty submersible centrifugal non-clogging drainage pumps complete with 3 phase motor with all necessary protection and mechanical seal etc. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.3 | 501050000 | Vendor to submit proposed pump model with duty curve. The pump selection shall be on the middle of the curve or on LHS. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.3.1 | 501050000 | Flow rate : 2 LPS Each pumpHead : 10 Mts Solid Handling : 30 - 38 MMNos. of Pumps : 2 ( 1 working + 1 standby )Location : Plumbing plant room & HVAC Plant roomPurpose : Plant Room DrainageMOC : Stainless steel | [8 empty] | Sets | 2 | 86000 | 0 | 86000 | 4300 | 0 | 90300 | 10290 | 1271.844 | 0 | 11561.844 | 180600 | 23123.688 | 203723.688
2.3.2 | 501050000 | Flow rate : 5 LPS Each pumpHead : 25 Mts Solid Handling : 30 - 38 MMNos. of Pumps : 2 ( 1 working + 1 standby )Location : Car parking areaPurpose : Car parking area drainageMOC : Stainless steel | [8 empty] | Set | 1 | 115022 | 0 | 115022 | 5751.1 | 0 | 120773.1 | 10290 | 1271.844 | 0 | 11561.844 | 120773.1 | 11561.844 | 132334.944
2.3.3 | 501050000 | Flow rate : 2 LPSHead : 10 Mts Solid Handling : 30 - 38 MMNos. of Pumps : 2 ( 1 working + 1 standby )Location : In hot water plantroomPurpose : Boiler blow down dischargeMOC : CI body / impeller & shaft | [8 empty] | Set | 1 | 131752 | 0 | 131752 | 6587.6 | 0 | 138339.6 | 10290 | 1271.844 | 0 | 11561.844 | 138339.6 | 11561.844 | 149901.444
4 | 501050000 | PIPING, VALVES & ACCESSORIES | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4.1 | 501050000 | Providing, fixing, jointing and testing in position the C.I. class LA pipe for (Sump Riser) confirming to IS:1536. Cut to required lengths including painting and all necessary fittings and specials such as bends, junctions, offsets, access pieces (plain or door) fixing at wall / ceiling level supported by galvanised steel clamps & hangers etc. Making proper connection to the satisfaction of the Project Manager and making good the same after pipe have been duly laid and testing complete. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4.1.1 | 501050000 | 80 mm dia (Ty-ton joint for pressure pumping) | [8 empty] | RM | 0 | 1502 | 0 | 1502 | 75.1 | 0 | 1577.1 | 336 | 41.5296 | 0 | 377.5296 | 0 | 0 | 0
4.1.2 | 501050000 | 100 mm dia (Ty-ton joint for pressure pumping) | [8 empty] | RM | 0 | 1865 | 0 | 1865 | 93.25 | 0 | 1958.25 | 420 | 51.912 | 0 | 471.912 | 0 | 0 | 0
5 | 501050000 | Providing and fixing in position Class C M.S. Galvanised pipe work for all pump suction / discharge line with common header complete with all fittings like elbow, tee, reducer, flange, union etc. conforming to IS:1239 (Part 1) for pipes and IS : 1879 (Part 1 to 10) for fittings including fixing in wall / ceiling / floor level, supported by galvanized clamps, hangers, vertical pipe support etc. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.1 | 501050000 | 65 mm dias | [8 empty] | RM | 10 | 770 | 0 | 770 | 38.5 | 0 | 808.5 | 267 | 33.0012 | 0 | 300.0012 | 8085 | 3000.012 | 11085.012
5.2 | 501050000 | 80 mm dias | [8 empty] | RM | 10 | 930 | 0 | 930 | 46.5 | 0 | 976.5 | 329 | 40.6644 | 0 | 369.6644 | 9765 | 3696.644 | 13461.644
5.3 | 501050000 | 100 mm dia | [8 empty] | RM | 20 | 1400 | 0 | 1400 | 70 | 0 | 1470 | 412 | 50.9232 | 0 | 462.9232 | 29400 | 9258.464 | 38658.464
5.4 | 501050000 | 150 mm dias | [8 empty] | RM | 20 | 1988 | 0 | 1988 | 99.4 | 0 | 2087.4 | 617 | 76.2612 | 0 | 693.2612 | 41748 | 13865.224 | 55613.224
5.5 | 501050000 | 200 mm dias | [8 empty] | RM | 20 | 2058 | 0 | 2058 | 102.9 | 0 | 2160.9 | 627 | 77.4972 | 0 | 704.4972 | 43218 | 14089.944 | 57307.944
6 | 501050000 | Providing & fixing M.S. (Heavy Class) header complete for submersiable pump discharge header comprising of flanges, unions, check nuts, Tee, Elbow etc. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6.1 | 501050000 | 80 mm dia | [8 empty] | RM | 0 | 780 | 0 | 780 | 39 | 0 | 819 | 336 | 41.5296 | 0 | 377.5296 | 0 | 0 | 0
6.2 | 501050000 | 100 mm dia | [8 empty] | RM | 85 | 1112 | 0 | 1112 | 55.6 | 0 | 1167.6 | 412 | 50.9232 | 0 | 462.9232 | 99246 | 39348.472 | 138594.472
7 | 501050000 | Providing and fixing C.I. Butterfly valve (Body : Grey Cast Iron, shaft : SS, Disc : SG Iron (nickel plated), Liner : HT - EPDM) of approved make with flange, washer, nuts & bolts and PN 10 pressure rating including rubber gasket & painting complete. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7.1 | 501050000 | 40 mm dia | [8 empty] | No. | 0 | 1720 | 0 | 1720 | 86 | 0 | 1806 | 210 | 25.956 | 0 | 235.956 | 0 | 0 | 0
7.2 | 501050000 | 50 mm dia | [8 empty] | No. | 0 | 2800 | 0 | 2800 | 140 | 0 | 2940 | 263 | 32.5068 | 0 | 295.5068 | 0 | 0 | 0
7.3 | 501050000 | 65 asas dia | [8 empty] | No. | 12 | 3047 | 0 | 3047 | 152.35 | 0 | 3199.35 | 334 | 41.2824 | 0 | 375.2824 | 38392.2 | 4503.3888 | 42895.5888
7.4 | 501050000 | 80 asas dia | [8 empty] | No. | 12 | 3626 | 0 | 3626 | 181.3 | 0 | 3807.3 | 412 | 50.9232 | 0 | 462.9232 | 45687.6 | 5555.0784 | 51242.6784
7.5 | 501050000 | 100 mm d ia | [8 empty] | No. | 2 | 4753 | 0 | 4753 | 237.65 | 0 | 4990.65 | 515 | 63.654 | 0 | 578.654 | 9981.3 | 1157.308 | 11138.608
7.6 | 501050000 | 150 mm dia | [8 empty] | No. | 5 | 7056 | 0 | 7056 | 352.8 | 0 | 7408.8 | 772 | 95.4192 | 0 | 867.4192 | 37044 | 4337.096 | 41381.096
7.7 | 501050000 | 200 mm dia | [8 empty] | No. | 0 | 14000 | 0 | 14000 | 700 | 0 | 14700 | 1050 | 129.78 | 0 | 1179.78 | 0 | 0 | 0
8 | 501050000 | Providing & fixing C.I. wafer type check valve of PN 1.6 rating, including rubber gasket, flanges, union, nuts, bolts, washers & painting complete as required. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8.1 | 501050000 | 50 mm dia | [8 empty] | No. | 6 | 3136 | 0 | 3136 | 156.8 | 0 | 3292.8 | 257 | 31.7652 | 0 | 288.7652 | 19756.8 | 1732.5912 | 21489.3912
8.2 | 501050000 | 65 mm dia | [8 empty] | No. | 6 | 3626 | 0 | 3626 | 181.3 | 0 | 3807.3 | 334 | 41.2824 | 0 | 375.2824 | 22843.8 | 2251.6944 | 25095.4944
8.3 | 501050000 | 80 mm dia | [8 empty] | No. | 5 | 4331 | 0 | 4331 | 216.55 | 0 | 4547.55 | 412 | 50.9232 | 0 | 462.9232 | 22737.75 | 2314.616 | 25052.366
8.4 | 501050000 | 100 mm dia | [8 empty] | No. | 0 | 6615 | 0 | 6615 | 330.75 | 0 | 6945.75 | 525 | 64.89 | 0 | 589.89 | 0 | 0 | 0
9 | 501050000 | Providing & fixing NRV (B-System with Ball) for Sewage Pump application. The NRV shall have synthetic resin ball (Self cleaning type) in CI casing & NBR seal (Make : Danfoss) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.1 | 501050000 | 100 mm dia | [8 empty] | Nos. | 0 | 8850 | 0 | 8850 | 442.5 | 0 | 9292.5 | 525 | 64.89 | 0 | 589.89 | 0 | 0 | 0
10 | 501050000 | Providing & Fixing dual flange CI Y Strainer (flanged) with stainless steel fine wire mesh perforated sheet basket with necessary flange / unions, nuts, bolts and wahsers complete as required. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10.1 | 501050000 | 65 mm dia | [8 empty] | No. | 0 | 3732 | 0 | 3732 | 186.6 | 0 | 3918.6 | 341 | 42.1476 | 0 | 383.1476 | 0 | 0 | 0
10.2 | 501050000 | 80 mm dia | [8 empty] | No. | 0 | 4542 | 0 | 4542 | 227.1 | 0 | 4769.1 | 420 | 51.912 | 0 | 471.912 | 0 | 0 | 0
10.3 | 501050000 | 100 mm dia | [8 empty] | No. | 0 | 6936 | 0 | 6936 | 346.8 | 0 | 7282.8 | 525 | 64.89 | 0 | 589.89 | 0 | 0 | 0
10.4 | 501050000 | 150 mm dia | [8 empty] | No. | 2 | 12559 | 0 | 12559 | 627.95 | 0 | 13186.95 | 772 | 95.4192 | 0 | 867.4192 | 26373.9 | 1734.8384 | 28108.7384
11 | 501050000 | Providing, testing and commissioning of 100 mm dia dial type pressure gauge with pressure scale of 0 to 15 Kg / sqm. Provision of isolation ball valve shall also be included in the cost. | [8 empty] | No. | 4 | 1764 | 0 | 1764 | 88.2 | 0 | 1852.2 | 155 | 19.158 | 0 | 174.158 | 7408.8 | 696.632 | 8105.432
H | 502000000 | FIRE PROTECTION SYSTEM: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.1 | 502010000 | Supply, installation, testing and commissioning of electrically driven high pressure centrifugal fire hydrant / sprinkler pump, suitable for automatic operation consisting of the following: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
a. | 502010000 | Horizontal end suction / high pressure single stage, centrifugal pump, suitable for operation on 415 volts ± 6%, 3 phase, 50 HZ A.C supply. The installation shall be complete with flexible coupling and coupling guard as required. Fire pump shall have C.I. casing, CS diffusers, bronze impeller (hard finished and dynamically balanced) and S.S. (304) Shaft with mechanical seal, capable for delivering 47.5 LPS at outlet head of 120 mts to ensure a minimum pressure of 3.5 Kg/Sqcm at the farthest or topmost hydrant / sprinkler. The installation shall be complete with necessary pressure gauge with gun metal shut off cock on delivery side. (The pump should be tested for bench mark at factory and shall be gotten approved by the Local fire Authority).Pump shall be capable of furnishing not less than 150% of rated capacity at a head of not less than 65% of the rated head. The shut off head shall not exceed 120% of rated head. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
b. | 502010000 | Squirrel cage induction motor, TEFC type suitable for operation on 415 volts, 3 phase 50 HZ A.C supply, for the above pump with synchronous speed of 2900 RPM, conforming to IP 55 protection & class F insulation. The motor shall conform to IS 325-1978 (up to date) with flexible coupling and coupling guard, complete as required. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
c. | 502010000 | Common base plate for (a) and (b) from M.S. Channel for required size. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
d. | 502010000 | Suitable cement concrete foundation with cement concrete plaster (design and drawing to be provided by the Contractor while the foundation will be done by others) complete with anti-vibration arrangement of cushy foot mountings. | [8 empty] | Set | 2 | 447770 | 0 | 447770 | 22388.5 | 0 | 470158.5 | 25725 | 3179.61 | 0 | 28904.61 | 940317 | 57809.22 | 998126.22
e. | 502010000 | Quote for UL -FM approved fire pumps as optional | [8 empty] | Nil | 0 | 3336000 | 0 | 3336000 | 166800 | 0 | 3502800 | 47250 | 5840.1 | 0 | 53090.1 | 0 | 0 | 0
f. | 502010000 | Pumps selection shall be on the Middle of the curve or on LHS. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.2 | 502010000 | Supply, installation, testing and commissioning of Diesel Engine driven fire pump suitable for automatic operation comprising of the following and conforming to BS 649/IS 10002 all amended upto date. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
a. | 502010000 | Horizontal, split casing, high pressure singel/ multistage centrifugal pump, The installation shall be complete with flexible coupling and coupling guard as required. Fire pump shall have C.I. casing, CS diffusers, bronze impeller (hard finished and dynamically balanced) and SS (304) shaft with mechanical seal, capable for delivering 47.5 LPS at outlet head of 120 mts to ensure a minimum pressure of 3.5 Kg/Sqcm at the farthest or topmost hydrant / sprinkler. The installation shall be complete with necessary pressure gauge with gun metal shut off cock on delivery side (The pump should be tested for bench mark at factory and shall be gotten approved by the Local fire Authority).Pump shall be capable of furnishing not less than 150% of rated capacity at a head of not less than 65% of the rated head. The shut off head shall not exceed 120% of rated head. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
b. | 502010000 | Heat exchanger cooled (secondary cooling) diesel engine of speed 1500 RPM suitable for the above pump with automatic starting mechanism and other accessories including fuel tank (fabricated from 3mm MS sheet, painted with two coats of synthetic enamel paint over a coat of primer) of capacity adequate to sustain pump operation for 8 hours continuous working. The tank shall be fitted with Magnetic oil level indicator, MH with cover, drain valve, air vent including structural supports (painted with approved shade), 2 Nos. x 12 volt battery with battery charger, heat exchanger with necessary piping connections & fittings, flexible coupling, coupling guard & exhaust pipe connection complete as required. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
c. | 502010000 | Common base plate for (a) and (b) from M.S. channel of required size. | [8 empty] | Set | 1 | 1025535 | 0 | 1025535 | 51276.75 | 0 | 1076811.75 | 36015 | 4451.454 | 0 | 40466.454 | 1076811.75 | 40466.454 | 1117278.204
d. | 502010000 | Suitable cement concrete foundation with plaster, (design and drawing to be provided by the Contractor while the foundation will be done by others) complete with antivibration arrangement of cushy foot mountings. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
e. | 502010000 | Quote for UL -FM approved fire pumps as optional | [8 empty] | Nil | 0 | 4346000 | 0 | 4346000 | 217300 | 0 | 4563300 | 63000 | 7786.8 | 0 | 70786.8 | 0 | 0 | 0
f. | 502010000 | Pumps selection shall be on the Middle of the curve or on LHS. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
g | 502010000 | Engine BHP tobe 30% higher than the pump shaft BHP. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
h | 502010000 | Engine shall be water cooled with prefitted circulation pump instead of radiators and the circulated water shall go to the Fire tank. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.3 | 502010000 | Supply, installation, testing and commissioning of jockey pump (pressurisation pump) comprising of the following: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
a. | 502010000 | Vertical Multistage centrifugal pump, suitable for operation on 415 volts ± 6%, 3 phase, 50 HZ A.C supply. The installation shall be complete with Flexible coupling and coupling guard, complete as required. Jockey pump shall be of stainless steel construction.The pump head and base shall be CI construction and impellers, diffusers, shaft sleeve, seal bush & pump shaft shall be in SS 304 material. The pump shall be provided with mechanical seal The system shall be complete with necessary pressure gauge with gun metal shut off cock on delivery side (The pump should meet the condition and shall be gotten approved by the Local fire Authority). | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
b. | 502010000 | Squirrel cage induction motor TEFC type for operation on 415 V, 3 phase 50 HZ AC supply for the above pump with a synchronous speed of 2900 R.P.M. with flexible coupling and coupling guard etc. as required. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
c. | 502010000 | Common base plate for (a) and (b) from M.S. channel as required size. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
d. | 502010000 | Suitable cement concrete foundation with plaster, (design and drawing to be provided by the Contractor while the foundation will be done by others) complete with Antivibration arrangement of cushy foot mounting. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
e. | 502010000 | Quote for UL -FM approved fire pumps as optional | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
f. | 502010000 | Pumps selection shall be on the Middle of the curve or on LHS.For pump defined above & of duty as follows : | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.3.1 | 502010000 | Hydrant SystemFlow : 180 LPMHead : 120 mts | [8 empty] | Set | 1 | 90357 | 0 | 90357 | 4517.85 | 0 | 94874.85 | 15435 | 1907.766 | 0 | 17342.766 | 94874.85 | 17342.766 | 112217.616
1.3.2 | 502010000 | Sprinkler SystemFlow : 180 LPMHead : 120 mts | [8 empty] | Set | 1 | 90357 | 0 | 90357 | 4517.85 | 0 | 94874.85 | 15435 | 1907.766 | 0 | 17342.766 | 94874.85 | 17342.766 | 112217.616
1.4 | 502010000 | Supply, installation, testing and commissioning of terrace fire pump comprising of the following: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
a. | 502010000 | Horizontal mono-block centrifugal pump, suitable for operation on 415 volts ± 6%, 3 phase, 50 HZ A.C supply.The pump casing shall be CI, shaft shall be CS & impeller / shaft sleeve / casing wearing ring shall be bronze. The system shall be complete with necessary pressure gauge with gun metal shut off cock on delivery side. (The pump should meet the condition and shall be gotten approved by the Local fire Authority). | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
b. | 502010000 | Squirrel cage induction motor TEFC type for operation on 415 V, 3 phase 50 HZ AC supply for the above pump with speed of 2900 R.P.M. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
c. | 502010000 | Suitable cement concrete foundation with plaster, (design and drawing to be provided by the Contractor while the foundation will be done by others) complete with Antivibration arrangement of cushy foot mounting. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
d. | 502010000 | For pump defined above & of duty as follows : | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.4.1 | 502010000 | Flow : 900 LPM | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.4.2 | 502010000 | Head :35 mts | [8 empty] | Set | 1 | 44025 | 0 | 44025 | 2201.25 | 0 | 46226.25 | 10290 | 1271.844 | 0 | 11561.844 | 46226.25 | 11561.844 | 57788.094
1.5 | 502010000 | Providing & fixing MS Class C diesel engine exhaust pipe (including all fittings, clamps, steel support) of suitable dia for the engine. The pipe shall be provided with 12 mm thick supercera ceramic fibre rope. | [8 empty] | RM | 20 | 1470 | 0 | 1470 | 73.5 | 0 | 1543.5 | 494 | 61.0584 | 0 | 555.0584 | 30870 | 11101.168 | 41971.168
1.6 | 502010000 | Providing, fixing, testing and commissioning of precharged air vessel (size 450 mm dia & 2000 mm height) for pressurization of hydrant / sprinkler system complete with adequate pressure switches (as per design / requirement) with valves to operate as per operating sequences including 25 mm dia drain valve, air release valve with stop cock on the top, minimum 50 mm dia inlet with isolating valve duly painted from inside and outside with two coats of synthetic enamel paint over a coat of primer complete as required. (Vessel should be suitable for rated working pressure. The air vessel shall be without diaphragm). | [8 empty] | Set | 2 | 40180 | 0 | 40180 | 2009 | 0 | 42189 | 2058 | 254.3688 | 0 | 2312.3688 | 84378 | 4624.7376 | 89002.7376
1.7 | 502010000 | Providing, fixing, testing & commissioning of MS air cushion tank on top of each riser fabricated from 6mm thick MS plate, 200 mm in diameter and 1.2 m in height with dished ends fabricated from 6 mm thick MS plate with Air release valve & stop cock, flanged inlet connection with all accessories as required and conforming to IS 4736-1968. (The cushion tank should be suitable for rated working pressure. | [8 empty] | Set | 3 | 15484 | 0 | 15484 | 774.2 | 0 | 16258.2 | 1286 | 158.9496 | 0 | 1444.9496 | 48774.6 | 4334.8488 | 53109.4488
1.8 | 502010000 | Providing & fixing dial type (100 mm) pressure gauge with isolation ball valve suitable for working pressure of 250 PSI. Cost shall be inclusive of providing any short pieces, nipples, elbows etc as required. | [8 empty] | Nos | 3 | 1960 | 0 | 1960 | 98 | 0 | 2058 | 257 | 31.7652 | 0 | 288.7652 | 6174 | 866.2956 | 7040.2956
1.9 | 502010000 | Supply, installation, testing and commissioning of sight tube (of 3.5 to 4 m length) with isolation valve at top / bottom, demarcation on tube for making the installation of level indication on the RCC water tank complete. | [8 empty] | Nos | 2 | 9310 | 0 | 9310 | 465.5 | 0 | 9775.5 | 515 | 63.654 | 0 | 578.654 | 19551 | 1157.308 | 20708.308
Note: i. | 502010000 | Contractor shall include in his rates for providing level controllers, pressure switches, wiring, cabling from level controller / pressure switch to panel etc. complete as required to operate the system automatic/manual. Pump shall be protected against running dry. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 502020000 | Hydrants, Piping & Accessories: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.1 | 502020000 | Providing, laying, jointing, testing and commissioning of following sizes of pipes conforming to IS-1239 with all accessories like all fittings (standard MS fitting with welded joint shall be used on the pipes) including tees, elbows, reducers, union, flanges, rubber gaskets, GI nuts bolts, washer including supporting/fixing the pipe on floor / wall /ceiling with clamps, hangers (using anchor fastners) as per specification. UPVC pipe sleeve of suitable higher size shall be provided wherever the pipes are crossing the walls/floors and sealing the sleeves with glass wool in between & fire sealent compound at either end all as per Project Managers / Consultants requirements including cutting holes and chases in brick, R.C.C work and making good the same to original conditions complete in all respects. All hangers, clamps, brackets etc. shall be of galvanized iron unless specified otherwire and then supply of the same shall also be included for rates under this head.. Welding of any kind on the galvanized support / hanger shall not be permitted. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.1.1 | 502020000 | For wet riser System - M.S.C Heavy class pipe | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.1.2 | 502020000 | 150 mm dia | [8 empty] | RM | 770 | 1675 | 0 | 1675 | 83.75 | 0 | 1758.75 | 494 | 61.0584 | 0 | 555.0584 | 1354237.5 | 427394.968 | 1781632.468
2.1.3 | 502020000 | 250 mm diat | [8 empty] | RM | 5 | 3332 | 0 | 3332 | 166.6 | 0 | 3498.6 | 823 | 101.7228 | 0 | 924.7228 | 17493 | 4623.614 | 22116.614
2.1.4 | 502020000 | 300 mm diau | [8 empty] | RM | 10 | 3332 | 0 | 3332 | 166.6 | 0 | 3498.6 | 875 | 108.15 | 0 | 983.15 | 34986 | 9831.5 | 44817.5
2.2 | 502020000 | Providing two coats of synthetic enamel paint of approved shade over a coat of primer. Prior to application of primer the surface should be cleaned for any dirt, rusts, rough substance etc. Including painting of legends both direction arrow as per the approval of the Project Manager | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.2.1 | 502020000 | 80 mm dia | [8 empty] | RM | 25 | 29 | 0 | 29 | 1.45 | 0 | 30.45 | 15 | 1.854 | 0 | 16.854 | 761.25 | 421.35 | 1182.6
2.2.2 | 502020000 | 100 mm diai | [8 empty] | RM | 50 | 39 | 0 | 39 | 1.95 | 0 | 40.95 | 20 | 2.472 | 0 | 22.472 | 2047.5 | 1123.6 | 3171.1
2.2.3 | 502020000 | 150 mm diao | [8 empty] | RM | 825 | 58 | 0 | 58 | 2.9 | 0 | 60.9 | 31 | 3.8316 | 0 | 34.8316 | 50242.5 | 28736.07 | 78978.57
2.2.4 | 502020000 | 250 mm diap | [8 empty] | RM | 5 | 98 | 0 | 98 | 4.9 | 0 | 102.9 | 51 | 6.3036 | 0 | 57.3036 | 514.5 | 286.518 | 801.018
2.2.5 | 502020000 | 300 mm dial | [8 empty] | RM | 10 | 93 | 0 | 93 | 4.65 | 0 | 97.65 | 61 | 7.5396 | 0 | 68.5396 | 976.5 | 685.396 | 1661.896
2.3 | 502020000 | Providing, laying, jointing and testing in trenches the following sizes of MS class C (heavy class) pipes conforming to IS:1239 with accessories like fittings including tees, elbows, reducers, flanges, rubber gaskets, G.I. nuts, bolts and washers including excavation in all kind of soil, refilling, ramming, shoring, removing the excavated surplus material, providing adequate support to the pipe and making good the same complete as required. Rate shall include for dewatering necessary to execute the work. The pipe shall not be less than 1.0 m below ground level at any point. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.3.1 | 502020000 | 80 mm diak | [8 empty] | RM | 25 | 839 | 0 | 839 | 41.95 | 0 | 880.95 | 277 | 34.2372 | 0 | 311.2372 | 22023.75 | 7780.93 | 29804.68
2.3.2 | 502020000 | 100 mm dim | [8 empty] | RM | 30 | 1217 | 0 | 1217 | 60.85 | 0 | 1277.85 | 370 | 45.732 | 0 | 415.732 | 38335.5 | 12471.96 | 50807.46
2.3.3 | 502020000 | 150 mm a | [8 empty] | RM | 350 | 1795 | 0 | 1795 | 89.75 | 0 | 1884.75 | 556 | 68.7216 | 0 | 624.7216 | 659662.5 | 218652.56 | 878315.06
2.4 | 502020000 | Providing protection to embedded M.S. pipes and fittings by applying protective primer (@ 100 gm/sqm) thereafter wrapping 4 mm thick protection coating by thermo fusion process. Overlap shall be maintained at 15 mm. The application process shall be strictly according to manufacturers specification. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.4.1 | 502020000 | 80 mm diaam | [8 empty] | RM | 15 | 106 | 0 | 106 | 5.3 | 0 | 111.3 | 30 | 3.708 | 0 | 33.708 | 1669.5 | 505.62 | 2175.12
2.4.2 | 502020000 | 100mm | [8 empty] | RM | 30 | 14 | 0 | 14 | 0.7 | 0 | 14.7 | 41 | 5.0676 | 0 | 46.0676 | 441 | 1382.028 | 1823.028
2.4.3 | 502020000 | 150mm | [8 empty] | RM | 350 | 211 | 0 | 211 | 10.55 | 0 | 221.55 | 61 | 7.5396 | 0 | 68.5396 | 77542.5 | 23988.86 | 101531.36
2.5 | 502020000 | Providing & fixing of butterfly valve (PN 16) with flanges, nut bolts, gaskets and necessary pad locking arrangement complete required. | [8 empty] | Nil | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.5.1 | 502020000 | 65 mm dia m | [8 empty] | No. | 3 | 3656 | 0 | 3656 | 182.8 | 0 | 3838.8 | 334 | 41.2824 | 0 | 375.2824 | 11516.4 | 1125.8472 | 12642.2472
2.5.2 | 502020000 | 80 mm dia m | [8 empty] | No. | 3 | 4351 | 0 | 4351 | 217.55 | 0 | 4568.55 | 412 | 50.9232 | 0 | 462.9232 | 13705.65 | 1388.7696 | 15094.4196
2.5.3 | 502020000 | 100 mm dia m | [8 empty] | No. | 5 | 5704 | 0 | 5704 | 285.2 | 0 | 5989.2 | 515 | 63.654 | 0 | 578.654 | 29946 | 2893.27 | 32839.27
2.5.4 | 502020000 | 150 mm dia m | [8 empty] | No. | 15 | 8467 | 0 | 8467 | 423.35 | 0 | 8890.35 | 772 | 95.4192 | 0 | 867.4192 | 133355.25 | 13011.288 | 146366.538
2.5.5 | 502020000 | 200 mm dia | [8 empty] | No. | 4 | 16464 | 0 | 16464 | 823.2 | 0 | 17287.2 | 900 | 111.24 | 0 | 1011.24 | 69148.8 | 4044.96 | 73193.76
2.5.6 | 502020000 | 250 mm dia m | [8 empty] | No. | 2 | 26460 | 0 | 26460 | 1323 | 0 | 27783 | 1029 | 127.1844 | 0 | 1156.1844 | 55566 | 2312.3688 | 57878.3688
2.6 | 502020000 | Providing and fixing tamper switch on butterfly valve / sluice valve / isolation valve for remote mointing of the valve open / close position. The tamper switch shall be provided with potential free contact with 2 nos. NONC. The valve shall also be provided with manual lock & chain arrangement. | [8 empty] | Set | 0 | 5000 | 0 | 5000 | 250 | 0 | 5250 | 263 | 32.5068 | 0 | 295.5068 | 0 | 0 | 0
2.7 | 502020000 | Providing & fixing C.I. wafer type check valve of rating PN 16 rating including rubber gasket, flanges, union, nuts, bolts, washers & painting complete as required. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.7.1 | 502020000 | 65mm | [8 empty] | No | 2 | 3626 | 0 | 3626 | 181.3 | 0 | 3807.3 | 334 | 41.2824 | 0 | 375.2824 | 7614.6 | 750.5648 | 8365.1648
2.7.2 | 502020000 | 80 mm dia | [8 empty] | No. | 0 | 4420 | 0 | 4420 | 221 | 0 | 4641 | 420 | 51.912 | 0 | 471.912 | 0 | 0 | 0
2.7.3 | 502020000 | 100 mm | [8 empty] | No. | 1 | 5635 | 0 | 5635 | 281.75 | 0 | 5916.75 | 515 | 63.654 | 0 | 578.654 | 5916.75 | 578.654 | 6495.404
2.7.4 | 502020000 | 150mm dia m | [8 empty] | No. | 3 | 7722 | 0 | 7722 | 386.1 | 0 | 8108.1 | 618 | 76.3848 | 0 | 694.3848 | 24324.3 | 2083.1544 | 26407.4544
2.7.5 | 502020000 | 200 mmd | [8 empty] | No. | 1 | 14210 | 0 | 14210 | 710.5 | 0 | 14920.5 | 823 | 101.7228 | 0 | 924.7228 | 14920.5 | 924.7228 | 15845.2228
2.8 | 502020000 | Providing, fixing and commissioning of spring loaded relief valve suitable for pressure of 15 Kg / sq.cm including flanges, nuts, bolts, washers etc. complete as required. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.8.1 | 502020000 | 80 mmd | [8 empty] | No. | 2 | 16587 | 0 | 16587 | 829.35 | 0 | 17416.35 | 515 | 63.654 | 0 | 578.654 | 34832.7 | 1157.308 | 35990.008
2.9 | 502020000 | Providing & fixing heavy duty double flanged flexicon rubber expansion joint (suitable for system test pressure) of standard length as per manufacturers specs including rubber gaskets, flanges, nuts, bolts and washers complete as required. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.9.1 | 502020000 | 65 mmd | [8 empty] | No. | 2 | 3733 | 0 | 3733 | 186.65 | 0 | 3919.65 | 257 | 31.7652 | 0 | 288.7652 | 7839.3 | 577.5304 | 8416.8304
2.9.2 | 502020000 | 80 mm di\ | [8 empty] | No. | 2 | 4395 | 0 | 4395 | 219.75 | 0 | 4614.75 | 309 | 38.1924 | 0 | 347.1924 | 9229.5 | 694.3848 | 9923.8848
2.9.3 | 502020000 | 100 m,m | [8 empty] | No. | 3 | 5576 | 0 | 5576 | 278.8 | 0 | 5854.8 | 412 | 50.9232 | 0 | 462.9232 | 17564.4 | 1388.7696 | 18953.1696
2.9.4 | 502020000 | 150 mm | [8 empty] | No. | 3 | 6517 | 0 | 6517 | 325.85 | 0 | 6842.85 | 618 | 76.3848 | 0 | 694.3848 | 20528.55 | 2083.1544 | 22611.7044
2.9.5 | 502020000 | 200 mm diam | [8 empty] | No. | 3 | 7315 | 0 | 7315 | 365.75 | 0 | 7680.75 | 823 | 101.7228 | 0 | 924.7228 | 23042.25 | 2774.1684 | 25816.4184
2.1 | 502020000 | Providing and fixing C.I.Y strainer with bronze perforated sheet basket including rubber gasket, flanges, nuts, bolts and washers, complete as required. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.10.1 | 502020000 | 65 mm diam | [8 empty] | No. | 2 | 3439 | 0 | 3439 | 171.95 | 0 | 3610.95 | 257 | 31.7652 | 0 | 288.7652 | 7221.9 | 577.5304 | 7799.4304
2.10.2 | 502020000 | 100 mm diam | [8 empty] | No. | 1 | 6428 | 0 | 6428 | 321.4 | 0 | 6749.4 | 412 | 50.9232 | 0 | 462.9232 | 6749.4 | 462.9232 | 7212.3232
2.10.3 | 502020000 | 150 mm diaa | [8 empty] | No. | 1 | 11799 | 0 | 11799 | 589.95 | 0 | 12388.95 | 618 | 76.3848 | 0 | 694.3848 | 12388.95 | 694.3848 | 13083.3348
2.10.4 | 502020000 | 200 mm diaa | [8 empty] | No. | 3 | 27910 | 0 | 27910 | 1395.5 | 0 | 29305.5 | 823 | 101.7228 | 0 | 924.7228 | 87916.5 | 2774.1684 | 90690.6684
2.11 | 502020000 | Providing and Fixing non rising sprindle type sluice valve PN 16 rating of following dia complete with flanges, nuts, bolts etc. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.11.1 | 502020000 | 150 mmd | [8 empty] | Nos. | 3 | 19560 | 0 | 19560 | 978 | 0 | 20538 | 618 | 76.3848 | 0 | 694.3848 | 61614 | 2083.1544 | 63697.1544
2.11.2 | 502020000 | 250 mm dia | [8 empty] | Nos. | 0 | 69800 | 0 | 69800 | 3490 | 0 | 73290 | 1050 | 129.78 | 0 | 1179.78 | 0 | 0 | 0
2.12 | 502020000 | Providing & fixing gun metal fire hydrant double landing valve with 100 mm N.B. flanged inlet, brass spindle controlled 63 mm dia female instantaneous outlet type. G.M. coupling, blank cap, chain, twist release type lug & all accessories Conforming to IS:5290. Including fixing with anchor fastner and flanged tapping from wet riser and providing pressure gauge with gun metal ball valve complete as required. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.12.1 | 502020000 | Double head landing valve | [8 empty] | Nos. | 50 | 16500 | 0 | 16500 | 825 | 0 | 17325 | 412 | 50.9232 | 0 | 462.9232 | 866250 | 23146.16 | 889396.16
2.12.2 | 502020000 | Single head landing valve | [8 empty] | Nos. | 9 | 7920 | 0 | 7920 | 396 | 0 | 8316 | 309 | 38.1924 | 0 | 347.1924 | 74844 | 3124.7316 | 77968.7316
2.13 | 502020000 | Providing & fixing gun metal controlled pressure hydrant valve (Class F Hose pressure regulator) with 2 1/2 " instantaneous female coupling to BS: 336. Inlet pressure range 4.8 to 20.7 bar; outlet pressure range 4.1 - 8.3 bar. The pressure regulator shall incorporate spring loaded balanced PRV combined with a hydrant slop valve. Cost shall be inclusive of fixing with anchor fastner and flanged tapping from wet riser and providing pressure gauge with gun metal ball valve complete as required. | [8 empty] | Nos. | 0 | 20300 | 0 | 20300 | 1015 | 0 | 21315 | 788 | 97.3968 | 0 | 885.3968 | 0 | 0 | 0
2.14 | 502020000 | Providing & fixing swinging type First Aid hose reel in red colour drum with 36 mts long and 20 mm dia heavy duty rubber water hose, 20 mm dia gate valve stop cock, (IS:778, class - II) terminating with G.M. coupling & nozzle of 6mm outlet with shut off valve confirming to IS 8090 - 1976 complete with MS socket for tap-off, drum and brackets (including painting) for fixing on wall with anchor fastner, bolts & nuts conforming to IS:884-1985 (Reaffirmed 2000) complete as required. | [8 empty] | No. | 50 | 7815 | 0 | 7815 | 390.75 | 0 | 8205.75 | 515 | 63.654 | 0 | 578.654 | 410287.5 | 28932.7 | 439220.2
2.15 | 502020000 | Providing & fixing non-percolating rubber reinforced lined fire hose pipe (as per IS : 636) type-B of 63 mm dia and length as described below. The hose shall be rated for brust pressure of 35.7 Kg/sqcm. Hose shall be complete with ISI marked brass male & female coupling (IS:903) bound & rivetted to hose pipe with copper rivets & 1.5 mm copper wire (Location : Internal fire hydrant) (with S.S. Coupling.) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.15.1 | 502020000 | 15 m length | [8 empty] | Nos. | 100 | 4700 | 0 | 4700 | 235 | 0 | 4935 | 128 | 15.8208 | 0 | 143.8208 | 493500 | 14382.08 | 507882.08
2.16 | 502020000 | Providing & fixing controlled percolation fire hose pipe (as per IS:8423) of 63 mm dia and 15 meter length rated for brust pressure of 35.7 Kg/sqcm. The hose shall be tested for flame resistance test in accordance to IS:8423. Hose shall be complete with ISI marked brass male & female coupling (IS:903) bound & riveted to hose pipe with copper rivets & 1.5 mm copper wire (Location : External fire hydrant) ( with S.S. couplings) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.16.1 | 502020000 | 15 m lengt | [8 empty] | Nos. | 18 | 5310 | 0 | 5310 | 265.5 | 0 | 5575.5 | 154 | 19.0344 | 0 | 173.0344 | 100359 | 3114.6192 | 103473.6192
2.17 | 502020000 | Providing and Fixing 63 mm dia instantaneous pattern branch short Stainless Steel pipe, 20 mm dia nozzle conforming to IS 903, suitable for inter connection to hose pipe coupling complete as required. | [8 empty] | Nos. | 109 | 2468 | 0 | 2468 | 123.4 | 0 | 2591.4 | 103 | 12.7308 | 0 | 115.7308 | 282462.6 | 12614.6572 | 295077.2572
2.18 | 502020000 | Providing and fixing standard firemans axe with heavy rubber handle. | [8 empty] | Nos. | 30 | 1142 | 0 | 1142 | 57.1 | 0 | 1199.1 | 103 | 12.7308 | 0 | 115.7308 | 35973 | 3471.924 | 39444.924
2.19 | 502020000 | Providing and fixing weather proof lockable cabinet of size not less than 0.9 x 0.6 x 0.45 mtr made out of SS304 sheet of 16 gauge thickness having central opening and 4 mm thick glazed glass doors (Two nos.) suitably marked on the outside with the letters "FIRE HOSE" including necessary locking arrangement and shall be painted with one coat of primer and two coats of synthetic enamel paint of approved shade.The cabinet shall be suitable to accommodate 2 nos. or 4 nos 15 mtr long Hose pipe & 2 Nos branch pipe nozzle. It shall be mounted on raised Brick platform complete as required.(Cost shall be inclusive of providing break glass box containing key for the cabinet along with hammer). | [8 empty] | Nos. | 9 | 4474 | 0 | 4474 | 223.7 | 0 | 4697.7 | 360 | 44.496 | 0 | 404.496 | 42279.3 | 3640.464 | 45919.764
2.2 | 502020000 | Providing & fixing lockable indoor type fire hose cabinet frames fabricated from 40 x 40 x 5 angle iron sections and 16 gauge MS sheet with full front glass door and locking arrangement, suitable to accommodate landing valves, 2 nos. 15 m long hoses, first-aid hose reel and branch pipe nozzle & fire mans axe. The cabinet frame shall be painted with one coat of primer and two or more coats of synthetic enamel paint of approved make and shade of as required (Approx 2.1 m (high) x 0.9 m (wide) x 0.6 m (deep) ). The item shall be complete of MS housing with front door.(Cost shall be inclusive of providing break glass box containing key for the cabinet along with hammer). | [8 empty] | Nos. | 0 | 11400 | 0 | 11400 | 570 | 0 | 11970 | 1050 | 129.78 | 0 | 1179.78 | 0 | 0 | 0
2.21 | 502020000 | Providing & fixing gun-metal fire brigade inlet connection (suction collecting head) consisting of 4 Nos. 63 mm dia instantaneous type male couplings with built-in check valves, 1 No. 150 mm dia sluice valve, and 150 mm dia flanged outlet complete with bolts, nuts and rubber insertions as required and as per IS:904-1963. | [8 empty] | No. | 1 | 28050 | 0 | 28050 | 1402.5 | 0 | 29452.5 | 2058 | 254.3688 | 0 | 2312.3688 | 29452.5 | 2312.3688 | 31764.8688
2.22 | 502020000 | Providing & fixing SS cabinet (to enclose above FB connection) fabricated from 16g SS 304 sheet with full front glass door and locking arrangement duly painted with one coat of primer and two or more coats of synthetic enamel paint of approved make and shade and suitably mounted on a raised masonry platform as required (Approx 0.6m x 0.6m x 0.45m) | [8 empty] | No. | 0 | 18000 | 0 | 18000 | 900 | 0 | 18900 | 368 | 45.4848 | 0 | 413.4848 | 0 | 0 | 0
2.23 | 502020000 | Providing & fixing gun-metal fire brigade suction hose coupling (draw-out connection) with nut for female coupling as per IS: 902-1992 (Reaffirmed 2007) complete with 100 mm dia GI suction pipe and 100 mm dia foot valve (to be connected to static tank). Provision of GI drop pipe and foot valve shall be made in all the fire water static storage tanks (2 Nos) (GI pipe to be paid separately through appropriate item while cost of foot valve to be included). | [8 empty] | Set | 1 | 18430 | 0 | 18430 | 921.5 | 0 | 19351.5 | 1029 | 127.1844 | 0 | 1156.1844 | 19351.5 | 1156.1844 | 20507.6844
2.24 | 502020000 | Providing & fixing SS cabinet (to enclose draw-out connection as per Item above) fabricated from 16 g SS 304 sheet with full front glass door and locking arrangement duly painted with one coat of primer and two or more coats of synthetic enamel paint of approved make and shade and suitably mounted on a raised masonry paltform as required (Approx 0.6 m x 0.6 m x 0.45 m) | [8 empty] | Nos. | 0 | 18000 | 0 | 18000 | 900 | 0 | 18900 | 368 | 45.4848 | 0 | 413.4848 | 0 | 0 | 0
2.25 | 502020000 | Providing and fixing 5 mm thick glass door (with M.S. frame) of size 1.5m x 0.9 m with center opening for fire hose cabinet. Suitably marked on the outside with the letters "FIRE HOSE" including locking arrangement. All M.S. work to be in Red P.O. colour over appropriate primer. The above item is only for masonary fire station. | [8 empty] | No. | 50 | 6321 | 0 | 6321 | 316.05 | 0 | 6637.05 | 772 | 95.4192 | 0 | 867.4192 | 331852.5 | 43370.96 | 375223.46
2.26 | 502020000 | Providing and fixing heavy class MS suction & delivery headers of required length conforming to IS:3589 with welded joints standard MS Fittings and with end flange connections having inlet & outlet flanged connections including MS supports from wall/ floors & ceiling complete as required. Cost should be inclusive of all supports / clamps / brackets, anchor fastner etc. as required (all in M.S.). | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.26.1 | 502020000 | 150 mm dia (C Class) | [8 empty] | RM | 8 | 1675 | 0 | 1675 | 83.75 | 0 | 1758.75 | 494 | 61.0584 | 0 | 555.0584 | 14070 | 4440.4672 | 18510.4672
2.26.2 | 502020000 | 200 mm dia (6 mm thick) | [8 empty] | RM | 8 | 2499 | 0 | 2499 | 124.95 | 0 | 2623.95 | 658 | 81.3288 | 0 | 739.3288 | 20991.6 | 5914.6304 | 26906.2304
2.26.3 | 502020000 | 250 mm dia (6 mm thick) | [8 empty] | RM | 5 | 3577 | 0 | 3577 | 178.85 | 0 | 3755.85 | 823 | 101.7228 | 0 | 924.7228 | 18779.25 | 4623.614 | 23402.864
2.26.4 | 502020000 | 300 mm dia (6 mm thick) | [8 empty] | RM | 0 | 4800 | 0 | 4800 | 240 | 0 | 5040 | 893 | 110.3748 | 0 | 1003.3748 | 0 | 0 | 0
2.27 | 502020000 | Providing two coats of synthetic enamel paint of approved shade over a coat of primer. Prior to application of primer the surface should be cleaned for any dirt, rusts, rough substance etc. Including painting of legends both direction arrow as per the approval of the Project Manager | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.27.1 | 502020000 | 150 mm da | [8 empty] | RM | 8 | 58 | 0 | 58 | 2.9 | 0 | 60.9 | 31 | 3.8316 | 0 | 34.8316 | 487.2 | 278.6528 | 765.8528
2.27.2 | 502020000 | 200 mm di | [8 empty] | RM | 8 | 78 | 0 | 78 | 3.9 | 0 | 81.9 | 41 | 5.0676 | 0 | 46.0676 | 655.2 | 368.5408 | 1023.7408
2.27.3 | 502020000 | 250 mm di | [8 empty] | RM | 5 | 98 | 0 | 98 | 4.9 | 0 | 102.9 | 52 | 6.4272 | 0 | 58.4272 | 514.5 | 292.136 | 806.636
2.27.4 | 502020000 | 300 mm dia | [8 empty] | RM | 0 | 120 | 0 | 120 | 6 | 0 | 126 | 63 | 7.7868 | 0 | 70.7868 | 0 | 0 | 0
2.28 | 502020000 | Constructing brick masonary chamber (for housing valve) in brick work with bricks of class 75 in cement mortar 1:5 (1 cement:5 fine sand) 12 mm thick plaster on inside with a floating coat of neat cement &rough plaster on external faces with cement mortar 1:3 (1 cement : 3 coarse sand) with 150 mm thick PCC (1:4:8). Including providing 100 mm thick R.C.C. top slab complete in all respect. Cost shall be inclusive of excavation in earth, shoring, dewatering, support to valve and access rungs as required to complete the work. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.28.1 | 502020000 | Size 1200 x 900 x 1000 mm deep | [8 empty] | No. | 3 | 10290 | 0 | 10290 | 514.5 | 0 | 10804.5 | 1544 | 190.8384 | 0 | 1734.8384 | 32413.5 | 5204.5152 | 37618.0152
2.29 | 502020000 | Providing & fixing DI medium duty manhole cover with frame of 560 mm internal dia for valve chamber (total weight of cover and frame to be not less than 70 kg for CI). | [8 empty] | No. | 3 | 5390 | 0 | 5390 | 269.5 | 0 | 5659.5 | 515 | 63.654 | 0 | 578.654 | 16978.5 | 1735.962 | 18714.462
2.3 | 502020000 | Providing and laying Cement concrete for anchor / thrust blocks of 1:2:4 [1 cement : 2 fine aggregate : 4 coarse aggregate, 40 mm nomional size as per standard design. | [8 empty] | Cum | 2 | 5390 | 0 | 5390 | 269.5 | 0 | 5659.5 | 515 | 63.654 | 0 | 578.654 | 11319 | 1157.308 | 12476.308
2.31 | 502020000 | Providing, Laying, Testing & Jointing RCC NP3 class pipes with collars jointed with stiff mixture of cement mortar in the proportion of 1:2 (1 cement :2 fine sand) including testing of joints etc. complete. Cost shall be inclusive of excavation in earth, trench works dewatering and shoring complete. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.31.1 | 502020000 | 350 mm dia | [8 empty] | RM | 0 | 975 | 0 | 975 | 48.75 | 0 | 1023.75 | 315 | 38.934 | 0 | 353.934 | 0 | 0 | 0
2.32 | 502020000 | Providing & laying cement concrete 1:2:4 (1 cement: 2 sand: 4 graded stone aggregate 40 mm nominal size) upto haunch of RCC pipes including minimum 150 mm thick and 750 mm wide bed concrete, complete as per standard design. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.32.1 | 502020000 | 350 mm dia | [8 empty] | RM | 0 | 1170 | 0 | 1170 | 58.5 | 0 | 1228.5 | 158 | 19.5288 | 0 | 177.5288 | 0 | 0 | 0
2.33 | 502020000 | Providing & fixing brass/ SS mosquito proof grating in elbow with necessary GI vent pipe with fittings | [8 empty] | Nos. | 2 | 2026 | 0 | 2026 | 101.3 | 0 | 2127.3 | 206 | 25.4616 | 0 | 231.4616 | 4254.6 | 462.9232 | 4717.5232
2.34 | 502020000 | Providing & fixing mosquito proof brass/ SS overflow grating for tanks | [8 empty] | Nos. | 2 | 2026 | 0 | 2026 | 101.3 | 0 | 2127.3 | 206 | 25.4616 | 0 | 231.4616 | 4254.6 | 462.9232 | 4717.5232
i | 502020000 | Note: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii | 502020000 | Core cut markings & cutting shall be done by services vendor. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 502030000 | Sprinkler, Piping & Accessories: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.1 | 502030000 | Providing, laying, jointing and testing of following sizes of pipes conforming to IS-1239 with all accessories like all fittings ( all pipes & fittings upto 50mm dia threaded & for pipes above 50 mm dia MS fitting with welded joint shall be used) including tees, elbows, reducers, union, flanges, rubber gaskets, GI nuts bolts, washer including supporting/fixing the pipe on wall /ceiling with clamps, hangers (using anchor fastners) as per specification. MS pipe sleeve of suitable higher size shall be provided wherever the pipes are crossing the walls/floors and sealing the sleeves with glass wool in between & fire sealent compound at either end all as per Project Managers requirements including cutting holes and chases in brick, R.C.C work and making good the same to original conditions complete in all respects. All hangers, clamps, brackets etc. shall be of galvanized iron unless specified otherwise and the supply of the same shall also be included in rates under this head. Welding of any kind on the galvanized support / hanger shall not be permitted.For Sprinkler system - MS C Heavy class pipe | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.1.1 | 502030000 | 25 mm | [8 empty] | RM | 4100 | 276 | 0 | 276 | 13.8 | 0 | 289.8 | 82 | 10.1352 | 0 | 92.1352 | 1188180 | 377754.32 | 1565934.32
3.1.2 | 502030000 | 32 mm dia | [8 empty] | RM | 600 | 324 | 0 | 324 | 16.2 | 0 | 340.2 | 103 | 12.7308 | 0 | 115.7308 | 204120 | 69438.48 | 273558.48
3.1.3 | 502030000 | 40 mm dia | [8 empty] | RM | 425 | 395 | 0 | 395 | 19.75 | 0 | 414.75 | 123 | 15.2028 | 0 | 138.2028 | 176268.75 | 58736.19 | 235004.94
3.1.4 | 502030000 | 50 mm dia e | [8 empty] | RM | 450 | 537 | 0 | 537 | 26.85 | 0 | 563.85 | 164 | 20.2704 | 0 | 184.2704 | 253732.5 | 82921.68 | 336654.18
3.1.5 | 502030000 | 65 mm dia c | [8 empty] | RM | 530 | 620 | 0 | 620 | 31 | 0 | 651 | 206 | 25.4616 | 0 | 231.4616 | 345030 | 122674.648 | 467704.648
3.1.6 | 502030000 | 80 mm dia b | [8 empty] | RM | 625 | 849 | 0 | 849 | 42.45 | 0 | 891.45 | 247 | 30.5292 | 0 | 277.5292 | 557156.25 | 173455.75 | 730612
3.1.7 | 502030000 | 100 mm dia a | [8 empty] | RM | 300 | 1230 | 0 | 1230 | 61.5 | 0 | 1291.5 | 329 | 40.6644 | 0 | 369.6644 | 387450 | 110899.32 | 498349.32
3.1.8 | 502030000 | 150 mm dia e | [8 empty] | RM | 850 | 1750 | 0 | 1750 | 87.5 | 0 | 1837.5 | 494 | 61.0584 | 0 | 555.0584 | 1561875 | 471799.64 | 2033674.64
3.2 | 502030000 | Providing, fixing, jointing and testing in position the for drainage purpose following heavy class (Class C) MS pipes conforming to IS:1239 cut to required lengths including all necessary fittings (All fittings shall confirm to IS:1879 (part 1 to 10) and specials such as bends, tees, unions, Reducers, flanges & plugs etc. fixing at wall / ceiling level supported by clamps, hangers (using anchor fastners) etc, as per specification. Threading, jointing, and making proper connections, cutting hole in wall / floor / slab and making good the same. GI pipe sleeves suitable higher size shall be provided wherever the pipes are crossing the fire rated walls / floors slab and sealing the sleeves with glass wool in between and fire sealent compound at either end all as per Project Managers / Consultant requirement. All hangers, clamps, brackets etc. shall be of galvanized iron unless specified otherwise and the supply of the same shall also be included in rates under this head. Welding of any kind on the galvanized support / hanger shall not be permitted. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.2.1 | 502030000 | 50 mm dia d | [8 empty] | RM | 25 | 538 | 0 | 538 | 26.9 | 0 | 564.9 | 164 | 20.2704 | 0 | 184.2704 | 14122.5 | 4606.76 | 18729.26
3.2.2 | 502030000 | 65 mm dia g | [8 empty] | RM | 10 | 620 | 0 | 620 | 31 | 0 | 651 | 206 | 25.4616 | 0 | 231.4616 | 6510 | 2314.616 | 8824.616
3.2.3 | 502030000 | 80 mm dia f | [8 empty] | RM | 150 | 855 | 0 | 855 | 42.75 | 0 | 897.75 | 247 | 30.5292 | 0 | 277.5292 | 134662.5 | 41629.38 | 176291.88
3.2.4 | 502030000 | 100 mm dia e | [8 empty] | RM | 50 | 1230 | 0 | 1230 | 61.5 | 0 | 1291.5 | 329 | 40.6644 | 0 | 369.6644 | 64575 | 18483.22 | 83058.22
3.2.5 | 502030000 | 150 mm dia | [8 empty] | RM | 0 | 1750 | 0 | 1750 | 87.5 | 0 | 1837.5 | 494 | 61.0584 | 0 | 555.0584 | 0 | 0 | 0
3.3 | 502030000 | Providing two coats of synthetic enamel paint of approved shade over a coat of primer. Prior to application of primer the surface should be cleaned for any dirt, rusts, rough substance etc. Including painting of legends both direction arrow as per the approval of the Project Manager | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.3.1 | 502030000 | 25 mmdia | [8 empty] | RM | 4100 | 9 | 0 | 9 | 0.45 | 0 | 9.45 | 6 | 0.7416 | 0 | 6.7416 | 38745 | 27640.56 | 66385.56
3.3.2 | 502030000 | 32 mm dia d | [8 empty] | RM | 600 | 11 | 0 | 11 | 0.55 | 0 | 11.55 | 8 | 0.9888 | 0 | 8.9888 | 6930 | 5393.28 | 12323.28
3.3.3 | 502030000 | 40 mmf | [8 empty] | RM | 425 | 14 | 0 | 14 | 0.7 | 0 | 14.7 | 9 | 1.1124 | 0 | 10.1124 | 6247.5 | 4297.77 | 10545.27
3.3.4 | 502030000 | 50 mmd | [8 empty] | RM | 450 | 19 | 0 | 19 | 0.95 | 0 | 19.95 | 11 | 1.3596 | 0 | 12.3596 | 8977.5 | 5561.82 | 14539.32
3.3.5 | 502030000 | 65 mm dia n | [8 empty] | RM | 530 | 24 | 0 | 24 | 1.2 | 0 | 25.2 | 14 | 1.7304 | 0 | 15.7304 | 13356 | 8337.112 | 21693.112
3.3.6 | 502030000 | 80 mm dia b | [8 empty] | RM | 625 | 29 | 0 | 29 | 1.45 | 0 | 30.45 | 16 | 1.9776 | 0 | 17.9776 | 19031.25 | 11236 | 30267.25
3.3.7 | 502030000 | 100 mm dia b | [8 empty] | RM | 300 | 39 | 0 | 39 | 1.95 | 0 | 40.95 | 21 | 2.5956 | 0 | 23.5956 | 12285 | 7078.68 | 19363.68
3.3.8 | 502030000 | 150 mm dia b | [8 empty] | RM | 1200 | 58 | 0 | 58 | 2.9 | 0 | 60.9 | 32 | 3.9552 | 0 | 35.9552 | 73080 | 43146.24 | 116226.24
3.4 | 502030000 | Designing, providing and fixing Orifice plate made out of stainless stand plate (thickness as per specification) for following size of pipe to reduce pressure upto 3.5 Kg/sqcm complete in all respects. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.4.1 | 502030000 | 65 mm dia | [8 empty] | No | 0 | 700 | 0 | 700 | 35 | 0 | 735 | 53 | 6.5508 | 0 | 59.5508 | 0 | 0 | 0
3.4.2 | 502030000 | 80 mm dia | [8 empty] | No. | 0 | 700 | 0 | 700 | 35 | 0 | 735 | 53 | 6.5508 | 0 | 59.5508 | 0 | 0 | 0
3.4.3 | 502030000 | 100 mm diaa | [8 empty] | No. | 7 | 686 | 0 | 686 | 34.3 | 0 | 720.3 | 53 | 6.5508 | 0 | 59.5508 | 5042.1 | 416.8556 | 5458.9556
3.5 | 502030000 | Providing and fixing forged brass ball valve with forged brass ball (suitable for test pressure of 30 Kg / sqm of the following size including providing necessary union / flange. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.5.1 | 502030000 | 25 mm diaa | [8 empty] | No. | 40 | 650 | 0 | 650 | 32.5 | 0 | 682.5 | 103 | 12.7308 | 0 | 115.7308 | 27300 | 4629.232 | 31929.232
3.6 | 502030000 | Providing & fixing of butterfly valve of PN 16 rating with flanges, nut bolts & gaskets complete required. Butterfly valve shall be with pad locking arrangement. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.6.1 | 502030000 | 80 mm | [8 empty] | No. | 35 | 3626 | 0 | 3626 | 181.3 | 0 | 3807.3 | 412 | 50.9232 | 0 | 462.9232 | 133255.5 | 16202.312 | 149457.812
3.6.2 | 502030000 | 100 mm | [8 empty] | No. | 11 | 4753 | 0 | 4753 | 237.65 | 0 | 4990.65 | 515 | 63.654 | 0 | 578.654 | 54897.15 | 6365.194 | 61262.344
3.6.3 | 502030000 | 150 mm | [8 empty] | No. | 0 | 7900 | 0 | 7900 | 395 | 0 | 8295 | 788 | 97.3968 | 0 | 885.3968 | 0 | 0 | 0
3.7 | 502030000 | Providing & Fixing of Installation Control Valve with turbine type automatic Alarm Gong to be connected with control valve, drain & test valve and all other necessary components as per manufacturers specifications complete as required. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.7.1 | 502030000 | 150 mm diaam | [8 empty] | No. | 3 | 44100 | 0 | 44100 | 2205 | 0 | 46305 | 3087 | 381.5532 | 0 | 3468.5532 | 138915 | 10405.6596 | 149320.6596
3.8 | 502030000 | Providing & fixing brass quartzoid sprinklers (UL listed) of 15 mm dia size, suitable for sustaining the pressure on the seat & water hammer effect. The type & temperature rating shall be as follows : | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.8.1 | 502030000 | Sidewall extended coverage (68 deg.C) sprinkler quick response type for Guest room area | [8 empty] | Nos | 215 | 520 | 0 | 520 | 26 | 0 | 546 | 53 | 6.5508 | 0 | 59.5508 | 117390 | 12803.422 | 130193.422
3.8.2 | 502030000 | Sidewall extended coverage (79 deg.C) sprinkler quick response type for Car Parking | [8 empty] | Nos | 115 | 645 | 0 | 645 | 32.25 | 0 | 677.25 | 53 | 6.5508 | 0 | 59.5508 | 77883.75 | 6848.342 | 84732.092
3.8.3 | 502030000 | Recessed pendent type quick responsetype sprinkler (20 mm adjustable) (68 deg.c) for Guest room area | [8 empty] | Nos | 720 | 255 | 0 | 255 | 12.75 | 0 | 267.75 | 53 | 6.5508 | 0 | 59.5508 | 192780 | 42876.576 | 235656.576
3.8.4 | 502030000 | Recessed pendent type quick responsetype sprinkler (20 mm adjustable) (79 deg.c) for BOH area | [8 empty] | Nos | 240 | 275 | 0 | 275 | 13.75 | 0 | 288.75 | 53 | 6.5508 | 0 | 59.5508 | 69300 | 14292.192 | 83592.192
3.8.5 | 502030000 | Side wall extended coverage quick response sprinkler (141 deg.C) for lift machine room. | [8 empty] | Nos | 10 | 825 | 0 | 825 | 41.25 | 0 | 866.25 | 72 | 8.8992 | 0 | 80.8992 | 8662.5 | 808.992 | 9471.492
3.8.6 | 502030000 | Quick response Pendent type (79) deg.C) sprinkler For Car parking Areas. | [8 empty] | Nos. | 300 | 437 | 0 | 437 | 21.85 | 0 | 458.85 | 53 | 6.5508 | 0 | 59.5508 | 137655 | 17865.24 | 155520.24
3.8.7 | 502030000 | Upright (79 deg. C) sprinkler for service floor, car parking and non A/c areas. | [8 empty] | Nos. | 400 | 437 | 0 | 437 | 21.85 | 0 | 458.85 | 53 | 6.5508 | 0 | 59.5508 | 183540 | 23820.32 | 207360.32
3.8.8 | 502030000 | Pendent (141 deg.C) sprinkler for Boiler room / DG set room, fire pump rom & lift machine room) | [8 empty] | Nos. | 8 | 864 | 0 | 864 | 43.2 | 0 | 907.2 | 53 | 6.5508 | 0 | 59.5508 | 7257.6 | 476.4064 | 7734.0064
3.8.9 | 502030000 | Quick response dry pendent sprinkler for cold store rooms (68 deg.c) | [8 empty] | Nos. | 10 | 10000 | 0 | 10000 | 500 | 0 | 10500 | 225 | 27.81 | 0 | 252.81 | 105000 | 2528.1 | 107528.1
3.8.10 | 502030000 | Automatic spray nozzle, deep fat fryer (for kitchen hoods) sprinkler | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
a. | 502030000 | 175 deg.C | [8 empty] | Nos. | 0 | 1230 | 0 | 1230 | 61.5 | 0 | 1291.5 | 105 | 12.978 | 0 | 117.978 | 0 | 0 | 0
b. | 502030000 | 250 deg.C | [8 empty] | Nos. | 0 | 1500 | 0 | 1500 | 75 | 0 | 1575 | 105 | 12.978 | 0 | 117.978 | 0 | 0 | 0
c. | 502030000 | 325 deg.C | [8 empty] | Nos. | 0 | 1680 | 0 | 1680 | 84 | 0 | 1764 | 105 | 12.978 | 0 | 117.978 | 0 | 0 | 0
3.8.11 | 502030000 | Multi spray sprinkler system for window / issue counter suitable for providing water curtain effect. | [8 empty] | Set | 0 | 690 | 0 | 690 | 34.5 | 0 | 724.5 | 53 | 6.5508 | 0 | 59.5508 | 0 | 0 | 0
i | 502030000 | All sprinkler shall be chrome finish except for the concealed ones. The concealed sprinkler shall be of brass finish. The cover plates of the concealed sprinkler shall be factory painted at manufacturers work and the shade shall be confirmed prior to application on the cover plate. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii | 502030000 | Core cut markings & cutting shall be done by services vendor. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.9 | 502030000 | Providing and Fixing electrically operated water flow switches (Vane type) including tamper switch and accessories, complete with tap off socket arrangement as required, with potential free contact with 2 Nos. NONC. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.9.1 | 502030000 | 65 mm diaa | [8 empty] | No. | 2 | 4214 | 0 | 4214 | 210.7 | 0 | 4424.7 | 200 | 24.72 | 0 | 224.72 | 8849.4 | 449.44 | 9298.84
3.9.2 | 502030000 | 80 mm diaa | [8 empty] | No. | 33 | 4214 | 0 | 4214 | 210.7 | 0 | 4424.7 | 200 | 24.72 | 0 | 224.72 | 146015.1 | 7415.76 | 153430.86
3.9.3 | 502030000 | 100 mmd | [8 empty] | No. | 11 | 4214 | 0 | 4214 | 210.7 | 0 | 4424.7 | 200 | 24.72 | 0 | 224.72 | 48671.7 | 2471.92 | 51143.62
3.9.4 | 502030000 | 150 mm di | [8 empty] | No. | 1 | 4214 | 0 | 4214 | 210.7 | 0 | 4424.7 | 200 | 24.72 | 0 | 224.72 | 4424.7 | 224.72 | 4649.42
3.1 | 502030000 | Providing and fixing inspectors test assembly complete with test valve, sight glass sectional drain valve, union; necessary piping, threading, jointing & with corrosion resistant orifice all complete strictly as per drawing. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.10.1 | 502030000 | 50 mm | [8 empty] | No. | 40 | 3283 | 0 | 3283 | 164.15 | 0 | 3447.15 | 257 | 31.7652 | 0 | 288.7652 | 137886 | 11550.608 | 149436.608
i | 502030000 | Cost shall be inclusive for approval of fire hydrant & sprinkler system from local fire authority and any other relevant statutory authority at initial & various other stages of works, including preparation of report / drawings as per fire authority. Contractor shall include cost of all liaison works which are not explicitly mentioned above but are mandatory to have fire authority approval (any statutory charges will be reimbursed as per actual upon production of the invoice / challan). | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 502040000 | Portable Chemical Fire Extinguishers:Supply, installation, testing and commissioning of following types of extinguisher with provision of wall bracket (fixed with anchor fastner). | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4.1 | 502040000 | ISI marked (IS:940) portable fire extinguisher, water (gas pressure) type capacity 9 litres with gun metal cap and nozzle and complete in all respects including initial fill and wall suspension brackets | [8 empty] | Each | 45 | 2058 | 0 | 2058 | 102.9 | 0 | 2160.9 | 53 | 6.5508 | 0 | 59.5508 | 97240.5 | 2679.786 | 99920.286
4.2 | 502040000 | ISI marked (IS:2878) portable CO2 type fire extinguisher type. Including valve, discharge hose of not less than 10 mm dia & 1 M long complete in all respects including initial filled with CO2 gas confirming to IS:307-1966 & filled to a filling rate of not more than 0.667 and wall suspension bracket. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4.2.1 | 502040000 | 4.5kg capacity | [8 empty] | Each | 0 | 6500 | 0 | 6500 | 325 | 0 | 6825 | 53 | 6.5508 | 0 | 59.5508 | 0 | 0 | 0
4.3 | 502040000 | ISI marked (IS:2171) Portable Dry Chemical Power Type Fire Extinguisher with Gun Metal cap and nozzle complete in all respects including initial fill of power and wall suspension bracket | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4.3.1 | 502040000 | 5 Kgg | [8 empty] | Each | 15 | 2468 | 0 | 2468 | 123.4 | 0 | 2591.4 | 53 | 6.5508 | 0 | 59.5508 | 38871 | 893.262 | 39764.262
4.4 | 502040000 | ABC (Powder Type) Fire Extinguisher. In HP Mild Steel Cylinders ISI marked/ TAC approved fitted with pressure indicating gauge, internal tube, squeeze lever type valve fully charged with ABC powder (Mono Ammonium Phosphate) pressured by Nitrogen complete in all respects including wall suspension bracket and confoming to IS:1349-1993 | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4.4.1 | 502040000 | 5 Kg | [8 empty] | Each | 0 | 2350 | 0 | 2350 | 117.5 | 0 | 2467.5 | 53 | 6.5508 | 0 | 59.5508 | 0 | 0 | 0
4.4.2 | 502040000 | 10 Kg | [8 empty] | Each | 20 | 2695 | 0 | 2695 | 134.75 | 0 | 2829.75 | 53 | 6.5508 | 0 | 59.5508 | 56595 | 1191.016 | 57786.016
4.5 | 502040000 | Supplying and installing at approved location approved make fire buckets of 24 gauge galvanized steel sheet, standard 9 litre capacity and of round bottom shape, painted white inside and red outside and black on the bottom, inscribed with letters “FIRE” in black and gold. Cost shall be inclusive of providing MS stand duly painted over a coat of primer. | [8 empty] | Nos. | 15 | 240 | 0 | 240 | 12 | 0 | 252 | 53 | 6.5508 | 0 | 59.5508 | 3780 | 893.262 | 4673.262
5 | 502060000 | Permits / Inspections and Approval of Systems | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.1 | 502060000 | Obtaining composite approval for the entire fire protection system including fire fighting, fire detection, fire doors etc. and all other related works which fall under the purview of the local statutory authority / Chief Fire Officer and making payments / liaisoning / incidental charges for the portion of works carried out by the Contractor. Drawings and other submittal for works done by other agencies as per the regulations will be furnished to the Contractor for obtaining such approval. All the expenses incurred in this regard including incidentals shall be borne by the Contractor. However all Statutory payments against challans shall be paid by client. | [8 empty] | Job | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 245000 | 30282 | 0 | 275282 | 0 | 275282 | 275282
I | 502050000 | ELECTRICAL INSTALLATION FOR PLUMBING | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 502050000 | Electrical panel for Plumbing System | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.1 | 502050000 | Design, fabrication, assembling, wiring, supply, installation, testing and commissioning of motor control centre shall be fabricated out of 14 gauge CRCA sheet steel in form in 3b formation with reinforcement of suitable size angle iron, channel T sections irons and/or flats wherever necessary. Cable gland plates shall be provided on top as well as at the bottom of the panels. Panels shall be treated with all anticorrosive process before painting as per specifications with 2 coats of red oxide primer and final approved shade of powder coated paint. 2 Nos. earthing terminals shall be provided for 3 phase, 4 wire, 50 Hz supply system. Lifting hooks shall also be provided in case of large panels. Approval shall be taken for each panel before fabrication. Cadmium Plated hardware shall be used in fabrication of panels. MCC for Plumbing systemIncoming200 amps TPN MCCB (25KA) with the following accessories: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
a. | 502050000 | a. 0-500 volts 96 x 96 mm square digital electronic voltmeter with selector switch protected by 2 amps TP MCB. 1 Set | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
b. | 502050000 | b. 0-200 amps 96 x 96 mm square digital electronic ammeter with selector switch and 3 nos 200/5 amps 5 VA CL:1 CTs. 1 Set | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
c. | 502050000 | Phase indicating lamps protected by 2 amp SP MCB 3 Sets | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
d. | 502050000 | Digital electronic KWH meter with RS 485 port.Bus Bar200 amps TPN (25KA) copper bus bar with heat shrinkable insulation sleeves. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 502050000 | Outgoings | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
a. | 502050000 | 1 Nos. 40 amps TPN MCCB outgoing feeder to Lower zone Domestic water Hydropneumatic system panel. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
b. | 502050000 | 1 No. 100 amps TPN MCCB outgoing to upper zone domestic water Hydropneumatic system panel | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
c. | 502050000 | 1 No. 100 amps TPN MCCB outgoing to flushing water Hydropneumatic system panel | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
d. | 502050000 | 25 amps TPN MCCB for plant room sump pump control panel | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
e | 502050000 | 3 nos 25 amps TPN MCCB for car park sump pump control panel | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
f | 502050000 | 1 Nos. suitable rating TPN MPCB for 7.5 HP/5.5 KW DOL starter and outgoing feeder to Plant room Exhaust fan motor. Each compartment shall contain CT operated digital electronic ammeter suitable range with auto/manual selector switch and indicating lamps with MCBs and ON/OFF/TRIP status of motor | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
g. | 502050000 | 1 Nos. suitable rating TPN MPCB for 7.5 HP/5.5 KW DOL starter and outgoing feeder to Plant room Supply fan motor. Each compartment shall contain CT operated digital electronic ammeter suitable range with auto/manual selector switch and indicating lamps with MCBs and ON/OFF/TRIP status of motor | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
h. | 502050000 | c. 2 Nos. suitable rating TPN MPCB for 2.5 HP/ 1.8 KW DOL starter and outgoing feeder to Filter Feed pump (1 working + 1 standby). Each compartment shall contain direct operated digital electronic ammeter of suitable range with auto/manual selector switch and indicating lamps with MCBs and ON/OFF/TRIP status of motor | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i | 502050000 | Spare MCCBs of following capacities: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
j | 502050000 | 63 amps TPN MCCB 2 Nos. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 502050000 | Necessary cable alleys, internal wiring, and interlocking, earthing for all equipment shall also included | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
a. | 502050000 | All MCCBs shall be of 25 KA breaking capacity and suitable for motor duty application. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
b. | 502050000 | Provision shall be made for providing potential free contacts to all pumps starters for connection to BAS | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
c. | 502050000 | Provision shall be made to ensure system protection from dry running of the pump | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
d. | 502050000 | MCCB/MPCB shall be Type 2 Co-ordinated with the Motor starter. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 502050000 | MCC for Plumbing system System as described above. | [8 empty] | Set | 1 | 313983 | 0 | 313983 | 15699.15 | 0 | 329682.15 | 25725 | 3179.61 | 0 | 28904.61 | 329682.15 | 28904.61 | 358586.76
2 | 502050000 | Control Panel For Drainage Sump Pump | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.1 | 502050000 | Incoming25 Amps 4 pole MCB with the following accessories:a. 0-500 volts 96 x 96 mm square digital electronic voltmeter with selector switch protected by 2 amps TP MCB. 1 Setb. 0-25 amps 96 x 96 mm square digital electronic ammeter with selector switch and 3 nos 25/5 amps 5 VA CL:1 CTs. 1 Setc. Phase indicating lamps protected by 2 amp SP MCB 3 SetsBus Bar25 Amps TPN copper bus bar with heat shrinkable insulation sleeves.Outgoingsa. 2 Nos. 16 amps 4 Pole MCB for 2 Nos. 4 HP/3 KW direct on line starter and outgoing feeders to Sump pump motor . Each compartment shall contain direct operated digital electronic ammeter of 0-16amps range with auto/manual selector switch and indicating lamps with MCBs and ON/OFF/TRIP status of motorb. Necessary cable alleys, internal wiring, and interlocking, earthing for all equipment shall also includedNotesa. All MCBs shall be of 10 kA breaking capacity. b. All motor starter shall be provided with Automatic float type level controllerc. Provision of high high level alarm shall also be maded. It shall be ensured that all pumps operate during high high level in the sumpe. Sequence timer for pump operation shall be providedf. Provision shall be made for providing potential free contacts to all pumps starters for connection to BASg. MCB shall be of type “C” characteristic | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 502050000 | Control Panel for Drainage Pumps as described above | [8 empty] | Nos. | 5 | 40250 | 0 | 40250 | 2012.5 | 0 | 42262.5 | 2573 | 318.0228 | 0 | 2891.0228 | 211312.5 | 14455.114 | 225767.614
3.1 | 502050000 | Control Panel for Swimming Pool : | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.2 | 502050000 | Design, fabrication, assembling, wiring, supply, installation, testing and commissioning of motor control centre shall be fabricated out of 14 gauge CRCA sheet steel in form in 3b formation with reinforcement of suitable size angle iron, channel T sections irons and/or flats wherever necessary. Cable gland plates shall be provided on top as well as at the bottom of the panels. Panels shall be treated with all anticorrosive process before painting as per specifications with 2 coats of red oxide primer and final approved shade of powder coated paint. 2 Nos. earthing terminals shall be provided for 3 phase, 4 wire, 50 Hz supply system. Lifting hooks shall also be provided in case of large panels. Approval shall be taken for each panel before fabrication. Cadimium plated hardware shall be used in fabrication of panels | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.3 | 502050000 | MCC Swimming Pool | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.4 | 502050000 | Incoming63 amps TPN MCCB with the following accessories:0-500 volts 96 x 96 mm square digital electronic voltmeter with selector switch protected by 2 amps TP MCB. 1 Set0-63 amps 96 x 96 mm square digital electronic ammeter with selector switch and 3 nos 63/5 amps 5 VA CL:1 CTs. 1 SetPhase indicating lamps protected by 2 amp SP MCB 3 SetsBus Bar63 amps TPN copper bus bar with heat shrinkable insulation sleeves.Outgoings2Nos suitable rating TPN MPCB with 2Nos. 12.5 HP/ 9.3 KW star delta starter and outgoing feeder to swimming pool pump. Each compartment shall contain CT operated digital electronic ammeter of suitable amps range with auto/manual selector switch and indicating lamps with MCBs and ON/OFF/TRIP status of motor1 nos. 25 amps DP MCBs for dosing pumps1 nos. 16 amps DP MCBs for UV unitSpare MCCBs of following capacities:25 amps TPN MCB 2 NosNecessary cable alleys, internal wiring, and interlocking, earthing for all equipment shall also included.All MCCBs shall be of 25 KA breaking capacity.Provision shall be made for providing potential free contacts to all pumps starters for connection to BASMPCB shall be Type 2 Co-ordinated with the Motor starter. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.5 | 502050000 | MCC for swimming pool as described above | [8 empty] | No. | 1 | 62830 | 0 | 62830 | 3141.5 | 0 | 65971.5 | 5145 | 635.922 | 0 | 5780.922 | 65971.5 | 5780.922 | 71752.422
J | 502050000 | ELECTRICAL WORK FOR FIRE PROTECTION SYSTEM: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 502050000 | Control Panel for Fire protection system: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.1 | 502050000 | Control Panel for fire fighting equipment in pump room :- | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.2 | 502050000 | Design, manufacture, supply, installation, testing and commissioning of the following integrated, cubicle type, dead front, extensible, sheet steel control panel anchoring the panel to the foundation. The panel shall be duly powder coated and suitable for 500 volts, 50 cycles, 4 wire supply. Quoted price shall include 1100 volts grade rubber mats over 50mm thick teak wood platform, control wiring. The panel shall have separate compartments for bus bar and cable alleys. The following components and accessories shall be mounted within each control panel. (IP 55) a. One No. 630 amps TPN incoming MCCB complete with the following:i. 0-500 volts 96 x 96mm square digital electronic voltmeter with selector switch protected by 2 amps TP MCB 1 Setii. 0-630 amps 96 x 96 mm square digital electronic ammeter with 3 nos 630/5 amps 15 VA CL:1 CTs and selector switch 1 Setiii. Phase indicating lamps protected by 2 amps SP MCB 3 Setsb. Copper bus bar with heat shrinkable sleeves, rated at 630amps(25KA) for three phase & neutral phase bus bar shall have maximum current density of 0.8 amps per sq.mm. and the neutral bus bar of not less than 50% capacity. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.3 | 502050000 | Outgoing:c. 1 Nos. 250 amps TPN MCCB with 125 HP/ 90 KW Star Delta starters & out going feeders to Fire Hydrant pump motor. The compartment shall contain CT operated digital electronic ammeter of 0-250 amps range with selector switch and indicating lamp with MCBs for ON/OFFTRIP status of motor.d. 1 Nos. 250 amps TPN MCCB with 125 HP/ 90 KW Star Delta starters & out going feeders to Fire sprinkler pump motor. The compartment shall contain CT operated digital electronic ammeter of 0-25 amps range with selector switch and indicating lamp with MCBs for ON/OFFTRIP status of motor.e. 1 Nos. suitable rating TPN MPCB with 10 HP/7.5 KW DOL starter with single phase preventer and outgoing feeder to hydrant jockey pump motor. The compartment shall contain CT operated digital electronic ammeter of suitable range and indicating lamps with MCBs for ON/OFFTRIP status of pump motors.f. 1 Nos.suitable range TPN MPCB, with 10HP/7.5 KW DOL starter with single phase preventer and outgoing feeder to sprinkler jockey pump motor. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0.1236 | 1 | 1.1236 | 0 | 0 | 0
1.4 | 502050000 | The compartment shall contain CT operated digital electronic ammeter suitable range and indicating lamps with MCBs for ON/OFFTRIP status of pump motors.g. 1 Nos. 25 Amps TPN Motor duty MCCB for hydrant booster pump motor control panel on terrace floor With ON/OFF Push button and indicating lamps with Mcbs for ON/OFFTRIP status of pump motors including necessary control wiring.h. 1 No. 63 amps TPN MCCB as sparei. Necessary cable alleys space for spare switches, internal wiring and earthing of all equipment shall also be included. All switch gears/control gears shall be motor duty rating.j. Providing and fixing 1 No. auto start panel activated with pressure switch for diesel engine complete with all accessories, batteries, battery charger of suitable rating, MCB timers, push buttons, microprocessor based alarm annunciator, wiring and cabling including connection to diesel engine complete as required ready for working.NoteAll MCCBs to be suitable for motor duty and shall be of 25 kA breaking capacity.Provision shall be made for providing potential free contacts to all pumps starters for connection to building automation system.MCCB shall be Type 2 Co-ordinated with the Motor starter. | [8 empty] | Nil | 0
1.5 | 502050000 | Motor control panel-FF as described above | [8 empty] | Set | 1 | 530000 | 0 | 530000 | 26500 | 0 | 556500 | 25725 | 3179.61 | 0 | 28904.61 | 556500 | 28904.61 | 585404.61
2 | 502050000 | CONTROL PANEL FOR TERRACE BOOSTER PUMP MOTOR. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.1 | 502050000 | Design, manufacture, supply, installation, testing and commissioning of the following cubicle type, dead front, sheet steel, wall mounted control panels, including anchoring into the wall, incoming cable wiring terminating into MCCB and copper earthing, to the starter panel. Starter control panel shall be provided with Stop /Manual /Auto selector switch to facilitate operation through BAS. starters shall be provided with potential free Contact for Connections to Building Automation System.All wiring and copper earthing of motors from the panel shall be included.The panel shall include the following components & accessories. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
a. | 502050000 | MCCB/MPCB as per the ratings given below, suitable for motor duty and able to withstand fault level of 25 KA. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
b. | 502050000 | SD starter as per HP gratings given. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
c. | 502050000 | Terminal block for power distribution as required. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
d. | 502050000 | Contactor, over load relay with built in single phasing protection. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
e | 502050000 | Phase indicating lights and indicating light for ON status. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
f | 502050000 | 144 mm x 144 mm voltmeter and digital ammeter. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
g. | 502050000 | Time delay relay for delayed automatic restart of motor. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
h. | 502050000 | For on/off/remote and local operation, 3 pole single throw switch shall be provided to facilitate override of the automatic operation. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i | 502050000 | Starters control panel shall be provided with suitable potential free contract for connections to the Building Automation System. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
j | 502050000 | MCCB/MPCB shall be Type 2 Co-ordinated with the Motor starter. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
k | 502050000 | Degree of Protection for the starter panel shall be IP 55. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 502050000 | CONTROL PANEL FOR TERRACE BOOSTER PUMP MOTOR as described above | [8 empty] | No. | 1 | 14700 | 0 | 14700 | 735 | 0 | 15435 | 3087 | 381.5532 | 0 | 3468.5532 | 15435 | 3468.5532 | 18903.5532
3.1 | 502050000 | Cable & Cable Trays for Plumbing & Fire Protection System | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.1.1 | 502050000 | Supplying & laying of following 1100 volt grade XLPE insulated PVC inner sheathed & FRLS PVC outer sheathed aluminium/copper conductor armoured cables as per specification buried, in existing , cable trays, ducts, clamped to wall with suitable clamps, saddles fixing bolts including connecting testing and commissioning. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.1.2 | 502050000 | 3 core 70 sq. mm Aluminium cable | [8 empty] | RM | 100 | 292 | 0 | 292 | 14.6 | 0 | 306.6 | 52 | 6.4272 | 0 | 58.4272 | 30660 | 5842.72 | 36502.72
3.1.3 | 502050000 | 3.5 core 50 sq. mm Aluminium cable | [8 empty] | RM | 50 | 244 | 0 | 244 | 12.2 | 0 | 256.2 | 52 | 6.4272 | 0 | 58.4272 | 12810 | 2921.36 | 15731.36
3.1.4 | 502050000 | 4 core 25 sq. mm Aluminium cable | [8 empty] | RM | 50 | 164 | 0 | 164 | 8.2 | 0 | 172.2 | 41 | 5.0676 | 0 | 46.0676 | 8610 | 2303.38 | 10913.38
3.1.5 | 502050000 | 4 core 4 sq. mm copper cable | [8 empty] | RM | 50 | 216 | 0 | 216 | 10.8 | 0 | 226.8 | 41 | 5.0676 | 0 | 46.0676 | 11340 | 2303.38 | 13643.38
3.1.6 | 502050000 | 3 core 6 sq. mm copper cable | [8 empty] | RM | 75 | 245 | 0 | 245 | 12.25 | 0 | 257.25 | 36 | 4.4496 | 0 | 40.4496 | 19293.75 | 3033.72 | 22327.47
3.1.7 | 502050000 | 3 core 4 sq. mm copper cable | [8 empty] | RM | 100 | 170 | 0 | 170 | 8.5 | 0 | 178.5 | 36 | 4.4496 | 0 | 40.4496 | 17850 | 4044.96 | 21894.96
3.2 | 502050000 | Cable end termination of the following XLPE insulated FRLS PVC outer sheathed aluminium/copper conductor armoured cables of 1100 volt grade including supplying and fixing of bimettalic crimping lugs, double compression glands with earthing. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.2.1 | 502050000 | 3 core 70 sq. mm Aluminium cabl | [8 empty] | Nos | 10 | 441 | 0 | 441 | 22.05 | 0 | 463.05 | 82 | 10.1352 | 0 | 92.1352 | 4630.5 | 921.352 | 5551.852
3.2.2 | 502050000 | MPCB suitable for 11 KW booster pump motor with star delta Starter as described above | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.2.3 | 502050000 | 3.5 core 50 sq. mm Aluminium cabl | [8 empty] | Nos | 6 | 318 | 0 | 318 | 15.9 | 0 | 333.9 | 61 | 7.5396 | 0 | 68.5396 | 2003.4 | 411.2376 | 2414.6376
3.2.4 | 502050000 | 4 core 25 sq. mm Aluminium cabl | [8 empty] | Nos | 2 | 240 | 0 | 240 | 12 | 0 | 252 | 52 | 6.4272 | 0 | 58.4272 | 504 | 116.8544 | 620.8544
3.2.5 | 502050000 | 4 core 4 sq. mm copper cabl | [8 empty] | Nos | 6 | 196 | 0 | 196 | 9.8 | 0 | 205.8 | 31 | 3.8316 | 0 | 34.8316 | 1234.8 | 208.9896 | 1443.7896
3.2.6 | 502050000 | 3 core 6 sq. mm copper cabl | [8 empty] | Nos | 10 | 171 | 0 | 171 | 8.55 | 0 | 179.55 | 31 | 3.8316 | 0 | 34.8316 | 1795.5 | 348.316 | 2143.816
3.2.7 | 502050000 | 3 core 4 sq. mm copper cabl | [8 empty] | Nos | 12 | 156 | 0 | 156 | 7.8 | 0 | 163.8 | 31 | 3.8316 | 0 | 34.8316 | 1965.6 | 417.9792 | 2383.5792
3.3 | 502050000 | Supply and fixing of factory fabricated Hot dip galvanized GI ladder type cable trays, with radial bends, suspenders and supports as per specification and of the following sizes. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.3.1 | 502050000 | 450 mm wide | [8 empty] | RM | 100 | 343 | 0 | 343 | 17.15 | 0 | 360.15 | 154 | 19.0344 | 0 | 173.0344 | 36015 | 17303.44 | 53318.44
3.4 | 502050000 | Supply and fixing of perforated type Hot dip galvanized GI cable trays with supports, hangers, fastners of the following sizes as per specification. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.4.1 | 502050000 | 150 mm wide | [8 empty] | RM | 50 | 122 | 0 | 122 | 6.1 | 0 | 128.1 | 103 | 12.7308 | 0 | 115.7308 | 6405 | 5786.54 | 12191.54
3.4.2 | 502050000 | 300 mm wide | [8 empty] | RM | 50 | 245 | 0 | 245 | 12.25 | 0 | 257.25 | 154 | 19.0344 | 0 | 173.0344 | 12862.5 | 8651.72 | 21514.22
4 | 502050000 | Earthing for Plumbing & Fire Protection System | [8 empty] | Nil | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4.1 | 502050000 | Supply and fixing of bare GI tapes / wires including all necessary fixing accessories and effecting connections as per specifications. | [8 empty] | LOT | 1 | 24500 | 0 | 24500 | 1225 | 0 | 25725 | 5145 | 635.922 | 0 | 5780.922 | 25725 | 5780.922 | 31505.922

## Certificates
Scenario 3
Local Supply Rates + Installation Rates |  |  | COP-R001 | [21 empty] | 74294634.9813 |  |  | 7125112.4 | 0 | 7125112.4 | 356255.62 | 0 | 7481368.02 | 1046839.925 | 129389.4147 | 0 | 1176229.3397 | 8657597.3597
|  | UNIQUE IDENTIFIERS | [8 empty] | UOM | QTY | RATE (can be entered directly or summed up for totals)
Sr. No. | Item Range Code | Description | Area | Make | Model No./ Product Code | Tag/ Item No. | ITC HS Code | Country of Origin | Port of Loading | User defined column |  |  | Local supply rate | [5 empty] | Installation Rate |  |  |  | Amount |  |  | LOCAL SUPPLY CERTIFICATION | [7 empty] | INSTALLATION CERTIFICATION |  |  |  | CERTIFICATION TOTAL
[13 empty] | Basic Rate | Excise | Subtotal = Basic + Excise | VAT/CST on Subtotal | Others | Supply Rate Total (sum or direct entry) | Basic Rate | Service Tax | Other | Installation Rate Total (sum or direct entry) | LOCAL SUPPLY AMOUNT | INSTALLATION AMOUNT | TOTAL AMOUNT | COP Percentage | COP Quantity | COP Supply Basic | COP Excise | COP Sub Total | COP VAT / CST | COP SupplyOthers | COP Supply Total | COP Installation Basic | COP Service TAX | COP Others | COP Installation Total | TOTAL COP AMOUNT
A | 501020000 | SANITARY FIXTURES & FITTINGS: (INSTALLATION) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 501020000 | Fixing, testing and commissioning of white vitreous China wall mounting type European water closet including Providing & fixing of C.P. bolts, nuts, C.I. chair (painted with two coats of enamel paint over a coat of primer) & Fixing, testing & commissioning of hanging arrangements, bakelite / poly propylene seat & cover (fixing only) with C.P. hinges & rubber buffers, C.P. brass screw, washer with all accessories. Including cutting & making good the walls, floors, slab wherever required. (Material cost of required hinges, screws etc to be included in the item) | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1024 | 126.5664 | 0 | 1150.5664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 501020000 | Fixing, testing and commissioning of white vitreous china floor mounting type European water closet including Providing & Fixing of C.P. bolts, nuts, supporting arrangements, bakelite / poly propylene seat & cover(fixing only) with C.P. hinges & rubber buffers, complete with all accessories. Including cutting & making good the walls & floors wherever required. The item also includes Fixing, testing and commissioning of exposed viterious china low level cistern for WC, with dual flush facility complete with all necessary fittings, CP / GI flush pipes & accessories including all supports & making good. (Material cost of required hinges, screws etc to be included in the item) | [8 empty] | No. | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 893 | 110.3748 | 0 | 1003.3748 | 0 | 270911.196 | 270911.196 | 10 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 24111 | 2980.1196 | 0 | 27091.1196 | 27091.1196
3 | 501020000 | Fixing of white viterous china wall mounting / floor mounting type bidet with Providing & Fixing single tap hole and CP bolts, nuts and including providing & fixing hanging arrangements, 32 mm dia CP brass waste, 32 mm dia CP cast brass bottle flange and rubber adapter for waste connection complete including cutting and making good the walls, floors wherever required. | [8 empty] | No. | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 683 | 84.4188 | 0 | 767.4188 | 0 | 1534.8376 | 1534.8376 | 10 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 136.6 | 16.8838 | 0 | 153.4838 | 153.4838
4 | 501020000 | Fixing, testing and commissioning of mixer fitting for bidet complete with connection to spray outlet including cutting and making good the walls, floor wherever required. | [8 empty] | No. | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 368 | 45.4848 | 0 | 413.4848 | 0 | 826.9696 | 826.9696 | 10 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 73.6 | 9.097 | 0 | 82.697 | 82.697
5 | 501020000 | Fixing, testing & commissioning of dual type Concealed type flush valve (suitable for shaft / wall) fittings push button arrangement, 32 mm dia C.P. flush pipe with clamp and adapter, rubber joint, C.P. brass wall flange, elbow complete with all other accessories. Including connection to water closet & cutting and making good the walls wherever required. | [8 empty] | No. | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 473 | 58.4628 | 0 | 531.4628 | 0 | 7971.942 | 7971.942 | 10 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 709.5 | 87.6942 | 0 | 797.1942 | 797.1942
6 | 501020000 | Fixing, testing & commissioning of ABS Rinsing spray with regulator of approved quality with plastic flexible pipe 1.5 m long, wall hook complete as required. | [8 empty] | No. | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 12.978 | 0 | 117.978 | 0 | 31854.06 | 31854.06 | 10 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 2835 | 350.406 | 0 | 3185.406 | 3185.406
7 | 501020000 | Fixing first quality white vitreous china oval / round / square wash basin (size as per architectural drawing) for under counter mounting, including providing & fixing of specially fabricated CI / MS brackets, painted with two or three coats of enamel paint of approved shade over a coat of primer, 32 mm CP brass waste and CP brass cast bottle trap and pipe to wall with CP brass flange and rubber adopter for waste connection complete including filling gap between counter and wash basin with approved type poly sulphide sealant, cutting and making good the walls wherever required. | [8 empty] | No. | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 630 | 77.868 | 0 | 707.868 | 0 | 212360.4 | 212360.4 | 10 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 18900 | 2336.04 | 0 | 21236.04 | 21236.04
8 | 501020000 | Fixing first quality white vitreous china wall mounting wash basin (size as per architectural drawing) including providing & fixing specially fabricated CI / MS brackets, painted with two or three coats of enamel paint of approved shade over a coat of primer, 32 mm CP brass waste and CP brass cast bottle trap and pipe to wall with CP brass flange and rubber adopter for waste connection complete including and wash basin with approved type poly sulphide sealant, cutting and making good the walls wherever required. | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 683 | 84.4188 | 0 | 767.4188 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 501020000 | Fixing, testing and commissioning of vitreous china pedestal for wash basin complete recessed at the back for the reception of pipes and fittings. | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 263 | 32.5068 | 0 | 295.5068 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 501020000 | Fixing, testing and commissioning of C.P. brass single hole basin mixer with pop-up waste and brass nuts complete as required. | [8 empty] | No. | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 236 | 29.1696 | 0 | 265.1696 | 0 | 79550.88 | 79550.88 | 10 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 7080 | 875.088 | 0 | 7955.088 | 7955.088
11 | 501020000 | Fixing, testing and commissioning of three hole basin mixer with popup waste and brass nuts complete as required. | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 263 | 32.5068 | 0 | 295.5068 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 501020000 | Fixing sensor based automatic battery operated hot & cold water tap with solenoid valve at inlet, Doppler based sensor, control box complete with all flexible pipes & accessories. | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 263 | 32.5068 | 0 | 295.5068 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 501020000 | Fixing, testing & commissioning of C.P. brass eurometic self closing pillar tap. | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210 | 25.956 | 0 | 235.956 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 501020000 | Fixing, testing, and commissioning of bath tub completely leveled, including waste overflow set, chain plug, cast brass P/S trap with overflow arrangement, legs, grouting of legs etc with cement concrete all complete as required. | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14.1 | 501020000 | ( Cost of grouting material shall be included in the rate) | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14.2 | 501020000 | Apron type bath tub | [8 empty] | No. | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 1575 | 194.67 | 0 | 1769.67 | 0 | 44241.75 | 44241.75 | 10 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 3937.5 | 486.675 | 0 | 4424.175 | 4424.175
14.3 | 501020000 | Free standing bath tub | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1575 | 194.67 | 0 | 1769.67 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14.4 | 501020000 | Bath Tub Spout / Spout | [8 empty] | No. | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 473 | 58.4628 | 0 | 531.4628 | 0 | 13286.57 | 13286.57 | 10 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 1182.5 | 146.157 | 0 | 1328.657 | 1328.657
14.5 | 501020000 | Deck mount bath tub mixer with spout and telephonic hand shower. | [8 empty] | No. | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 578 | 71.4408 | 0 | 649.4408 | 0 | 16236.02 | 16236.02 | 10 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 1445 | 178.602 | 0 | 1623.602 | 1623.602
15 | 501020000 | Fixing, testing and commissioning of bathing facucets including necessary wall chases and making good. | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15.1 | 501020000 | Concealed bath shower divertor, faucet, 115 mm long bend pipe, overhead shower and wall flanges complete. | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 263 | 32.5068 | 0 | 295.5068 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15.2 | 501020000 | Single lever wall divertor assembly with non-return valves | [8 empty] | No. | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 236 | 29.1696 | 0 | 265.1696 | 0 | 58337.312 | 58337.312 | 10 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 5192 | 641.7312 | 0 | 5833.7312 | 5833.7312
15.3 | 501020000 | Concealed stop valves with wall flanges | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 19.5288 | 0 | 177.5288 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15.4 | 501020000 | Overhead shower with short / long arm and wall flange | [8 empty] | No. | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 19.5288 | 0 | 177.5288 | 0 | 4438.22 | 4438.22 | 10 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 395 | 48.822 | 0 | 443.822 | 443.822
15.5 | 501020000 | Overhead drencher shower, ceiling mounted | [8 empty] | No. | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 19.5288 | 0 | 177.5288 | 0 | 37281.048 | 37281.048 | 10 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 3318 | 410.1048 | 0 | 3728.1048 | 3728.1048
16 | 501020000 | Fixing of SS 304 SS shower channel with grating (polished surface), socket type outlet (50 mm dia), slope towards socket, effective tray depth 20 mm, width 70 mm approximate 900 following length. | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16.1 | 501020000 | 900 mm Length | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 473 | 58.4628 | 0 | 531.4628 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16.2 | 501020000 | 1000 mm Length | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578 | 71.4408 | 0 | 649.4408 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 501020000 | Fixing, testing and commissioning of white viterous china large flat back / half stall urinal including providing & fixing CI / MS bracket (duly painted with 2 coats of paints over a coat of primer), including CP brass waste with dome type grating, CP cast brass bottle trap with extension piece, wall flanges complete with all accessories. | [8 empty] | No. | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 788 | 97.3968 | 0 | 885.3968 | 0 | 22134.92 | 22134.92 | 10 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 1970 | 243.492 | 0 | 2213.492 | 2213.492
18 | 501020000 | Fixing, testing and commissioning of white vitreous china large urinal partition including providing & fixing concealed CI bracket, cutting and making good. | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 263 | 32.5068 | 0 | 295.5068 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 501020000 | Fixing, testing and commissioning of automatic flushing systems for urinal to ensure pre-flush & flushing only immediately after use, comprising of all plumbing, electronic and electrical items. CP brass flush pipe with CP brass elbow, CP brass spreader, CP wall flange, infrared photo cells, eyes electrically operated solenoid valve, step down transformer / equipment and any other item required to provide satisfactory functioning. Including necessary wall cutting / chasing and making good, as required. | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 578 | 71.4408 | 0 | 649.4408 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 501020000 | Fixing battery operated automatic urinal flushing systems for urinal flushing complete as mentioned above. | [8 empty] | No. | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 394 | 48.6984 | 0 | 442.6984 | 0 | 11067.46 | 11067.46 | 10 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 985 | 121.746 | 0 | 1106.746 | 1106.746
21 | 501020000 | Fixing, testing & commissioning of white acrylic shower tray of size 780x780x125 mm deep with C.P. brass waste, C.I lugs and all other accessories complete as required. | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 473 | 58.4628 | 0 | 531.4628 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 501020000 | Fixing, testing and commissioning of sink including providing & fixing C.I./M.S. Brackets (duly painted with 2 coats of paint over a coat of primer) C.P. cast brass bottle trap with extension piece, rubber adaptor, wall flange, union, C.P. brass chainrubber plug & making good. | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22.1 | 501020000 | Stainless Steel sink w/o drain board | [8 empty] | No. | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 604 | 74.6544 | 0 | 678.6544 | 0 | 10179.816 | 10179.816 | 10 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 906 | 111.9816 | 0 | 1017.9816 | 1017.9816
22.2 | 501020000 | Stainless steel sink with drain board. | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 788 | 97.3968 | 0 | 885.3968 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22.3 | 501020000 | Sainless sink with double drain board | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 840 | 103.824 | 0 | 943.824 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 501020000 | Providing, fixing, testing and commissioning of C.P. brass wall / counter mounted sink mixer with C.P. wall flange, overhead swinging spout complete as required and making good. | [8 empty] | No. | 20 | 4344 | 0 | 4344 | 217.2 | 0 | 4561.2 | 210 | 25.956 | 0 | 235.956 | 91224 | 4719.12 | 95943.12 | 10 | 20 | 8688 | 0 | 8688 | 434.4 | 0 | 9122.4 | 420 | 51.912 | 0 | 471.912 | 9594.312
24 | 501020000 | Providing, fixing of white viterous china Janitor sink of size 470 x 370 x 180mm deep including providing & fixing CI/MS brackets (duly painted with 2 coats of paint over a coat of primer) C.P. cast brass bottle trap with extension piece, rubber adopter, wall flange, union, C.P. brass chain rubber plug complete as required. | [8 empty] | No. | 5 | 5322 | 0 | 5322 | 266.1 | 0 | 5588.1 | 420 | 51.912 | 0 | 471.912 | 27940.5 | 2359.56 | 30300.06 | 10 | 5 | 2661 | 0 | 2661 | 133.05 | 0 | 2794.05 | 210 | 25.956 | 0 | 235.956 | 3030.006
25 | 501020000 | Fixing storage type water heater of approved shade with copper container, glasswool insulation,stove enamelled M.S jacket, thermostatically controlled inner heater with pilot neon lamps, angle valve on inlet connection, 15mm dia C.P flexible connection pipe in inlet & outlet suitable for working pressure of 5 kg/sqcm complete as required. | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25.1 | 501020000 | Capacity 15 litres | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 263 | 32.5068 | 0 | 295.5068 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25.2 | 501020000 | Capacity 25 litres | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 368 | 45.4848 | 0 | 413.4848 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 501020000 | Fixing storage type water cooler of the following capacity, I.S.I marked, stainless steel front panel, C.P brass push cock, inlet float valve with all plumbing and electrical accessories, inlet, outlet, overflow and PVC drain out connection to F.D complete as required. | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26.1 | 501020000 | Cooling capacity 15 Lts./hr Storage capacity 40 Lts. | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 525 | 64.89 | 0 | 589.89 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26.2 | 501020000 | Cooling capacity 40Lts./hr Storage capacity 80 Lts. | [8 empty] | No. | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 683 | 84.4188 | 0 | 767.4188 | 0 | 1534.8376 | 1534.8376 | 10 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 136.6 | 16.8838 | 0 | 153.4838 | 153.4838
27 | 501020000 | Providing , fixing commercial water purifier of water flow rate 2.0 Lit/min. Including all components as per manufacture specifications, including connection from water supply line, and final connection to water cooler electric wiring & plug top etc. with all accessories. | [8 empty] | No. | 7 | 15250 | 0 | 15250 | 762.5 | 0 | 16012.5 | 473 | 58.4628 | 0 | 531.4628 | 112087.5 | 3720.2396 | 115807.7396 | 10 | 7 | 10675 | 0 | 10675 | 533.75 | 0 | 11208.75 | 331.1 | 40.924 | 0 | 372.024 | 11580.774
28 | 501020000 | Fixing solid state, no touch operting, fully hygienic hand drier of approved shade with single blower, with time delay, summer & winter control, volume ON/OFF controls including providing necessary brackets, cable from drier to Plug, Plug top key and lock etc, complete as required. | [8 empty] | No. | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 38.934 | 0 | 353.934 | 0 | 5309.01 | 5309.01 | 10 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 472.5 | 58.401 | 0 | 530.901 | 530.901
29 | 501020000 | Fixing solid state, no touch operating, fully hygienic hand drier of approved shade with double blower, continous repeat usage,time delay, summer & winter control including providing necessary brackets, cable from drier to Plug, Plug to key and lock etc. complete as required. | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 51.912 | 0 | 471.912 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | 501020000 | Fixing S.S. toilet paper holder with PVC rawl plug & C.P. brass screw complete as required. | [8 empty] | No. | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 9.7644 | 0 | 88.7644 | 0 | 23966.388 | 23966.388 | 10 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 2133 | 263.6388 | 0 | 2396.6388 | 2396.6388
31 | 501020000 | Fixing S.S. reserve toilet paper holder with PVC rawl plug & C.P. brass screw complete as required. | [8 empty] | No. | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 9.7644 | 0 | 88.7644 | 0 | 18640.524 | 18640.524 | 10 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 1659 | 205.0524 | 0 | 1864.0524 | 1864.0524
32 | 501020000 | Fixing Recessed type S.S. soap dish with PVC rawl plug & C.P. brass screw complete as required. | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 12.978 | 0 | 117.978 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | 501020000 | Fixing C.P. brass liquid soap container with PVC rawl plug & C.P. brass screw complete as required. | [8 empty] | No. | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 12.978 | 0 | 117.978 | 0 | 1179.78 | 1179.78 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 12.978 | 0 | 117.978 | 117.978
34 | 501020000 | Fixing push type liquid soap dispenser with PVC rawl plug & C.P. brass screw complete as required. | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 12.978 | 0 | 117.978 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | 501020000 | Fixing C.P. brass twin coat hook with PVC rawl plug & C.P. brass screw complete as required. | [8 empty] | No. | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 6.5508 | 0 | 59.5508 | 0 | 16078.716 | 16078.716 | 10 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 1431 | 176.8716 | 0 | 1607.8716 | 1607.8716
36 | 501020000 | Fixing C.P brass deodourizer. | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131 | 16.1916 | 0 | 147.1916 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | 501020000 | Fixing deodoriser system with turbo fan, battery & cartridge including wall mounting arrangement complete as required. | [8 empty] | No. | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 263 | 32.5068 | 0 | 295.5068 | 0 | 7387.67 | 7387.67 | 10 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 657.5 | 81.267 | 0 | 738.767 | 738.767
38 | 501020000 | Fixing towel rack deluxe with PVC rawl plug & C.P. brass screw complete as required of size Size 230 x 600 mm | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 19.5288 | 0 | 177.5288 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
39 | 501020000 | Fixing, testing and commissioning of 15 mm dia C.P. brass 2 way angle valve with C.P. wall flange of approved quality and making good. | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 12.978 | 0 | 117.978 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40 | 501020000 | Fixing, testing and commissioning of 15 mm dia C.P. brass bib cock with C.P. wall flange of approved quality and making good as required. | [8 empty] | No. | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 12.978 | 0 | 117.978 | 0 | 1179.78 | 1179.78 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 12.978 | 0 | 117.978 | 117.978
41 | 501020000 | Fixing, testing and commissioning of C.P. brass angle valve with C.P. wall flange, Nut and Washer etc. complete as required. | [8 empty] | No. | 1170 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 10.3824 | 0 | 94.3824 | 0 | 110427.408 | 110427.408 | 10 | 1170 | 0 | 0 | 0 | 0 | 0 | 0 | 9828 | 1214.7408 | 0 | 11042.7408 | 11042.7408
42 | 501020000 | Fixing, testing and commissioning of C.P Copper connection 375 mm long including nuts and washers and making connection to fixtures and fittings complete as required. | [8 empty] | No. | 870 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 12.978 | 0 | 117.978 | 0 | 102640.86 | 102640.86 | 10 | 870 | 0 | 0 | 0 | 0 | 0 | 0 | 9135 | 1129.086 | 0 | 10264.086 | 10264.086
43 | 501020000 | Fixing, testing and commissioning of pillar cock for sinks and making good as required. | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 12.978 | 0 | 117.978 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
44 | 501020000 | Fixing Jacuzzi-whirl pool bath system consist the following items. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
45 | 501020000 | 1 No. Acrylic bath tub of 1780 mm dia with bottom supports.6 Nos CP brass venturi jets with revolving outlet.ON/OFF switch, ELCB, control wiring & cabling.2 HP motor pump set with electronic device to prevent the motor from running dry.Air controller, suction outlet.Automatic waste cum over flow with cast brass P/S trap and all necessary fittings and final connection to F.D.PVC pipe connecting to the system.C.P brass bath mixer (bath tub mounted) with telephonic shower, stand & crutch. Bath System as described above | [8 empty] | Set | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46 | 501020000 | Fixing adjustable type wash basin for handicap toilet complete with brackets, tracks, waste pipes and other accessories complete as required. | [8 empty] | No. | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 998 | 123.3528 | 0 | 1121.3528 | 0 | 4485.4112 | 4485.4112 | 10 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 399.2 | 49.3411 | 0 | 448.5411 | 448.5411
47 | 501020000 | Fixing 2 Nos. support arms and backrest to mounted on the track (vertically and laterally) for handicap toilet complete as required. | [8 empty] | No. | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 38.934 | 0 | 353.934 | 0 | 1415.736 | 1415.736 | 10 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 15.5736 | 0 | 141.5736 | 141.5736
48 | 501020000 | Fixing raised toilet seat with cover for handicap toilet | [8 empty] | No. | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 263 | 32.5068 | 0 | 295.5068 | 0 | 1182.0272 | 1182.0272 | 10 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 105.2 | 13.0027 | 0 | 118.2027 | 118.2027
49 | 501020000 | Fixing 35 mm dia powder coated steel grab bar. | [8 empty] | No. | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 210 | 25.956 | 0 | 235.956 | 0 | 943.824 | 943.824 | 10 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 10.3824 | 0 | 94.3824 | 94.3824
50 | 501020000 | Fixing shower chair comprising of individual seat & bank completely adjustable, counter balanced fold & hold mechanisum | [8 empty] | No. | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 368 | 45.4848 | 0 | 413.4848 | 0 | 1653.9392 | 1653.9392 | 10 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 147.2 | 18.1939 | 0 | 165.3939 | 165.3939
B | 501030000 | COLD WATER SUPPLY : (INTERNAL / EXTERNAL) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 501030000 | Providing, fixing,commissioning & testing ( at required pressure) CPVC (Chlorinated Poly Vinyl Chloride) water supply pipes with pipe as per CTS SDR 11 (operating pressure - 7 Bar @ 82 Deg C and 28 Bar @ 23 Deg C)for pipes from 1/2 Inch to 2 Inch. Schedule 40 Pipe to be used from 2-1/2 Inch to 6 Inch. Pipes shall be joined using solvent welded CPVC fittings i.e. Tees, Elbows, Couplers, Unions, Reducers, brushings etc. including transition fittings (connection between CPVC & metal pipe/GI) i.e. Brass Adaptors (both Male & Female threaded) conforming to ASTM D-2846. ASTM F441 with only CPVC solvent cement conforming to ASTM F-493. All termination points for installation of faucets shall have brass termination fittings. Installation shall be to as per Technical Manual of manufacturer of pipes & fittings.Cost shall be inclusive of (a)Making maximum of 7.5 x 7.5 cm chase in wall and floors for the pipe, making good the same by using 1:2 cement mortar over the wire mesh complete as required or (b) Fixing/supporting the pipes (& fittings) at wall/ceiling level supported by galvanized clamps, fastener, hangers etc, as per specification. Exposed pipes to be painted of legends with direction arrow. M.S. pipe sleeves suitable higher size shall be provided wherever the pipes are crossing the fire rated walls / floors slab and sealing the sleeves with glass wool in between and fire sealant compound at either end all as per Project Managers / Consultant requirement. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.1 | 501030000 | 1/2" dia (15 mm) | [8 empty] | RM | 5500 | 102 | 0 | 102 | 5.1 | 0 | 107.1 | 41 | 5.0676 | 0 | 46.0676 | 589050 | 253371.8 | 842421.8 | 10 | 5500 | 56100 | 0 | 56100 | 2805 | 0 | 58905 | 22550 | 2787.18 | 0 | 25337.18 | 84242.18
1.1 | 501030000 | 1/2" dia (15 mm) | [8 empty] | RM | 5500 | 102 | 0 | 102 | 5.1 | 0 | 107.1 | 41 | 5.0676 | 0 | 46.0676 | 589050 | 253371.8 | 842421.8 | 60 | 2484 | 152020.8 | 0 | 152020.8 | 7601.04 | 0 | 159621.84 | 0 | 0 | 0 | 0 | 159621.84
1.2 | 501030000 | 3/4" dia (20 mm | [8 empty] | RM | 3500 | 163 | 0 | 163 | 8.15 | 0 | 171.15 | 41 | 5.0676 | 0 | 46.0676 | 599025 | 161236.6 | 760261.6 | 10 | 3500 | 57050 | 0 | 57050 | 2852.5 | 0 | 59902.5 | 14350 | 1773.66 | 0 | 16123.66 | 76026.16
1.2 | 501030000 | 3/4" dia (20 mm | [8 empty] | RM | 3500 | 163 | 0 | 163 | 8.15 | 0 | 171.15 | 41 | 5.0676 | 0 | 46.0676 | 599025 | 161236.6 | 760261.6 | 60 | 1545 | 151101 | 0 | 151101 | 7555.05 | 0 | 158656.05 | 0 | 0 | 0 | 0 | 158656.05
1.3 | 501030000 | 1" dia (25 mm) a | [8 empty] | RM | 2000 | 228 | 0 | 228 | 11.4 | 0 | 239.4 | 51 | 6.3036 | 0 | 57.3036 | 478800 | 114607.2 | 593407.2 | 10 | 2000 | 45600 | 0 | 45600 | 2280 | 0 | 47880 | 10200 | 1260.72 | 0 | 11460.72 | 59340.72
1.3 | 501030000 | 1" dia (25 mm) a | [8 empty] | RM | 2000 | 228 | 0 | 228 | 11.4 | 0 | 239.4 | 51 | 6.3036 | 0 | 57.3036 | 478800 | 114607.2 | 593407.2 | 60 | 518 | 70862.4 | 0 | 70862.4 | 3543.12 | 0 | 74405.52 | 0 | 0 | 0 | 0 | 74405.52
1.4 | 501030000 | 1.1/4" dia (32 mm) | [8 empty] | RM | 1200 | 327 | 0 | 327 | 16.35 | 0 | 343.35 | 56 | 6.9216 | 0 | 62.9216 | 412020 | 75505.92 | 487525.92 | 10 | 1200 | 39240 | 0 | 39240 | 1962 | 0 | 41202 | 6720 | 830.592 | 0 | 7550.592 | 48752.592
1.4 | 501030000 | 1.1/4" dia (32 mm) | [8 empty] | RM | 1200 | 327 | 0 | 327 | 16.35 | 0 | 343.35 | 56 | 6.9216 | 0 | 62.9216 | 412020 | 75505.92 | 487525.92 | 60 | 483 | 94764.6 | 0 | 94764.6 | 4738.23 | 0 | 99502.83 | 0 | 0 | 0 | 0 | 99502.83
1.5 | 501030000 | 1.1/2: dia (40 mm | [8 empty] | RM | 700 | 425 | 0 | 425 | 21.25 | 0 | 446.25 | 77 | 9.5172 | 0 | 86.5172 | 312375 | 60562.04 | 372937.04 | 10 | 700 | 29750 | 0 | 29750 | 1487.5 | 0 | 31237.5 | 5390 | 666.204 | 0 | 6056.204 | 37293.704
1.5 | 501030000 | 1.1/2: dia (40 mm | [8 empty] | RM | 700 | 425 | 0 | 425 | 21.25 | 0 | 446.25 | 77 | 9.5172 | 0 | 86.5172 | 312375 | 60562.04 | 372937.04 | 60 | 212 | 54060 | 0 | 54060 | 2703 | 0 | 56763 | 0 | 0 | 0 | 0 | 56763
1.6 | 501030000 | 2" dia (50 mm | [8 empty] | RM | 350 | 660 | 0 | 660 | 33 | 0 | 693 | 92 | 11.3712 | 0 | 103.3712 | 242550 | 36179.92 | 278729.92 | 10 | 350 | 23100 | 0 | 23100 | 1155 | 0 | 24255 | 3220 | 397.992 | 0 | 3617.992 | 27872.992
1.6 | 501030000 | 2" dia (50 mm | [8 empty] | RM | 350 | 660 | 0 | 660 | 33 | 0 | 693 | 92 | 11.3712 | 0 | 103.3712 | 242550 | 36179.92 | 278729.92 | 60 | 188 | 74448 | 0 | 74448 | 3722.4 | 0 | 78170.4 | 0 | 0 | 0 | 0 | 78170.4
1.7 | 501030000 | 2.1/2" dia (65 mm) | [8 empty] | RM | 200 | 1300 | 0 | 1300 | 65 | 0 | 1365 | 128 | 15.8208 | 0 | 143.8208 | 273000 | 28764.16 | 301764.16 | 10 | 200 | 26000 | 0 | 26000 | 1300 | 0 | 27300 | 2560 | 316.416 | 0 | 2876.416 | 30176.416
1.7 | 501030000 | 2.1/2" dia (65 mm) | [8 empty] | RM | 200 | 1300 | 0 | 1300 | 65 | 0 | 1365 | 128 | 15.8208 | 0 | 143.8208 | 273000 | 28764.16 | 301764.16 | 60 | 200 | 156000 | 0 | 156000 | 7800 | 0 | 163800 | 0 | 0 | 0 | 0 | 163800
1.8 | 501030000 | 3" dia (80 mm | [8 empty] | RM | 200 | 1980 | 0 | 1980 | 99 | 0 | 2079 | 154 | 19.0344 | 0 | 173.0344 | 415800 | 34606.88 | 450406.88 | 10 | 200 | 39600 | 0 | 39600 | 1980 | 0 | 41580 | 3080 | 380.688 | 0 | 3460.688 | 45040.688
1.8 | 501030000 | 3" dia (80 mm | [8 empty] | RM | 200 | 1980 | 0 | 1980 | 99 | 0 | 2079 | 154 | 19.0344 | 0 | 173.0344 | 415800 | 34606.88 | 450406.88 | 60 | 42 | 49896 | 0 | 49896 | 2494.8 | 0 | 52390.8 | 0 | 0 | 0 | 0 | 52390.8
1.9 | 501030000 | 4" dia (100 mm | [8 empty] | RM | 250 | 2870 | 0 | 2870 | 143.5 | 0 | 3013.5 | 200 | 24.72 | 0 | 224.72 | 753375 | 56180 | 809555 | 10 | 250 | 71750 | 0 | 71750 | 3587.5 | 0 | 75337.5 | 5000 | 618 | 0 | 5618 | 80955.5
1.9 | 501030000 | 4" dia (100 mm | [8 empty] | RM | 250 | 2870 | 0 | 2870 | 143.5 | 0 | 3013.5 | 200 | 24.72 | 0 | 224.72 | 753375 | 56180 | 809555 | 60 | 189 | 325458 | 0 | 325458 | 16272.9 | 0 | 341730.9 | 0 | 0 | 0 | 0 | 341730.9
1.1 | 501030000 | 6" dia (150 mm | [8 empty] | RM | 0 | 4700 | 0 | 4700 | 235 | 0 | 4935 | 315 | 38.934 | 0 | 353.934 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 501030000 | Providing, fixing, commissioning & testing male/ female screwed end full way lever operated forged brass ball valve of brass body with forged brass hard chromeplated ball & teflon seat tested to a pressure 30 Kg / sqcm with (threaded joints) complete as required. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.1 | 501030000 | 15 mm di | [8 empty] | No. | 250 | 266 | 0 | 266 | 13.3 | 0 | 279.3 | 72 | 8.8992 | 0 | 80.8992 | 69825 | 20224.8 | 90049.8 | 10 | 250 | 6650 | 0 | 6650 | 332.5 | 0 | 6982.5 | 1800 | 222.48 | 0 | 2022.48 | 9004.98
2.1 | 501030000 | 15 mm di | [8 empty] | No. | 250 | 266 | 0 | 266 | 13.3 | 0 | 279.3 | 72 | 8.8992 | 0 | 80.8992 | 69825 | 20224.8 | 90049.8 | 60 | 2 | 319.2 | 0 | 319.2 | 15.96 | 0 | 335.16 | 0 | 0 | 0 | 0 | 335.16
2.2 | 501030000 | 20 mm di | [8 empty] | No. | 15 | 382 | 0 | 382 | 19.1 | 0 | 401.1 | 72 | 8.8992 | 0 | 80.8992 | 6016.5 | 1213.488 | 7229.988 | 10 | 15 | 573 | 0 | 573 | 28.65 | 0 | 601.65 | 108 | 13.3488 | 0 | 121.3488 | 722.9988
2.3 | 501030000 | 25 mm di | [8 empty] | No. | 240 | 594 | 0 | 594 | 29.7 | 0 | 623.7 | 103 | 12.7308 | 0 | 115.7308 | 149688 | 27775.392 | 177463.392 | 10 | 240 | 14256 | 0 | 14256 | 712.8 | 0 | 14968.8 | 2472 | 305.5392 | 0 | 2777.5392 | 17746.3392
2.3 | 501030000 | 25 mm di | [8 empty] | No. | 240 | 594 | 0 | 594 | 29.7 | 0 | 623.7 | 103 | 12.7308 | 0 | 115.7308 | 149688 | 27775.392 | 177463.392 | 60 | 4 | 1425.6 | 0 | 1425.6 | 71.28 | 0 | 1496.88 | 0 | 0 | 0 | 0 | 1496.88
2.4 | 501030000 | 32 mm di | [8 empty] | No. | 15 | 1055 | 0 | 1055 | 52.75 | 0 | 1107.75 | 128 | 15.8208 | 0 | 143.8208 | 16616.25 | 2157.312 | 18773.562 | 10 | 15 | 1582.5 | 0 | 1582.5 | 79.125 | 0 | 1661.625 | 192 | 23.7312 | 0 | 215.7312 | 1877.3562
2.4 | 501030000 | 32 mm di | [8 empty] | No. | 15 | 1055 | 0 | 1055 | 52.75 | 0 | 1107.75 | 128 | 15.8208 | 0 | 143.8208 | 16616.25 | 2157.312 | 18773.562 | 60 | 2 | 1266 | 0 | 1266 | 63.3 | 0 | 1329.3 | 0 | 0 | 0 | 0 | 1329.3
2.5 | 501030000 | 40 mm d | [8 empty] | No. | 35 | 1528 | 0 | 1528 | 76.4 | 0 | 1604.4 | 158 | 19.5288 | 0 | 177.5288 | 56154 | 6213.508 | 62367.508 | 10 | 35 | 5348 | 0 | 5348 | 267.4 | 0 | 5615.4 | 553 | 68.3508 | 0 | 621.3508 | 6236.7508
2.6 | 501030000 | 50 mm a | [8 empty] | No. | 25 | 2321 | 0 | 2321 | 116.05 | 0 | 2437.05 | 210 | 25.956 | 0 | 235.956 | 60926.25 | 5898.9 | 66825.15 | 10 | 25 | 5802.5 | 0 | 5802.5 | 290.125 | 0 | 6092.625 | 525 | 64.89 | 0 | 589.89 | 6682.515
3 | 501030000 | Providing, fixing & commissioning C.I. Butterfly valve (Body : Grey Cast Iron, shaft : SS, Disc : SG Iron (nickel plated), Liner : HT - EPDM) of approved make with flange, washer, nuts & bolts and PN 10 pressure rating including rubber gasket & painting complete. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.1 | 501030000 | 50 mm | [8 empty] | No. | 0 | 3360 | 0 | 3360 | 168 | 0 | 3528 | 263 | 32.5068 | 0 | 295.5068 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.2 | 501030000 | 65 mm di | [8 empty] | No. | 0 | 3732 | 0 | 3732 | 186.6 | 0 | 3918.6 | 341 | 42.1476 | 0 | 383.1476 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.3 | 501030000 | 80mm | [8 empty] | No. | 0 | 4440 | 0 | 4440 | 222 | 0 | 4662 | 420 | 51.912 | 0 | 471.912 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.4 | 501030000 | 100 mm di | [8 empty] | No. | 0 | 5820 | 0 | 5820 | 291 | 0 | 6111 | 525 | 64.89 | 0 | 589.89 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.5 | 501030000 | 150 mm d | [8 empty] | No. | 0 | 8640 | 0 | 8640 | 432 | 0 | 9072 | 788 | 97.3968 | 0 | 885.3968 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 501030000 | Providing & fixing C.I. wafer type check valve of rating PN 10 including rubber gasket, flanges, union, nuts, bolts, washers & painting complete as required. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4.1 | 501030000 | 50 mm d | [8 empty] | No. | 9 | 3136 | 0 | 3136 | 156.8 | 0 | 3292.8 | 258 | 31.8888 | 0 | 289.8888 | 29635.2 | 2608.9992 | 32244.1992 | 10 | 9 | 2822.4 | 0 | 2822.4 | 141.12 | 0 | 2963.52 | 232.2 | 28.6999 | 0 | 260.8999 | 3224.4199
4.2 | 501030000 | 65 mm d | [8 empty] | No. | 6 | 3626 | 0 | 3626 | 181.3 | 0 | 3807.3 | 334 | 41.2824 | 0 | 375.2824 | 22843.8 | 2251.6944 | 25095.4944 | 10 | 6 | 2175.6 | 0 | 2175.6 | 108.78 | 0 | 2284.38 | 200.4 | 24.7694 | 0 | 225.1694 | 2509.5494
4.3 | 501030000 | 80 mm d | [8 empty] | No. | 5 | 4331 | 0 | 4331 | 216.55 | 0 | 4547.55 | 412 | 50.9232 | 0 | 462.9232 | 22737.75 | 2314.616 | 25052.366 | 10 | 5 | 2165.5 | 0 | 2165.5 | 108.275 | 0 | 2273.775 | 206 | 25.4616 | 0 | 231.4616 | 2505.2366
4.4 | 501030000 | 100 mm d | [8 empty] | No. | 4 | 5635 | 0 | 5635 | 281.75 | 0 | 5916.75 | 515 | 63.654 | 0 | 578.654 | 23667 | 2314.616 | 25981.616 | 10 | 4 | 2254 | 0 | 2254 | 112.7 | 0 | 2366.7 | 206 | 25.4616 | 0 | 231.4616 | 2598.1616
4.5 | 501030000 | 150 mm | [8 empty] | No. | 0 | 8200 | 0 | 8200 | 410 | 0 | 8610 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 501030000 | Providing & fixing dual flanged C.I. Y Strainer with stainless steel fine wire mesh perforated sheet basket with necessary flange/ unions nuts, bolts and washers complete as required. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.1 | 501030000 | 65 mm di | [8 empty] | No. | 0 | 3732 | 0 | 3732 | 186.6 | 0 | 3918.6 | 341 | 42.1476 | 0 | 383.1476 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.2 | 501030000 | 80 mm | [8 empty] | No. | 0 | 4542 | 0 | 4542 | 227.1 | 0 | 4769.1 | 420 | 51.912 | 0 | 471.912 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.3 | 501030000 | 100 mm di | [8 empty] | No. | 0 | 6936 | 0 | 6936 | 346.8 | 0 | 7282.8 | 525 | 64.89 | 0 | 589.89 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.4 | 501030000 | 150 mm d | [8 empty] | No. | 0 | 12816 | 0 | 12816 | 640.8 | 0 | 13456.8 | 788 | 97.3968 | 0 | 885.3968 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 501030000 | Providing & fixing of gun metal screwed ended Y type strainer with SS fine wire mash/ perforated sheet with necessary fitting complete as required. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6.1 | 501030000 | 40 mm di | [8 empty] | No | 0 | 3725 | 0 | 3725 | 186.25 | 0 | 3911.25 | 210 | 25.956 | 0 | 235.956 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6.2 | 501030000 | 50 mm di | [8 empty] | No | 0 | 4800 | 0 | 4800 | 240 | 0 | 5040 | 263 | 32.5068 | 0 | 295.5068 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 501030000 | Providing and fixing in position of approved quality high pressure rated Gun Metal Float Valve with copper ball float and brass rods of required length suitable for test pressure of not less than 15 Kg/sqcm of the following sizes: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7.1 | 501030000 | 40 mm diaa | [8 empty] | No. | 2 | 3273 | 0 | 3273 | 163.65 | 0 | 3436.65 | 206 | 25.4616 | 0 | 231.4616 | 6873.3 | 462.9232 | 7336.2232 | 10 | 2 | 654.6 | 0 | 654.6 | 32.73 | 0 | 687.33 | 41.2 | 5.0923 | 0 | 46.2923 | 733.6223
7.2 | 501030000 | 50 mm dia b | [8 empty] | No. | 2 | 5791 | 0 | 5791 | 289.55 | 0 | 6080.55 | 258 | 31.8888 | 0 | 289.8888 | 12161.1 | 579.7776 | 12740.8776 | 10 | 2 | 1158.2 | 0 | 1158.2 | 57.91 | 0 | 1216.11 | 51.6 | 6.3778 | 0 | 57.9778 | 1274.0878
7.3 | 501030000 | 80 mm di | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7.4 | 501030000 | 100 mm dia | [8 empty] | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 501030000 | Providing and fixing heavy duty floating flange EPDM rubber expansion joint with unit control (tie rod & gusset plate) as per manufacturers specifications of standard length complete with all accessories tested to a pressure not less than 15 Kg./sqcm including rubber gaskets, flanges, nuts, bolts & washers complete as required. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8.1 | 501030000 | 50 mm dia | [8 empty] | No. | 0 | 3715 | 0 | 3715 | 185.75 | 0 | 3900.75 | 158 | 19.5288 | 0 | 177.5288 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8.2 | 501030000 | 65 mm dia | [8 empty] | No. | 0 | 4100 | 0 | 4100 | 205 | 0 | 4305 | 210 | 25.956 | 0 | 235.956 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8.3 | 501030000 | 80 mm dia | [8 empty] | No. | 0 | 4465 | 0 | 4465 | 223.25 | 0 | 4688.25 | 252 | 31.1472 | 0 | 283.1472 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8.4 | 501030000 | 100 mm dia | [8 empty] | No. | 0 | 5805 | 0 | 5805 | 290.25 | 0 | 6095.25 | 315 | 38.934 | 0 | 353.934 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8.5 | 501030000 | 150 mm dia | [8 empty] | No. | 0 | 7530 | 0 | 7530 | 376.5 | 0 | 7906.5 | 473 | 58.4628 | 0 | 531.4628 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 501030000 | Providing and fixing pressure reducing station for cold water supply comprising of 2 Nos PRV,4Nos Gun Metal ball valves on inlet & outlet & Screwed connection, 2 No. Y strainer, 2 Nos Pressure gauge on inlet & outlet, and 1 No. 15 mm dia safety valve. The complete system is tested to a pressure not less than 15 Kg/Sq.cm and suitable to reduce the pressure upto 2 Kg/Sq.cm) Including necessary pipe & fittings; i.e. flanges/ unions, nuts, bolts and washers complete as required. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.1 | 501030000 | 25 mm dia (Brass Housing - PRV) | [8 empty] | No. | 0 | 12810 | 0 | 12810 | 640.5 | 0 | 13450.5 | 525 | 64.89 | 0 | 589.89 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.2 | 501030000 | 32 mm dia (Brass Housing - PRV) a | [8 empty] | No. | 5 | 15648 | 0 | 15648 | 782.4 | 0 | 16430.4 | 658 | 81.3288 | 0 | 739.3288 | 82152 | 3696.644 | 85848.644 | 10 | 5 | 7824 | 0 | 7824 | 391.2 | 0 | 8215.2 | 329 | 40.6644 | 0 | 369.6644 | 8584.8644
9.3 | 501030000 | 40 mm dia (CI Housing - PRV) | [8 empty] | No. | 10 | 19400 | 0 | 19400 | 970 | 0 | 20370 | 823.2 | 101.7475 | 0 | 924.9475 | 203700 | 9249.4752 | 212949.4752 | 10 | 10 | 19400 | 0 | 19400 | 970 | 0 | 20370 | 823.2 | 101.7475 | 0 | 924.9475 | 21294.9475
9.4 | 501030000 | 50 mm dia (CI Housing - PRV) | [8 empty] | No. | 2 | 27165 | 0 | 27165 | 1358.25 | 0 | 28523.25 | 1029 | 127.1844 | 0 | 1156.1844 | 57046.5 | 2312.3688 | 59358.8688 | 10 | 2 | 5433 | 0 | 5433 | 271.65 | 0 | 5704.65 | 205.8 | 25.4369 | 0 | 231.2369 | 5935.8869
9.5 | 501030000 | 65 mm dia (CI Housing - PRV) | [8 empty] | No. | 0 | 46335 | 0 | 46335 | 2316.75 | 0 | 48651.75 | 1365 | 168.714 | 0 | 1533.714 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 501030000 | Providing, fixing , testing and commissioning water meter with direct reading dial in KL with all necessary fitting such as threaded pieces, unions pressure gauge, isolation cock, flanges piece for future removal, flanges / unions complete with all necessary testing charges and obtaining test certificates from municipal authorities, on following size pipe lines (1 no. strainer shall be provided at inlet & outlet and cost shall be inclusive for the same). | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10.1 | 501030000 | 50 mm dia (CI) | [8 empty] | No. | 2 | 8584 | 0 | 8584 | 429.2 | 0 | 9013.2 | 1235 | 152.646 | 0 | 1387.646 | 18026.4 | 2775.292 | 20801.692 | 10 | 2 | 1716.8 | 0 | 1716.8 | 85.84 | 0 | 1802.64 | 247 | 30.5292 | 0 | 277.5292 | 2080.1692
10.2 | 501030000 | 65 mm dia (CI) | [8 empty] | No. | 3 | 11387 | 0 | 11387 | 569.35 | 0 | 11956.35 | 1544 | 190.8384 | 0 | 1734.8384 | 35869.05 | 5204.5152 | 41073.5652 | 10 | 3 | 3416.1 | 0 | 3416.1 | 170.805 | 0 | 3586.905 | 463.2 | 57.2515 | 0 | 520.4515 | 4107.3565
10.3 | 501030000 | 80 mm dia (CI) | [8 empty] | No. | 2 | 14327 | 0 | 14327 | 716.35 | 0 | 15043.35 | 2573 | 318.0228 | 0 | 2891.0228 | 30086.7 | 5782.0456 | 35868.7456 | 10 | 2 | 2865.4 | 0 | 2865.4 | 143.27 | 0 | 3008.67 | 514.6 | 63.6046 | 0 | 578.2046 | 3586.8746
11 | 501030000 | Making water supply connection to kitchen / laundry equipment, appliances, coolers etc. including necessary fittings, (pipes and valves to be paid separately). | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11.1 | 501030000 | 15 mm to 25 mm dia | [8 empty] | No. | 40 | 400 | 0 | 400 | 20 | 0 | 420 | 77 | 9.5172 | 0 | 86.5172 | 16800 | 3460.688 | 20260.688 | 10 | 40 | 1600 | 0 | 1600 | 80 | 0 | 1680 | 308 | 38.0688 | 0 | 346.0688 | 2026.0688
11.2 | 501030000 | 32 mm to 50 mm dia | [8 empty] | No. | 15 | 550 | 0 | 550 | 27.5 | 0 | 577.5 | 103 | 12.7308 | 0 | 115.7308 | 8662.5 | 1735.962 | 10398.462 | 10 | 15 | 825 | 0 | 825 | 41.25 | 0 | 866.25 | 154.5 | 19.0962 | 0 | 173.5962 | 1039.8462
12 | 501030000 | Providing and fixing stainless steel hose connection with flange / union connection. | [8 empty] | No. | 3 | 2940 | 0 | 2940 | 147 | 0 | 3087 | 257 | 31.7652 | 0 | 288.7652 | 9261 | 866.2956 | 10127.2956 | 10 | 3 | 882 | 0 | 882 | 44.1 | 0 | 926.1 | 77.1 | 9.5296 | 0 | 86.6296 | 1012.7296
13 | 501030000 | Providing & fixing Auto Air vent with isolation valve for cold water supply risers, suitable for pressure not less than 10 Kg/Sq.cm. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13.1 | 501030000 | 15 mm dia a | [8 empty] | No. | 10 | 1421 | 0 | 1421 | 71.05 | 0 | 1492.05 | 103 | 12.7308 | 0 | 115.7308 | 14920.5 | 1157.308 | 16077.808 | 10 | 10 | 1421 | 0 | 1421 | 71.05 | 0 | 1492.05 | 103 | 12.7308 | 0 | 115.7308 | 1607.7808
13.2 | 501030000 | 20 mmdia | [8 empty] | No. | 15 | 1764 | 0 | 1764 | 88.2 | 0 | 1852.2 | 103 | 12.7308 | 0 | 115.7308 | 27783 | 1735.962 | 29518.962 | 10 | 15 | 2646 | 0 | 2646 | 132.3 | 0 | 2778.3 | 154.5 | 19.0962 | 0 | 173.5962 | 2951.8962
13.3 | 501030000 | 25 mm dia a | [8 empty] | No. | 12 | 2156 | 0 | 2156 | 107.8 | 0 | 2263.8 | 128 | 15.8208 | 0 | 143.8208 | 27165.6 | 1725.8496 | 28891.4496 | 10 | 12 | 2587.2 | 0 | 2587.2 | 129.36 | 0 | 2716.56 | 153.6 | 18.985 | 0 | 172.585 | 2889.145
14 | 501030000 | Providing, laying, jointing and testing in position the following Upvc pipes for under ground piping conforming to IS:13592 (Type B 6 kg/sq.cm) including all necessary fittings such as elbow, coupler & tee etc. Cost shall be inclusive of excavation, dewatering, backfilling, ramming surrounding the pipe all round with minimum 150 mm thick all round compacted silver sand and providing thrust block. All work complete as per specification and satisfaction of the Project Manager. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14.1 | 501030000 | 25 mm d | [8 empty] | RM | 20 | 45 | 0 | 45 | 2.25 | 0 | 47.25 | 25 | 3.09 | 0 | 28.09 | 945 | 561.8 | 1506.8 | 10 | 20 | 90 | 0 | 90 | 4.5 | 0 | 94.5 | 50 | 6.18 | 0 | 56.18 | 150.68
14.2 | 501030000 | 32 mm dia a | [8 empty] | RM | 10 | 55 | 0 | 55 | 2.75 | 0 | 57.75 | 30 | 3.708 | 0 | 33.708 | 577.5 | 337.08 | 914.58 | 10 | 10 | 55 | 0 | 55 | 2.75 | 0 | 57.75 | 30 | 3.708 | 0 | 33.708 | 91.458
14.3 | 501030000 | 40 mm dia a | [8 empty] | RM | 5 | 59 | 0 | 59 | 2.95 | 0 | 61.95 | 41 | 5.0676 | 0 | 46.0676 | 309.75 | 230.338 | 540.088 | 10 | 5 | 29.5 | 0 | 29.5 | 1.475 | 0 | 30.975 | 20.5 | 2.5338 | 0 | 23.0338 | 54.0088
14.4 | 501030000 | 50 mm dia a | [8 empty] | RM | 20 | 88 | 0 | 88 | 4.4 | 0 | 92.4 | 52 | 6.4272 | 0 | 58.4272 | 1848 | 1168.544 | 3016.544 | 10 | 20 | 176 | 0 | 176 | 8.8 | 0 | 184.8 | 104 | 12.8544 | 0 | 116.8544 | 301.6544
14.5 | 501030000 | 65 mm dia a | [8 empty] | RM | 50 | 135 | 0 | 135 | 6.75 | 0 | 141.75 | 72 | 8.8992 | 0 | 80.8992 | 7087.5 | 4044.96 | 11132.46 | 10 | 50 | 675 | 0 | 675 | 33.75 | 0 | 708.75 | 360 | 44.496 | 0 | 404.496 | 1113.246
14.6 | 501030000 | 80 mm da | [8 empty] | RM | 100 | 323 | 0 | 323 | 16.15 | 0 | 339.15 | 93 | 11.4948 | 0 | 104.4948 | 33915 | 10449.48 | 44364.48 | 10 | 100 | 3230 | 0 | 3230 | 161.5 | 0 | 3391.5 | 930 | 114.948 | 0 | 1044.948 | 4436.448
14.7 | 501030000 | 100 mm di a | [8 empty] | RM | 50 | 424 | 0 | 424 | 21.2 | 0 | 445.2 | 112 | 13.8432 | 0 | 125.8432 | 22260 | 6292.16 | 28552.16 | 10 | 50 | 2120 | 0 | 2120 | 106 | 0 | 2226 | 560 | 69.216 | 0 | 629.216 | 2855.216
15 | 501030000 | Providing & fixing in position 25 mm dia lawn hydrants consisting of 25 mm dia Ball valve, GI nipple and quick release coupling / threaded hose receiver complete as required. | [8 empty] | No. | 5 | 2205 | 0 | 2205 | 110.25 | 0 | 2315.25 | 257 | 31.7652 | 0 | 288.7652 | 11576.25 | 1443.826 | 13020.076 | 10 | 5 | 1102.5 | 0 | 1102.5 | 55.125 | 0 | 1157.625 | 128.5 | 15.8826 | 0 | 144.3826 | 1302.0076
16 | 501030000 | Constructing brick masonary chamber (for housing valves, Meters etc.) of brick work with bricks of class 75 with cement mortar 1:5 (1 cement:5 fine sand) plastering internal face & (with a floating coat of neat cement) cement mortar 1:3 (1 cement: 3 fine sand and rough plaster on outer face. R.C.C top slab with medium duty D.I. manhole cover and frame of 600 mm dia (weight : 60 KG). Including excavation, dewatering, refilling, watering, ramming and removing the surplus excavated material complete as required. (All sizes are clear internal sizes). | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16.1 | 501030000 | Size 1000 x 800 x 1200 mm deep | [8 empty] | No. | 1 | 16660 | 0 | 16660 | 833 | 0 | 17493 | 4631 | 572.3916 | 0 | 5203.3916 | 17493 | 5203.3916 | 22696.3916 | 10 | 1 | 1666 | 0 | 1666 | 83.3 | 0 | 1749.3 | 463.1 | 57.2392 | 0 | 520.3392 | 2269.6392
17 | 501030000 | Constructing brick masonary chamber (for housing lawn hydrant) of brick work with bricks of class 75 in cement mortar 1:5 (1 cement:5 fine sand) plastering internal face with cement 1:3 (1 cement mortar: 3 fine sand) and a rough plaster on outer face with a floating coat of neat cement. R.C.C. top slab with manhole cover & frame. Including excavation, dewatering, refilling, watering, ramming & removing the surplus excavated material complete as required. (All sizes are clear internal sizes). | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17.1 | 501030000 | Size 300 x 300 x 450 mm deep (with 300 x 300 LD : DI cover (Wt: 8 kg)) | [8 empty] | No. | 5 | 3234 | 0 | 3234 | 161.7 | 0 | 3395.7 | 1235 | 152.646 | 0 | 1387.646 | 16978.5 | 6938.23 | 23916.73 | 10 | 5 | 1617 | 0 | 1617 | 80.85 | 0 | 1697.85 | 617.5 | 76.323 | 0 | 693.823 | 2391.673
18 | 501030000 | Effecting connection from Existing/ Municipal Water Supply line including necessary excavation & making good the same including cutting, boring and tapping the Existing line by providing and installing ferrule / Tee connections with necessary fittings as required and making good the same. The rate for this item also includes complete services from the contractor for liasoning works such as filing necessary applications, submission of forms for approval to the municipal authorities, depositing the fees / other amounts as required for getting the premises / installations, inspected and approved and all other formalities required till the water connection is obtained. All the expenses incurred in this regard shall be borne by the Contractor except for the official payments to be made for any security deposit etc. which will be reimbursed on production of original voucher. | [8 empty] | LS | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 135000 | 16686 | 0 | 151686 | 0 | 151686 | 151686 | 10 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 13500 | 1668.6 | 0 | 15168.6 | 15168.6
C | 501030000 | HOT WATER SUPPLY: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 501030000 | Providing, fixing,commissioning & testing(at required pressure) CPVC (Chlorinated Poly Vinyl Chloride) water supply pipes with pipe as per CTS SDR 11 (operating pressure - 7 Bar @ 82 Deg C and 28 Bar @ 23 Deg C)for pipes from 1/2 Inch to 2 Inch. Schedule 80 Pipe to be used from 2-1/2 Inch to 6 Inch. Pipes shall be joined using solvent welded CPVC fittings i.e. Tees, Elbows, Couplers, Unions, Reducers, brushings etc. including transition fittings (connection between CPVC & metal pipe/GI) i.e. Brass Adaptors (both Male & Female threaded) conforming to ASTM D-2846. ASTM F441 with only CPVC solvent cement conforming to ASTM F-493. Cost shall be inclusive of (a) Making maximum of 7.5 x 7.5 cm chase in wall and floors for the pipe, making good the same by using 1:2 cement mortar wire mesh and providing insulation (seprate item) or (b) Fixing/supporting the pipes & fittings at wall/ceiling level supported by galvanized clamps, fastener, puff blocks, hangers etc, as per specification. Exposed pipes to be insulated (seprate item) and painting of legends with direction arrow on insulation. All termination points for installation of faucets shall have brass termination fittings. Installation shall be to as per Technical Manual of manufacturer of pipes & fittings. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 501030000 | M.S. pipe sleeves suitable higher size shall be provided wherever the pipes are crossing the fire rated wall / floor slab and sealing the sleeves with glass wool in between and fire sealant compound at either end all as per Project Managers / Consultant requirement. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.1 | 501030000 | 1/2" dia (15 mm) | [8 empty] | RM | 8000 | 102 | 0 | 102 | 5.1 | 0 | 107.1 | 41 | 5.0676 | 0 | 46.0676 | 856800 | 368540.8 | 1225340.8 | 10 | 8000 | 81600 | 0 | 81600 | 4080 | 0 | 85680 | 32800 | 4054.08 | 0 | 36854.08 | 122534.08
2.1 | 501030000 | 1/2" dia (15 mm) | [8 empty] | RM | 8000 | 102 | 0 | 102 | 5.1 | 0 | 107.1 | 41 | 5.0676 | 0 | 46.0676 | 856800 | 368540.8 | 1225340.8 | 60 | 2448 | 149817.6 | 0 | 149817.6 | 7490.88 | 0 | 157308.48 | 0 | 0 | 0 | 0 | 157308.48
2.2 | 501030000 | 3/4" dia (20 mm) | [8 empty] | RM | 4000 | 163 | 0 | 163 | 8.15 | 0 | 171.15 | 41 | 5.0676 | 0 | 46.0676 | 684600 | 184270.4 | 868870.4 | 10 | 4000 | 65200 | 0 | 65200 | 3260 | 0 | 68460 | 16400 | 2027.04 | 0 | 18427.04 | 86887.04
2.2 | 501030000 | 3/4" dia (20 mm) | [8 empty] | RM | 4000 | 163 | 0 | 163 | 8.15 | 0 | 171.15 | 41 | 5.0676 | 0 | 46.0676 | 684600 | 184270.4 | 868870.4 | 60 | 1500 | 146700 | 0 | 146700 | 7335 | 0 | 154035 | 0 | 0 | 0 | 0 | 154035
2.3 | 501030000 | 1" dia (25 mm) | [8 empty] | RM | 1500 | 228 | 0 | 228 | 11.4 | 0 | 239.4 | 52 | 6.4272 | 0 | 58.4272 | 359100 | 87640.8 | 446740.8 | 10 | 1500 | 34200 | 0 | 34200 | 1710 | 0 | 35910 | 7800 | 964.08 | 0 | 8764.08 | 44674.08
2.3 | 501030000 | 1" dia (25 mm) | [8 empty] | RM | 1500 | 228 | 0 | 228 | 11.4 | 0 | 239.4 | 52 | 6.4272 | 0 | 58.4272 | 359100 | 87640.8 | 446740.8 | 60 | 499 | 68263.2 | 0 | 68263.2 | 3413.16 | 0 | 71676.36 | 0 | 0 | 0 | 0 | 71676.36
2.4 | 501030000 | 1.1/4" dia (32 mm ) | [8 empty] | RM | 1200 | 327 | 0 | 327 | 16.35 | 0 | 343.35 | 56 | 6.9216 | 0 | 62.9216 | 412020 | 75505.92 | 487525.92 | 10 | 1200 | 39240 | 0 | 39240 | 1962 | 0 | 41202 | 6720 | 830.592 | 0 | 7550.592 | 48752.592
2.4 | 501030000 | 1.1/4" dia (32 mm ) | [8 empty] | RM | 1200 | 327 | 0 | 327 | 16.35 | 0 | 343.35 | 56 | 6.9216 | 0 | 62.9216 | 412020 | 75505.92 | 487525.92 | 60 | 328 | 64353.6 | 0 | 64353.6 | 3217.68 | 0 | 67571.28 | 0 | 0 | 0 | 0 | 67571.28
2.5 | 501030000 | 1.1/2: dia (40 mm) | [8 empty] | RM | 700 | 425 | 0 | 425 | 21.25 | 0 | 446.25 | 77 | 9.5172 | 0 | 86.5172 | 312375 | 60562.04 | 372937.04 | 10 | 700 | 29750 | 0 | 29750 | 1487.5 | 0 | 31237.5 | 5390 | 666.204 | 0 | 6056.204 | 37293.704
2.5 | 501030000 | 1.1/2: dia (40 mm) | [8 empty] | RM | 700 | 425 | 0 | 425 | 21.25 | 0 | 446.25 | 77 | 9.5172 | 0 | 86.5172 | 312375 | 60562.04 | 372937.04 | 60 | 199 | 50745 | 0 | 50745 | 2537.25 | 0 | 53282.25 | 0 | 0 | 0 | 0 | 53282.25
2.6 | 501030000 | 2" dia (50 mm) | [8 empty] | RM | 450 | 660 | 0 | 660 | 33 | 0 | 693 | 92 | 11.3712 | 0 | 103.3712 | 311850 | 46517.04 | 358367.04 | 10 | 450 | 29700 | 0 | 29700 | 1485 | 0 | 31185 | 4140 | 511.704 | 0 | 4651.704 | 35836.704
2.6 | 501030000 | 2" dia (50 mm) | [8 empty] | RM | 450 | 660 | 0 | 660 | 33 | 0 | 693 | 92 | 11.3712 | 0 | 103.3712 | 311850 | 46517.04 | 358367.04 | 60 | 130 | 51480 | 0 | 51480 | 2574 | 0 | 54054 | 0 | 0 | 0 | 0 | 54054
2.7 | 501030000 | 2.1/2" dia | [8 empty] | RM | 200 | 1300 | 0 | 1300 | 65 | 0 | 1365 | 128 | 15.8208 | 0 | 143.8208 | 273000 | 28764.16 | 301764.16 | 10 | 200 | 26000 | 0 | 26000 | 1300 | 0 | 27300 | 2560 | 316.416 | 0 | 2876.416 | 30176.416
2.7 | 501030000 | 2.1/2" dia | [8 empty] | RM | 200 | 1300 | 0 | 1300 | 65 | 0 | 1365 | 128 | 15.8208 | 0 | 143.8208 | 273000 | 28764.16 | 301764.16 | 60 | 107 | 83460 | 0 | 83460 | 4173 | 0 | 87633 | 0 | 0 | 0 | 0 | 87633
2.8 | 501030000 | 3" dia (80 mm) | [8 empty] | RM | 250 | 1980 | 0 | 1980 | 99 | 0 | 2079 | 155 | 19.158 | 0 | 174.158 | 519750 | 43539.5 | 563289.5 | 10 | 250 | 49500 | 0 | 49500 | 2475 | 0 | 51975 | 3875 | 478.95 | 0 | 4353.95 | 56328.95
2.9 | 501030000 | 4" dia (100 mm) | [8 empty] | RM | 150 | 2870 | 0 | 2870 | 143.5 | 0 | 3013.5 | 200 | 24.72 | 0 | 224.72 | 452025 | 33708 | 485733 | 10 | 150 | 43050 | 0 | 43050 | 2152.5 | 0 | 45202.5 | 3000 | 370.8 | 0 | 3370.8 | 48573.3
2.1 | 501030000 | 6" dia (150 mm) | [8 empty] | RM | 0 | 4700 | 0 | 4700 | 235 | 0 | 4935 | 315 | 38.934 | 0 | 353.934 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 501030000 | Providing and fixing 6 mm thick supercera rope insulation with SS304 brading for return, hot water supply / return, pipes & fittings (in chases) for the following diameter of pipes. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.1 | 501030000 | 15 mm dia to 32 mm dia | [8 empty] | RM | 0 | 180 | 0 | 180 | 9 | 0 | 189 | 53 | 6.5508 | 0 | 59.5508 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 501030000 | Providing and fixing nitrle rubber insulation on hot water supply / return pipes. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4.1 | 501030000 | 15 mm dia (9 mm thickness) | [8 empty] | RM | 8000 | 38 | 0 | 38 | 1.9 | 0 | 39.9 | 15 | 1.854 | 0 | 16.854 | 319200 | 134832 | 454032 | 10 | 8000 | 30400 | 0 | 30400 | 1520 | 0 | 31920 | 12000 | 1483.2 | 0 | 13483.2 | 45403.2
4.2 | 501030000 | 20 mm dia (9 mm thickness) | [8 empty] | RM | 4000 | 41 | 0 | 41 | 2.05 | 0 | 43.05 | 20 | 2.472 | 0 | 22.472 | 172200 | 89888 | 262088 | 10 | 4000 | 16400 | 0 | 16400 | 820 | 0 | 17220 | 8000 | 988.8 | 0 | 8988.8 | 26208.8
4.3 | 501030000 | 25 mm dia (9 mm thickness) | [8 empty] | RM | 1500 | 43 | 0 | 43 | 2.15 | 0 | 45.15 | 25 | 3.09 | 0 | 28.09 | 67725 | 42135 | 109860 | 10 | 1500 | 6450 | 0 | 6450 | 322.5 | 0 | 6772.5 | 3750 | 463.5 | 0 | 4213.5 | 10986
4.4 | 501030000 | 32 mm dia (13 mm thickness) | [8 empty] | RM | 1200 | 63 | 0 | 63 | 3.15 | 0 | 66.15 | 31 | 3.8316 | 0 | 34.8316 | 79380 | 41797.92 | 121177.92 | 10 | 1200 | 7560 | 0 | 7560 | 378 | 0 | 7938 | 3720 | 459.792 | 0 | 4179.792 | 12117.792
4.5 | 501030000 | 40 mm dia (13 mm thickness) | [8 empty] | RM | 700 | 110 | 0 | 110 | 5.5 | 0 | 115.5 | 41 | 5.0676 | 0 | 46.0676 | 80850 | 32247.32 | 113097.32 | 10 | 700 | 7700 | 0 | 7700 | 385 | 0 | 8085 | 2870 | 354.732 | 0 | 3224.732 | 11309.732
4.6 | 501030000 | 50 mm dia (13 mm thickness) | [8 empty] | RM | 450 | 132 | 0 | 132 | 6.6 | 0 | 138.6 | 52 | 6.4272 | 0 | 58.4272 | 62370 | 26292.24 | 88662.24 | 10 | 450 | 5940 | 0 | 5940 | 297 | 0 | 6237 | 2340 | 289.224 | 0 | 2629.224 | 8866.224
4.7 | 501030000 | 65mm dia (19 mm thickness) | [8 empty] | RM | 200 | 161 | 0 | 161 | 8.05 | 0 | 169.05 | 66 | 8.1576 | 0 | 74.1576 | 33810 | 14831.52 | 48641.52 | 10 | 200 | 3220 | 0 | 3220 | 161 | 0 | 3381 | 1320 | 163.152 | 0 | 1483.152 | 4864.152
4.8 | 501030000 | 80mm dia (19 mm thickness) | [8 empty] | RM | 250 | 199 | 0 | 199 | 9.95 | 0 | 208.95 | 82 | 10.1352 | 0 | 92.1352 | 52237.5 | 23033.8 | 75271.3 | 10 | 250 | 4975 | 0 | 4975 | 248.75 | 0 | 5223.75 | 2050 | 253.38 | 0 | 2303.38 | 7527.13
4.9 | 501030000 | 100 mm dia (19 mm thickness) | [8 empty] | RM | 150 | 233 | 0 | 233 | 11.65 | 0 | 244.65 | 103 | 12.7308 | 0 | 115.7308 | 36697.5 | 17359.62 | 54057.12 | 10 | 150 | 3495 | 0 | 3495 | 174.75 | 0 | 3669.75 | 1545 | 190.962 | 0 | 1735.962 | 5405.712
4.1 | 501030000 | 150 mm dia (19 mm thickness) | [8 empty] | RM | 0 | 370 | 0 | 370 | 18.5 | 0 | 388.5 | 131 | 16.1916 | 0 | 147.1916 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 501030000 | Providing and fixing proprietary polyshield outer mechanical protection ON nitrile rubber insulation comprising of wrapping with poly glass tape helically wound and subsequently applying 2 coats of polyshield material (resin & hardner) as per manufacturers specification and approved by Project Manager / Consultnats. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.1 | 501030000 | 15 mm dia | [8 empty] | RM | 0 | 105 | 0 | 105 | 5.25 | 0 | 110.25 | 21 | 2.5956 | 0 | 23.5956 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.2 | 501030000 | 20 mm dia | [8 empty] | RM | 0 | 120 | 0 | 120 | 6 | 0 | 126 | 26 | 3.2136 | 0 | 29.2136 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.3 | 501030000 | 25 mm dia | [8 empty] | RM | 0 | 140 | 0 | 140 | 7 | 0 | 147 | 37 | 4.5732 | 0 | 41.5732 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.4 | 501030000 | 32 mm dia | [8 empty] | RM | 0 | 178 | 0 | 178 | 8.9 | 0 | 186.9 | 42 | 5.1912 | 0 | 47.1912 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.5 | 501030000 | 40 mm dia | [8 empty] | RM | 0 | 250 | 0 | 250 | 12.5 | 0 | 262.5 | 58 | 7.1688 | 0 | 65.1688 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.6 | 501030000 | 50mm dia | [8 empty] | RM | 0 | 266 | 0 | 266 | 13.3 | 0 | 279.3 | 74 | 9.1464 | 0 | 83.1464 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.7 | 501030000 | 65 mm dia | [8 empty] | RM | 0 | 336 | 0 | 336 | 16.8 | 0 | 352.8 | 89 | 11.0004 | 0 | 100.0004 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.8 | 501030000 | 80mm dia | [8 empty] | RM | 0 | 390 | 0 | 390 | 19.5 | 0 | 409.5 | 110 | 13.596 | 0 | 123.596 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.9 | 501030000 | 100 mm dia | [8 empty] | RM | 0 | 425 | 0 | 425 | 21.25 | 0 | 446.25 | 142 | 17.5512 | 0 | 159.5512 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.1 | 501030000 | 150mm dia | [8 empty] | RM | 0 | 620 | 0 | 620 | 31 | 0 | 651 | 210 | 25.956 | 0 | 235.956 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 501030000 | Providing and fixing 22 SWG GI sheet cladding over nitrile rubber insulation on hot water pipe work for the following size pipes. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6.1 | 501030000 | 40 mm dia | [8 empty] | RM | 0 | 259 | 0 | 259 | 12.95 | 0 | 271.95 | 58 | 7.1688 | 0 | 65.1688 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6.2 | 501030000 | 50 mm dia | [8 empty] | RM | 0 | 301 | 0 | 301 | 15.05 | 0 | 316.05 | 73 | 9.0228 | 0 | 82.0228 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6.3 | 501030000 | 65 mm dia | [8 empty] | RM | 0 | 415 | 0 | 415 | 20.75 | 0 | 435.75 | 89 | 11.0004 | 0 | 100.0004 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6.4 | 501030000 | 80mm dia | [8 empty] | RM | 0 | 427 | 0 | 427 | 21.35 | 0 | 448.35 | 110 | 13.596 | 0 | 123.596 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6.5 | 501030000 | 100 mm dia | [8 empty] | RM | 0 | 483 | 0 | 483 | 24.15 | 0 | 507.15 | 142 | 17.5512 | 0 | 159.5512 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 501030000 | Providing and fixing male/ female screw ended full way lever operated forged brass ball valves with brass body with forged brass hard chrome plated ball / stem, union. Rated to temperature of 85 Deg C and tested to a pressure not less than 30 Kg/Sq.cm. Including covering with nitrile rubber insulation having protective coating against mechanical damage as per manufacturers specification (GI boxing to be provided). | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7.1 | 501030000 | 15 mm di a | [8 empty] | No. | 10 | 266 | 0 | 266 | 13.3 | 0 | 279.3 | 72 | 8.8992 | 0 | 80.8992 | 2793 | 808.992 | 3601.992 | 10 | 10 | 266 | 0 | 266 | 13.3 | 0 | 279.3 | 72 | 8.8992 | 0 | 80.8992 | 360.1992
7.2 | 501030000 | 20 mm dia a | [8 empty] | No. | 230 | 382 | 0 | 382 | 19.1 | 0 | 401.1 | 72 | 8.8992 | 0 | 80.8992 | 92253 | 18606.816 | 110859.816 | 10 | 230 | 8786 | 0 | 8786 | 439.3 | 0 | 9225.3 | 1656 | 204.6816 | 0 | 1860.6816 | 11085.9816
7.3 | 501030000 | 25 mm dia b | [8 empty] | No. | 230 | 594 | 0 | 594 | 29.7 | 0 | 623.7 | 103 | 12.7308 | 0 | 115.7308 | 143451 | 26618.084 | 170069.084 | 10 | 230 | 13662 | 0 | 13662 | 683.1 | 0 | 14345.1 | 2369 | 292.8084 | 0 | 2661.8084 | 17006.9084
7.4 | 501030000 | 32 mm dia b | [8 empty] | No. | 15 | 1055 | 0 | 1055 | 52.75 | 0 | 1107.75 | 128 | 15.8208 | 0 | 143.8208 | 16616.25 | 2157.312 | 18773.562 | 10 | 15 | 1582.5 | 0 | 1582.5 | 79.125 | 0 | 1661.625 | 192 | 23.7312 | 0 | 215.7312 | 1877.3562
7.5 | 501030000 | 40 mm dia b | [8 empty] | No. | 15 | 1528 | 0 | 1528 | 76.4 | 0 | 1604.4 | 155 | 19.158 | 0 | 174.158 | 24066 | 2612.37 | 26678.37 | 10 | 15 | 2292 | 0 | 2292 | 114.6 | 0 | 2406.6 | 232.5 | 28.737 | 0 | 261.237 | 2667.837
7.6 | 501030000 | 50 mm dia c | [8 empty] | No. | 10 | 2321 | 0 | 2321 | 116.05 | 0 | 2437.05 | 206 | 25.4616 | 0 | 231.4616 | 24370.5 | 2314.616 | 26685.116 | 10 | 10 | 2321 | 0 | 2321 | 116.05 | 0 | 2437.05 | 206 | 25.4616 | 0 | 231.4616 | 2668.5116
8 | 501030000 | Providing and fixing C.I. Butterfly valve (Body : Grey Cast Iron, shaft : SS, Disc : SG Iron (nickel plated coated), Liner : HT - EPDM) of approved make with union / flange, washer, nuts & bolts. Rated to temperature of 85 Deg C and PN 10/16 pressure rating including nitrile rubber insulation with proprietary fire proof protective coating against mechanical damage as per manufacturers specification (GI boxing to be provided). | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8.1 | 501030000 | 65 mm dia b | [8 empty] | No. | 10 | 3732 | 0 | 3732 | 186.6 | 0 | 3918.6 | 334 | 41.2824 | 0 | 375.2824 | 39186 | 3752.824 | 42938.824 | 10 | 10 | 3732 | 0 | 3732 | 186.6 | 0 | 3918.6 | 334 | 41.2824 | 0 | 375.2824 | 4293.8824
8.2 | 501030000 | 80 mm dia a | [8 empty] | No. | 10 | 4440 | 0 | 4440 | 222 | 0 | 4662 | 412 | 50.9232 | 0 | 462.9232 | 46620 | 4629.232 | 51249.232 | 10 | 10 | 4440 | 0 | 4440 | 222 | 0 | 4662 | 412 | 50.9232 | 0 | 462.9232 | 5124.9232
8.3 | 501030000 | 100 mm dia a | [8 empty] | No. | 5 | 5820 | 0 | 5820 | 291 | 0 | 6111 | 515 | 63.654 | 0 | 578.654 | 30555 | 2893.27 | 33448.27 | 10 | 5 | 2910 | 0 | 2910 | 145.5 | 0 | 3055.5 | 257.5 | 31.827 | 0 | 289.327 | 3344.827
9 | 501030000 | Providing & fixing C.I. Wafer type Check Valve of PN 16 rating of approved make with union / flange, washer, nuts & bolts. Rated to temperature of 85 Deg C and including nitrile rubber insulation with proprietary fire proof protective coating against mechanical damage as per manufacturers specification. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.1 | 501030000 | 65 mm dia | [8 empty] | No. | 0 | 5106 | 0 | 5106 | 255.3 | 0 | 5361.3 | 341 | 42.1476 | 0 | 383.1476 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.2 | 501030000 | 80 mm dia | [8 empty] | No. | 0 | 6144 | 0 | 6144 | 307.2 | 0 | 6451.2 | 420 | 51.912 | 0 | 471.912 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.3 | 501030000 | 100 mm dia | [8 empty] | No. | 0 | 7938 | 0 | 7938 | 396.9 | 0 | 8334.9 | 525 | 64.89 | 0 | 589.89 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 501030000 | Providing & fixing C.I. Y (flange type) with stainless steel fine wire mesh and perforated sheet basket with necessary flange/unions, nuts, bolts, washers suitable for test pressure not less than 10 Kg/Sq.cm. Including nitrile rubber insulation with proprietory fire proof protective coating against mechanical damage as per manufacturers specification and approved by Project Manager.Suitable for operation at 85 deg. C. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10.1 | 501030000 | 50 mm dia | [8 empty] | No. | 0 | 4682 | 0 | 4682 | 234.1 | 0 | 4916.1 | 263 | 32.5068 | 0 | 295.5068 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10.2 | 501030000 | 65 mm dia | [8 empty] | No. | 0 | 5256 | 0 | 5256 | 262.8 | 0 | 5518.8 | 341 | 42.1476 | 0 | 383.1476 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10.3 | 501030000 | 80 mm dia | [8 empty] | No. | 0 | 6696 | 0 | 6696 | 334.8 | 0 | 7030.8 | 420 | 51.912 | 0 | 471.912 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10.4 | 501030000 | 100 mm dia | [8 empty] | No. | 0 | 9720 | 0 | 9720 | 486 | 0 | 10206 | 525 | 64.89 | 0 | 589.89 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 501030000 | Providing and fixing heavy duty floating flange EPDM rubber expansion joint with unit control (tie rod & gusset plate) as per manufacturers specifications of standard length complete with all accessories testing to a pressure not less than 15 KG / sqcm including rubber gaskets, flanges nuts, bolts & washers complete as required suitable for operation at 85 deg. C. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11.1 | 501030000 | 80 mm dia | [8 empty] | No. | 0 | 5358 | 0 | 5358 | 267.9 | 0 | 5625.9 | 252 | 31.1472 | 0 | 283.1472 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11.2 | 501030000 | 100 mm dia | [8 empty] | No. | 0 | 6966 | 0 | 6966 | 348.3 | 0 | 7314.3 | 315 | 38.934 | 0 | 353.934 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 501030000 | Providing and fixing auto air vent with isolation valve for Hot water supply system suitable for pressure not less than 10 Kg / Sqcm. suitable for operation at 85 deg. C. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12.1 | 501030000 | 15 mm dia | [8 empty] | No. | 5 | 1294 | 0 | 1294 | 64.7 | 0 | 1358.7 | 103 | 12.7308 | 0 | 115.7308 | 6793.5 | 578.654 | 7372.154 | 10 | 5 | 647 | 0 | 647 | 32.35 | 0 | 679.35 | 51.5 | 6.3654 | 0 | 57.8654 | 737.2154
12.2 | 501030000 | 20 mm dia | [8 empty] | No. | 30 | 1680 | 0 | 1680 | 84 | 0 | 1764 | 105 | 12.978 | 0 | 117.978 | 52920 | 3539.34 | 56459.34 | 10 | 30 | 5040 | 0 | 5040 | 252 | 0 | 5292 | 315 | 38.934 | 0 | 353.934 | 5645.934
12.3 | 501030000 | 25 mm dia | [8 empty] | No. | 0 | 2640 | 0 | 2640 | 132 | 0 | 2772 | 131 | 16.1916 | 0 | 147.1916 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 501030000 | Providing and fixing insulated pressure reducing station for hot water supply comprising of 2 nos Gun Metal ball valves on inlet, outlet & 1 nos. globe valve for by pass, 1 No pressure reducing valve with flanged/ screwed connection, 1 No. Y strainer, 2 Nos Pressure gauge on inlet & outlet, and 1 No. 15 mm dia safety valve. The complete system is tested to a pressure not less than 15 Kg/Sq.cm and suitable to reduce the pressure upto 2 Kg/Sq.cm. Including necessary pipes & fittings i.e. flanges/ unions, nuts, bolts and washers complete as required (GI boxing to be provided on the installation).PRV should be operable at 85 deg C. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13.1 | 501030000 | 32 mm dia (Brass Housing - PRV) | [8 empty] | No. | 5 | 16224 | 0 | 16224 | 811.2 | 0 | 17035.2 | 672 | 83.0592 | 0 | 755.0592 | 85176 | 3775.296 | 88951.296 | 10 | 5 | 8112 | 0 | 8112 | 405.6 | 0 | 8517.6 | 336 | 41.5296 | 0 | 377.5296 | 8895.1296
13.2 | 501030000 | 40 mm dia (Brass Housing - PRV) | [8 empty] | No. | 10 | 20161 | 0 | 20161 | 1008.05 | 0 | 21169.05 | 840 | 103.824 | 0 | 943.824 | 211690.5 | 9438.24 | 221128.74 | 10 | 10 | 20161 | 0 | 20161 | 1008.05 | 0 | 21169.05 | 840 | 103.824 | 0 | 943.824 | 22112.874
13.3 | 501030000 | 50 mm dia (Brass Housing - PRV) | [8 empty] | No. | 2 | 28184 | 0 | 28184 | 1409.2 | 0 | 29593.2 | 1050 | 129.78 | 0 | 1179.78 | 59186.4 | 2359.56 | 61545.96 | 10 | 2 | 5636.8 | 0 | 5636.8 | 281.84 | 0 | 5918.64 | 210 | 25.956 | 0 | 235.956 | 6154.596
14 | 501030000 | Making water supply connection to laundry / kitchen equipment, appliances etc., including necessary fittings, (pipes & valves to paid separately). | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14.1 | 501030000 | Size 15 mm to 25 mm dia | [8 empty] | No. | 40 | 563 | 0 | 563 | 28.15 | 0 | 591.15 | 77 | 9.5172 | 0 | 86.5172 | 23646 | 3460.688 | 27106.688 | 10 | 40 | 2252 | 0 | 2252 | 112.6 | 0 | 2364.6 | 308 | 38.0688 | 0 | 346.0688 | 2710.6688
14.2 | 501030000 | Size 32 mm to 50 mm dia | [8 empty] | No. | 15 | 637 | 0 | 637 | 31.85 | 0 | 668.85 | 103 | 12.7308 | 0 | 115.7308 | 10032.75 | 1735.962 | 11768.712 | 10 | 15 | 955.5 | 0 | 955.5 | 47.775 | 0 | 1003.275 | 154.5 | 19.0962 | 0 | 173.5962 | 1176.8712
D | 501040000 | INTERNAL DRAINAGE : (SOIL, WASTE & VENT) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  |  |  | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 501040000 | Providing, fixing, jointing, testing and commissioning spun/centri C.I. pipe for soil, waste & vent pipes installation conforming to IS:3989 cut to required lengths including all necessary fittings and specials such as Bends, junctions, offsets, access pieces (plain or door) & vent cowl. Fixing at wall/ceiling level supported by galvanized steel clamps & hangers etc. duly epoxy coated. Making proper connection with drip seal PJS joint of required depth as per manufacturer. Cutting, chases/holes in floors / walls / slab. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 501040000 | Providing MS pipe sleeves of suitable higher size wherever pipes crossing a fire rated wall / floor slab and sealing of space around pipe and pipe sleeve with glass wool in between and fire proof sealent at either end to the satisfaction of the Project Manager / Consultants and making good the same after pipes have been duly laid and testing complete | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 501040000 | Cost shall also be inclusive of painting the pipes & fittings with two coats of synthetic enamel paint of approved shade over a coat of primer. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.1 | 501040000 | 75 mm di | [8 empty] | RM | 1400 | 1065 | 0 | 1065 | 53.25 | 0 | 1118.25 | 215 | 26.574 | 0 | 241.574 | 1565550 | 338203.6 | 1903753.6 | 10 | 1400 | 149100 | 0 | 149100 | 7455 | 0 | 156555 | 30100 | 3720.36 | 0 | 33820.36 | 190375.36
3.1 | 501040000 | 75 mm di | [8 empty] | RM | 1400 | 1065 | 0 | 1065 | 53.25 | 0 | 1118.25 | 215 | 26.574 | 0 | 241.574 | 1565550 | 338203.6 | 1903753.6 | 60 | 742.5 | 474457.5 | 0 | 474457.5 | 23722.875 | 0 | 498180.375 | 0 | 0 | 0 | 0 | 498180.375
3.2 | 501040000 | 100 mm dia b | [8 empty] | RM | 3500 | 1300 | 0 | 1300 | 65 | 0 | 1365 | 288 | 35.5968 | 0 | 323.5968 | 4777500 | 1132588.8 | 5910088.8 | 10 | 3500 | 455000 | 0 | 455000 | 22750 | 0 | 477750 | 100800 | 12458.88 | 0 | 113258.88 | 591008.88
3.2 | 501040000 | 100 mm dia b | [8 empty] | RM | 3500 | 1300 | 0 | 1300 | 65 | 0 | 1365 | 288 | 35.5968 | 0 | 323.5968 | 4777500 | 1132588.8 | 5910088.8 | 60 | 675 | 526500 | 0 | 526500 | 26325 | 0 | 552825 | 0 | 0 | 0 | 0 | 552825
3.3 | 501040000 | 150 mm dia a | [8 empty] | RM | 200 | 2295 | 0 | 2295 | 114.75 | 0 | 2409.75 | 426 | 52.6536 | 0 | 478.6536 | 481950 | 95730.72 | 577680.72 | 10 | 200 | 45900 | 0 | 45900 | 2295 | 0 | 48195 | 8520 | 1053.072 | 0 | 9573.072 | 57768.072
3.3 | 501040000 | 150 mm dia a | [8 empty] | RM | 200 | 2295 | 0 | 2295 | 114.75 | 0 | 2409.75 | 426 | 52.6536 | 0 | 478.6536 | 481950 | 95730.72 | 577680.72 | 60 | 90 | 123930 | 0 | 123930 | 6196.5 | 0 | 130126.5 | 0 | 0 | 0 | 0 | 130126.5
4 | 501040000 | Providing, fixing, jointing, testing and commissioning UPVC (Class III) 6 Kg/cm sq. Rain water down take pipe conforming to IS:4985 cut to required lengths including all necessary fittings and specials. Fixing at wall/ceiling level supported by galvanized steel clamps & hangers etc. Making proper connection with cement solvent joint as per BIS / manufacturer. Cutting, chases / holes in floors / walls / slab. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4.1 | 501040000 | 75 mm dia | [8 empty] | RM | 20 | 144 | 0 | 144 | 7.2 | 0 | 151.2 | 93 | 11.4948 | 0 | 104.4948 | 3024 | 2089.896 | 5113.896 | 10 | 20 | 288 | 0 | 288 | 14.4 | 0 | 302.4 | 186 | 22.9896 | 0 | 208.9896 | 511.3896
4.2 | 501040000 | 110 mm dia a | [8 empty] | RM | 25 | 363 | 0 | 363 | 18.15 | 0 | 381.15 | 112 | 13.8432 | 0 | 125.8432 | 9528.75 | 3146.08 | 12674.83 | 10 | 25 | 907.5 | 0 | 907.5 | 45.375 | 0 | 952.875 | 280 | 34.608 | 0 | 314.608 | 1267.483
4.3 | 501040000 | 160 mm dia a | [8 empty] | RM | 400 | 830 | 0 | 830 | 41.5 | 0 | 871.5 | 185 | 22.866 | 0 | 207.866 | 348600 | 83146.4 | 431746.4 | 10 | 400 | 33200 | 0 | 33200 | 1660 | 0 | 34860 | 7400 | 914.64 | 0 | 8314.64 | 43174.64
4.4 | 501040000 | 200 mm dia a | [8 empty] | RM | 50 | 1514 | 0 | 1514 | 75.7 | 0 | 1589.7 | 247 | 30.5292 | 0 | 277.5292 | 79485 | 13876.46 | 93361.46 | 10 | 50 | 7570 | 0 | 7570 | 378.5 | 0 | 7948.5 | 1235 | 152.646 | 0 | 1387.646 | 9336.146
4.5 | 501040000 | 250 mm dia a | [8 empty] | RM | 150 | 1750 | 0 | 1750 | 87.5 | 0 | 1837.5 | 309 | 38.1924 | 0 | 347.1924 | 275625 | 52078.86 | 327703.86 | 10 | 150 | 26250 | 0 | 26250 | 1312.5 | 0 | 27562.5 | 4635 | 572.886 | 0 | 5207.886 | 32770.386
5 | 501040000 | Providing, fixing, jointing and testing in position the C.I. class LA pipe for soil & waste installation conforming to IS:1536. Cut to required lengths including all necessary fittings & specials such as bends, junctions, offsets, access pieces (plain or door). Fixing at wall / ceiling level supported by galvanized steel clamps & hangers etc. duly epoxy coated. Making proper connection. Cuting, chases/holes in floors / walls / slab. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 501040000 | Providing MS pipe sleeves of suitable higher size wherever pipes crossing a fire rated wall or floor slab & sealing of space around pipe and pipe sleeve with glass wool inbetween and fire proof sealant at either end to the satisfaction of the Project Manager / Consultant and making good the same after pipe have been duly laid and testing complete The piping shall have proper connection with dripsed of required depth as per BIS / manufacturer, | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 501040000 | Cost shall also be inclusive of painting the pipes & fittings with two coats of synthetic enamel paint of approved shade over a coat of primer. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7.1 | 501040000 | 100 mm dia | [8 empty] | RM | 0 | 2202 | 0 | 2202 | 110.1 | 0 | 2312.1 | 294 | 36.3384 | 0 | 330.3384 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7.2 | 501040000 | 150 mm dia | [8 empty] | RM | 0 | 3524 | 0 | 3524 | 176.2 | 0 | 3700.2 | 446 | 55.1256 | 0 | 501.1256 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7.3 | 501040000 | 200 mm dia a | [8 empty] | RM | 300 | 4047 | 0 | 4047 | 202.35 | 0 | 4249.35 | 575 | 71.07 | 0 | 646.07 | 1274805 | 193821 | 1468626 | 10 | 300 | 121410 | 0 | 121410 | 6070.5 | 0 | 127480.5 | 17250 | 2132.1 | 0 | 19382.1 | 146862.6
7.4 | 501040000 | 250 mm dia | [8 empty] | RM | 0 | 6325 | 0 | 6325 | 316.25 | 0 | 6641.25 | 720 | 88.992 | 0 | 808.992 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 501040000 | Providing, fixing, jointing, testing and commissioning of UPVC pipe (for Planter / landscape drain) confirming to IS : 13592 (Type B 6kg/sq.cm.), cut to required lengths including all necessary fittings and specials such as bends, junctions offsets, access pieces (plain or door) & vent cowl. Fixing at wall / ceiling level supported by G.I. clamps, hangers etc. duly epoxy coated. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8.1 | 501040000 | 110 mm dia | [8 empty] | RM | 25 | 351 | 0 | 351 | 17.55 | 0 | 368.55 | 113 | 13.9668 | 0 | 126.9668 | 9213.75 | 3174.17 | 12387.92 | 10 | 25 | 877.5 | 0 | 877.5 | 43.875 | 0 | 921.375 | 282.5 | 34.917 | 0 | 317.417 | 1238.792
8.2 | 501040000 | 160 mm dia | [8 empty] | RM | 25 | 695 | 0 | 695 | 34.75 | 0 | 729.75 | 185 | 22.866 | 0 | 207.866 | 18243.75 | 5196.65 | 23440.4 | 10 | 25 | 1737.5 | 0 | 1737.5 | 86.875 | 0 | 1824.375 | 462.5 | 57.165 | 0 | 519.665 | 2344.04
9 | 501040000 | Providing and fixing in position G.I. pipe and fittings of heavy class (c) conforming to IS:1239 (for waste pipe from individual fixtures to floor trap / floor drain & vent pipe) Including fixing at wall / ceiling level supported by galvanized clamps and hangers providing two coats of synthetic enamel paint of approved shade as per pipe colour code over a coat of primer or cutting & chasing in wall & floors, providing protection to embedded GI pipes & fittings by wrapping of 400 microne polythene sheet over two coats of bitumen including proper overlaps in joints complete as required and making good the chase by using 1:1 cement mortar. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.1 | 501040000 | 32 mm dia c | [8 empty] | RM | 330 | 352 | 0 | 352 | 17.6 | 0 | 369.6 | 134 | 16.5624 | 0 | 150.5624 | 121968 | 49685.592 | 171653.592 | 10 | 330 | 11616 | 0 | 11616 | 580.8 | 0 | 12196.8 | 4422 | 546.5592 | 0 | 4968.5592 | 17165.3592
9.2 | 501040000 | 40 mm dia c | [8 empty] | RM | 320 | 396 | 0 | 396 | 19.8 | 0 | 415.8 | 164 | 20.2704 | 0 | 184.2704 | 133056 | 58966.528 | 192022.528 | 10 | 320 | 12672 | 0 | 12672 | 633.6 | 0 | 13305.6 | 5248 | 648.6528 | 0 | 5896.6528 | 19202.2528
9.3 | 501040000 | 50 mmdia | [8 empty] | RM | 825 | 558 | 0 | 558 | 27.9 | 0 | 585.9 | 206 | 25.4616 | 0 | 231.4616 | 483367.5 | 190955.82 | 674323.32 | 10 | 825 | 46035 | 0 | 46035 | 2301.75 | 0 | 48336.75 | 16995 | 2100.582 | 0 | 19095.582 | 67432.332
10 | 501040000 | Providing and fixing in position 75 mm N.B. C.I. Nahni traps of self cleaning design including 125 mm dia CP grating, joining, embedding in concrete etc. complete rate to include making of opening in floor, marble / tiles, for fixing grating. | [8 empty] | Nos. | 25 | 488 | 0 | 488 | 24.4 | 0 | 512.4 | 52 | 6.4272 | 0 | 58.4272 | 12810 | 1460.68 | 14270.68 | 10 | 25 | 1220 | 0 | 1220 | 61 | 0 | 1281 | 130 | 16.068 | 0 | 146.068 | 1427.068
11 | 501040000 | Providing and fixing in position CI full bore P trap of the following sizes for underslab location including providing necessary galvanized steel support and as per Specification and duly epoxy coated. Making proper connection with refined pig lead / drip seal joints, cutting chase / hole in floors / slabs and bringing the same in proper condition and shape after placing the trap in right position complete by supporting by GI clamps / hangers as required. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11.1 | 501040000 | 100 mm inlet and 80 mm outlet. | [8 empty] | No. | 780 | 588 | 0 | 588 | 29.4 | 0 | 617.4 | 155 | 19.158 | 0 | 174.158 | 481572 | 135843.24 | 617415.24 | 10 | 780 | 45864 | 0 | 45864 | 2293.2 | 0 | 48157.2 | 12090 | 1494.324 | 0 | 13584.324 | 61741.524
11.1 | 501040000 | 100 mm inlet and 80 mm outlet. | [8 empty] | No. | 780 | 588 | 0 | 588 | 29.4 | 0 | 617.4 | 155 | 19.158 | 0 | 174.158 | 481572 | 135843.24 | 617415.24 | 60 | 100 | 35280 | 0 | 35280 | 1764 | 0 | 37044 | 0 | 0 | 0 | 0 | 37044
11.2 | 501040000 | 100 mm inlet and 100 mm outlet. | [8 empty] | No. | 230 | 759 | 0 | 759 | 37.95 | 0 | 796.95 | 155 | 19.158 | 0 | 174.158 | 183298.5 | 40056.34 | 223354.84 | 10 | 230 | 17457 | 0 | 17457 | 872.85 | 0 | 18329.85 | 3565 | 440.634 | 0 | 4005.634 | 22335.484
11.2 | 501040000 | 100 mm inlet and 100 mm outlet. | [8 empty] | No. | 230 | 759 | 0 | 759 | 37.95 | 0 | 796.95 | 155 | 19.158 | 0 | 174.158 | 183298.5 | 40056.34 | 223354.84 | 60 | 50 | 22770 | 0 | 22770 | 1138.5 | 0 | 23908.5 | 0 | 0 | 0 | 0 | 23908.5
12 | 501040000 | Providing & fixing 80mm x 50mm GI waste with reducing elbow & nipple cutting chases, the floor / slab, repairs complete as required and connection to waste pipe. | [8 empty] | No. | 0 | 2040 | 0 | 2040 | 102 | 0 | 2142 | 53 | 6.5508 | 0 | 59.5508 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 501040000 | Providing and fixing uPVC boss pipe with three inlet fittings to receive waste pipes from fixtures waste. | [8 empty] | No. | 0 | 1680 | 0 | 1680 | 84 | 0 | 1764 | 53 | 6.5508 | 0 | 59.5508 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 501040000 | Providing and fixing Heavy class SS grating with Cockroach proof SS strainer of approved design including setting in floor with cement mortar to match with floor finish as per architect requirement & suitable for waste and FD. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14.1 | 501040000 | Size 100 mm x 100 mm or 100 mm dia | [8 empty] | No. | 0 | 790 | 0 | 790 | 39.5 | 0 | 829.5 | 79 | 9.7644 | 0 | 88.7644 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14.2 | 501040000 | Size 150 mm x 150 mm or 125 mm di | [8 empty] | No. | 500 | 793 | 0 | 793 | 39.65 | 0 | 832.65 | 103 | 12.7308 | 0 | 115.7308 | 416325 | 57865.4 | 474190.4 | 10 | 500 | 39650 | 0 | 39650 | 1982.5 | 0 | 41632.5 | 5150 | 636.54 | 0 | 5786.54 | 47419.04
15 | 501040000 | Providing and fixing heavy duty S.S. Floor grating with frame of approved design including setting in floor with cement mortar to match with floor finish as per architect requirement. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15.1 | 501040000 | Size 100 mm x 100 mm or 100 mm dia | [8 empty] | No. | 0 | 540 | 0 | 540 | 27 | 0 | 567 | 79 | 9.7644 | 0 | 88.7644 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15.2 | 501040000 | Size 150 mm x 150 mm or 125 mm dia | [8 empty] | No. | 0 | 810 | 0 | 810 | 40.5 | 0 | 850.5 | 105 | 12.978 | 0 | 117.978 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | 501040000 | Providing and fixing CP brass heavy duty grating with frame of approved design including setting in floor with cement mortar to match with floor finish as per architect requirement. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16.1 | 501040000 | Size 100 mm x 100 mm or 100 mm dia | [8 empty] | No. | 0 | 185 | 0 | 185 | 9.25 | 0 | 194.25 | 53 | 6.5508 | 0 | 59.5508 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16.2 | 501040000 | Size 150 mm x 150 mm or 125 mm dia | [8 empty] | No. | 0 | 290 | 0 | 290 | 14.5 | 0 | 304.5 | 79 | 9.7644 | 0 | 88.7644 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 501040000 | Providing and fixing 6 mm thick CP brass hinged grating with rim of approved design including setting floor with cement mortar (as per approved by Project Manager design). | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17.1 | 501040000 | For 75 mm dia pipe | [8 empty] | No. | 0 | 360 | 0 | 360 | 18 | 0 | 378 | 53 | 6.5508 | 0 | 59.5508 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17.2 | 501040000 | For 100 mm dia pipes | [8 empty] | No. | 200 | 235 | 0 | 235 | 11.75 | 0 | 246.75 | 77 | 9.5172 | 0 | 86.5172 | 49350 | 17303.44 | 66653.44 | 10 | 200 | 4700 | 0 | 4700 | 235 | 0 | 4935 | 1540 | 190.344 | 0 | 1730.344 | 6665.344
18 | 501040000 | Providing and fixing ABS heavy duty grating with frame of approved design including setting in floor with cement mortar to match with floor finish as per architect requirement. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18.1 | 501040000 | Size 100 mm x 100 mm | [8 empty] | No. | 0 | 480 | 0 | 480 | 24 | 0 | 504 | 53 | 6.5508 | 0 | 59.5508 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18.2 | 501040000 | Size 150 mm x 150 mm | [8 empty] | No. | 0 | 600 | 0 | 600 | 30 | 0 | 630 | 79 | 9.7644 | 0 | 88.7644 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 501040000 | Providing and fixing Brass floor clean out plug comprising of GI pipe, socket, elbow, extension piece caulked to pipe and cast brass plug with suitable inlet key for opening male threaded joint with GI class C pipe & socket. Including drip seal caulked to CI pipes or CI class LA pipes complete as required. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19.1 | 501040000 | For 75 mm dia pip | [8 empty] | No. | 5 | 999 | 0 | 999 | 49.95 | 0 | 1048.95 | 103 | 12.7308 | 0 | 115.7308 | 5244.75 | 578.654 | 5823.404 | 10 | 5 | 499.5 | 0 | 499.5 | 24.975 | 0 | 524.475 | 51.5 | 6.3654 | 0 | 57.8654 | 582.3404
19.2 | 501040000 | For 100 mm dia pip | [8 empty] | No. | 10 | 1470 | 0 | 1470 | 73.5 | 0 | 1543.5 | 103 | 12.7308 | 0 | 115.7308 | 15435 | 1157.308 | 16592.308 | 10 | 10 | 1470 | 0 | 1470 | 73.5 | 0 | 1543.5 | 103 | 12.7308 | 0 | 115.7308 | 1659.2308
19.3 | 501040000 | For 150 mm dia pip | [8 empty] | No. | 5 | 2117 | 0 | 2117 | 105.85 | 0 | 2222.85 | 154 | 19.0344 | 0 | 173.0344 | 11114.25 | 865.172 | 11979.422 | 10 | 5 | 1058.5 | 0 | 1058.5 | 52.925 | 0 | 1111.425 | 77 | 9.5172 | 0 | 86.5172 | 1197.9422
19.4 | 501040000 | For 200 mm dia pipe | [8 empty] | No. | 0 | 2940 | 0 | 2940 | 147 | 0 | 3087 | 210 | 25.956 | 0 | 235.956 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 501040000 | Providing and fixing cleaning eye on horizontal CI soil & waste pipes, for med of 300 mm long GI pipe with one plain end lead / drip seal caulked in to the collar of CI pipe and the other end with flange which in covered by neoprene rubber gasket and blank flange, complete with nuts, bolts etc and hot dip galvanization after fabrication to the satisfaction of the Project Manager / Consultants. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20.1 | 501040000 | For 75 mm dia pipw | [8 empty] | No. | 5 | 490 | 0 | 490 | 24.5 | 0 | 514.5 | 52 | 6.4272 | 0 | 58.4272 | 2572.5 | 292.136 | 2864.636 | 10 | 5 | 245 | 0 | 245 | 12.25 | 0 | 257.25 | 26 | 3.2136 | 0 | 29.2136 | 286.4636
20.2 | 501040000 | For 100 mm dia pi | [8 empty] | No. | 8 | 588 | 0 | 588 | 29.4 | 0 | 617.4 | 77 | 9.5172 | 0 | 86.5172 | 4939.2 | 692.1376 | 5631.3376 | 10 | 8 | 470.4 | 0 | 470.4 | 23.52 | 0 | 493.92 | 61.6 | 7.6138 | 0 | 69.2138 | 563.1338
20.3 | 501040000 | For 150 mm dia pipe | [8 empty] | No. | 10 | 769 | 0 | 769 | 38.45 | 0 | 807.45 | 103 | 12.7308 | 0 | 115.7308 | 8074.5 | 1157.308 | 9231.808 | 10 | 10 | 769 | 0 | 769 | 38.45 | 0 | 807.45 | 103 | 12.7308 | 0 | 115.7308 | 923.1808
20.4 | 501040000 | For 200 mm dia pie | [8 empty] | No. | 10 | 970 | 0 | 970 | 48.5 | 0 | 1018.5 | 128 | 15.8208 | 0 | 143.8208 | 10185 | 1438.208 | 11623.208 | 10 | 10 | 970 | 0 | 970 | 48.5 | 0 | 1018.5 | 128 | 15.8208 | 0 | 143.8208 | 1162.3208
20.5 | 501040000 | For 250 mm dia pipe | [8 empty] | No. | 5 | 1215 | 0 | 1215 | 60.75 | 0 | 1275.75 | 155 | 19.158 | 0 | 174.158 | 6378.75 | 870.79 | 7249.54 | 10 | 5 | 607.5 | 0 | 607.5 | 30.375 | 0 | 637.875 | 77.5 | 9.579 | 0 | 87.079 | 724.954
21 | 501040000 | Providing and fixing P.V.C. WC connector (straight or bend type) with rubber lip ring. Including 110 mm dia PVC pipe / bend of required length and proper connection with M seal to C.I. pipe complete as required | [8 empty] | No. | 270 | 196 | 0 | 196 | 9.8 | 0 | 205.8 | 52 | 6.4272 | 0 | 58.4272 | 55566 | 15775.344 | 71341.344 | 10 | 270 | 5292 | 0 | 5292 | 264.6 | 0 | 5556.6 | 1404 | 173.5344 | 0 | 1577.5344 | 7134.1344
22 | 501040000 | Making drainage connection to kitchen / laundry equipment, appliances etc. including necessary GI pipes / fittings & Flexiable pipes complete as required. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22.1 | 501040000 | 32 mm dia to 50 mm dia | [8 empty] | No. | 40 | 392 | 0 | 392 | 19.6 | 0 | 411.6 | 52 | 6.4272 | 0 | 58.4272 | 16464 | 2337.088 | 18801.088 | 10 | 40 | 1568 | 0 | 1568 | 78.4 | 0 | 1646.4 | 208 | 25.7088 | 0 | 233.7088 | 1880.1088
23 | 501040000 | Providing and fixing 25 mm thick CI grating with 30 x 30 x 5 mm angle frame with hold fasts welded at intervals of 600 mm with frame, setting with cement mortar 1:3 (1 cement : 3 sand) true to levels as required (for plant room). All M.S. Angles etc. must be hot dip galvanized. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23.1 | 501040000 | 300 mm wide x 600 mm length | [8 empty] | No. | 0 | 3000 | 0 | 3000 | 150 | 0 | 3150 | 263 | 32.5068 | 0 | 295.5068 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23.2 | 501040000 | 200 mm wide x 600 mm length | [8 empty] | No. | 0 | 2500 | 0 | 2500 | 125 | 0 | 2625 | 210 | 25.956 | 0 | 235.956 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 501040000 | Providing & fixing rain water Khurras size 450x450 mm required depth with lead flashing around the pipe with one piece lead sheet of 3 mm thick set on a layer of cold bitumen. Including Heavy duty CI/MS grating as per drawing complete as required. | [8 empty] | No. | 10 | 2842 | 0 | 2842 | 142.1 | 0 | 2984.1 | 926 | 114.4536 | 0 | 1040.4536 | 29841 | 10404.536 | 40245.536 | 10 | 10 | 2842 | 0 | 2842 | 142.1 | 0 | 2984.1 | 926 | 114.4536 | 0 | 1040.4536 | 4024.5536
25 | 501040000 | Constructing Grease Trap of size as mentioned below of 1200 liquid depth in brick work of class 75 with cement mortar (1:6), inside plastering 16 mm thick with cement mortar 1:3 with floating coat of neat cement and rough plaster on outside. Including aluminium bucket as per detail to collect the grease. RCC top slab with 2 nos. 600 x 600 mm dia medium duty, double seal manhole covers with frame (weight of covers & weight of frame 75 Kg), necessary 150 mm thick foundation concrete (1:2:4). | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25.1 | 501040000 | 2500 x 1200 mm | [8 empty] | No. | 0 | 131250 | 0 | 131250 | 6562.5 | 0 | 137812.5 | 21000 | 2595.6 | 0 | 23595.6 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E | 501040000 | EXTERNAL SEWAGE / STORM WATER DRAINAGE: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 501040000 | Providing, laying, jointing and testing in position the following C.I. pipes class (LA) conforming to IS: 1536 for drainage cut to required lengths making proper connections with drip seal of required depths. Pipe to be laid below ground level in trenches upto required depth including excavation in all kind of soil (hard rock), dewatering, refilling, watering, ramming & removing the surplus excavated material and making good the same complete as required. Cost shall be inclusive of providing protection to pipe all round / haunches as per specification. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.1 | 501040000 | 100mm d | [8 empty] | RM | 50 | 1827 | 0 | 1827 | 91.35 | 0 | 1918.35 | 412 | 50.9232 | 0 | 462.9232 | 95917.5 | 23146.16 | 119063.66 | 10 | 50 | 9135 | 0 | 9135 | 456.75 | 0 | 9591.75 | 2060 | 254.616 | 0 | 2314.616 | 11906.366
1.2 | 501040000 | 150 mm diaaa | [8 empty] | RM | 10 | 2941 | 0 | 2941 | 147.05 | 0 | 3088.05 | 618 | 76.3848 | 0 | 694.3848 | 30880.5 | 6943.848 | 37824.348 | 10 | 10 | 2941 | 0 | 2941 | 147.05 | 0 | 3088.05 | 618 | 76.3848 | 0 | 694.3848 | 3782.4348
2 | 501040000 | Providing, fixing, jointing and testing in position the following UPVC pipes confirming to IS:4985 of 6 Kg / Sq.cm for drainage system cut to required length. Pipe to be laid below ground level in trenches upto required depth including excavation in all kind of soil (hard rock), dewatering, refilling, watering, ramming and removing the surplus excavated material and making good the same complete as required. Cost shall be inclusive of providing protection to pipe all round / haunches as per specification. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.1 | 501040000 | 110 mm diaaa | [8 empty] | RM | 10 | 496 | 0 | 496 | 24.8 | 0 | 520.8 | 180 | 22.248 | 0 | 202.248 | 5208 | 2022.48 | 7230.48 | 10 | 10 | 496 | 0 | 496 | 24.8 | 0 | 520.8 | 180 | 22.248 | 0 | 202.248 | 723.048
2.2 | 501040000 | 160 mm diaaa | [8 empty] | RM | 25 | 1208 | 0 | 1208 | 60.4 | 0 | 1268.4 | 262 | 32.3832 | 0 | 294.3832 | 31710 | 7359.58 | 39069.58 | 10 | 25 | 3020 | 0 | 3020 | 151 | 0 | 3171 | 655 | 80.958 | 0 | 735.958 | 3906.958
2.3 | 501040000 | 200 mm dia | [8 empty] | RM | 0 | 1986 | 0 | 1986 | 99.3 | 0 | 2085.3 | 329 | 40.6644 | 0 | 369.6644 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.4 | 501040000 | 250 mm dia | [8 empty] | RM | 0 | 3340 | 0 | 3340 | 167 | 0 | 3507 | 412 | 50.9232 | 0 | 462.9232 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 501040000 | Providing,laying, jointing and testing socketed and spigotted RCC pipes (NP2 class) conforming to IS:458 collars jointed with stiff mixture of cement mortar in the proporation of 1:2 (1 cement : 2 find sand) laid to correct levels below ground in trenches upto required depth including excavation in all kind of soil (hard / soft), dewatering, refilling, watering, ramming and removing the surplus excavated material and making good the same complete as required. Cost shall be inclusive of providing protection to pipe all round / haunches as per specification. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.1 | 501040000 | 150 mm dia | [8 empty] | RM | 0 | 465 | 0 | 465 | 23.25 | 0 | 488.25 | 189 | 23.3604 | 0 | 212.3604 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.2 | 501040000 | 200 mm diaaa | [8 empty] | RM | 20 | 560 | 0 | 560 | 28 | 0 | 588 | 247 | 30.5292 | 0 | 277.5292 | 11760 | 5550.584 | 17310.584 | 10 | 20 | 1120 | 0 | 1120 | 56 | 0 | 1176 | 494 | 61.0584 | 0 | 555.0584 | 1731.0584
3.3 | 501040000 | 250 mm diaaa | [8 empty] | RM | 10 | 563 | 0 | 563 | 28.15 | 0 | 591.15 | 309 | 38.1924 | 0 | 347.1924 | 5911.5 | 3471.924 | 9383.424 | 10 | 10 | 563 | 0 | 563 | 28.15 | 0 | 591.15 | 309 | 38.1924 | 0 | 347.1924 | 938.3424
3.4 | 501040000 | 300 mm diaa | [8 empty] | RM | 10 | 382 | 0 | 382 | 19.1 | 0 | 401.1 | 370 | 45.732 | 0 | 415.732 | 4011 | 4157.32 | 8168.32 | 10 | 10 | 382 | 0 | 382 | 19.1 | 0 | 401.1 | 370 | 45.732 | 0 | 415.732 | 816.832
3.5 | 501040000 | 350 mm diaa | [8 empty] | RM | 5 | 996 | 0 | 996 | 49.8 | 0 | 1045.8 | 432 | 53.3952 | 0 | 485.3952 | 5229 | 2426.976 | 7655.976 | 10 | 5 | 498 | 0 | 498 | 24.9 | 0 | 522.9 | 216 | 26.6976 | 0 | 242.6976 | 765.5976
3.6 | 501040000 | 400 mm dia | [8 empty] | RM | 5 | 1122 | 0 | 1122 | 56.1 | 0 | 1178.1 | 494 | 61.0584 | 0 | 555.0584 | 5890.5 | 2775.292 | 8665.792 | 10 | 5 | 561 | 0 | 561 | 28.05 | 0 | 589.05 | 247 | 30.5292 | 0 | 277.5292 | 866.5792
3.7 | 501040000 | 450 mm dia | [8 empty] | RM | 0 | 1668 | 0 | 1668 | 83.4 | 0 | 1751.4 | 567 | 70.0812 | 0 | 637.0812 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.8 | 501040000 | 600 mm dia | [8 empty] | RM | 0 | 3006 | 0 | 3006 | 150.3 | 0 | 3156.3 | 756 | 93.4416 | 0 | 849.4416 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 501040000 | Construction of road gully chamber of the following sizes in brick work with bricks of class 75 in cement mortar 1 : 5 (1 cement : 5 find sand) necessary foundation concrete(1 : 4 : 8). Inside & outside plastering 12 mm thick with cement mortar 1 : 3 with a floating a coat of neat cement. Including the RCC top slab for fixing the grating including necessary excavation, dewatering, refilling, watering, ramming, removing, the surplus excavated material and making good the same complete as required. Cost shall be inclusive of providing, DI grating with frame. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4.1 | 501040000 | Internal size 450 x 500 x 450 - 600 mm deep; Pre Cast /SFRC Grating with frame 450 x 450 mm | [8 empty] | No. | 5 | 4900 | 0 | 4900 | 245 | 0 | 5145 | 2573 | 318.0228 | 0 | 2891.0228 | 25725 | 14455.114 | 40180.114 | 10 | 5 | 2450 | 0 | 2450 | 122.5 | 0 | 2572.5 | 1286.5 | 159.0114 | 0 | 1445.5114 | 4018.0114
4.2 | 501040000 | Internal size 450 x 500 x 600 - 750 mm deep; DI Grating with frame 600 x 600 mm (B-125; 70 kg) | [8 empty] | No. | 0 | 11800 | 0 | 11800 | 590 | 0 | 12390 | 3675 | 454.23 | 0 | 4129.23 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 501040000 | Designing and constructing brick masonry inspection chamber of the following sizes in brick work of class 75 in cement mortar 1:5 (1 cement:5 fine sand), R.C.C. top slab with 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm. nominal size) embeded with frame for manhole, RCC foundation slab. 1:2:4 mix (1 cement : 2 coarse sand:4 graded stone aggregate 40 mm nominal size) both inside and outside of plastering 12 mm thick with cement motar 1:3 (1 cement : 3 coarse sand) with a floating coat of neat cement on inside face, proper water proofing to ensure no ground water seepage in the manhole, Poly propylene (conforming to ASTMD - 4101) foot rests (meeting the 224 kg load requirement as per IS 5455) at 300 mm spacing, benching and making channels with 1:2:4 cement concrete neatly finished, including necessary centering and shuttering, reinforcement, excavation, in all kind of soil, dewatering, refilling, watering, ramming and removing the surplus excavated earth, making good the same complete as required. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.1 | 501040000 | Contractor shall submit the structural design and drawings for the approval of Project Manager prior to execution. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.2 | 501040000 | 450 x 450 mm x 600mm | [8 empty] | No. | 0 | 6600 | 0 | 6600 | 330 | 0 | 6930 | 2888 | 356.9568 | 0 | 3244.9568 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.3 | 501040000 | 900 x 600 mm ( 600 to 900 mm deep) | [8 empty] | Nos. | 3 | 9310 | 0 | 9310 | 465.5 | 0 | 9775.5 | 3087 | 381.5532 | 0 | 3468.5532 | 29326.5 | 10405.6596 | 39732.1596 | 10 | 3 | 2793 | 0 | 2793 | 139.65 | 0 | 2932.65 | 926.1 | 114.466 | 0 | 1040.566 | 3973.216
5.4 | 501040000 | Extra depth for (5.2) above 90 cm to 120 cm | [8 empty] | RM | 3 | 1470 | 0 | 1470 | 73.5 | 0 | 1543.5 | 515 | 63.654 | 0 | 578.654 | 4630.5 | 1735.962 | 6366.462 | 10 | 3 | 441 | 0 | 441 | 22.05 | 0 | 463.05 | 154.5 | 19.0962 | 0 | 173.5962 | 636.6462
5.5 | 501040000 | Extra depth for (5.2) above 120cm to 180 cm | [8 empty] | RM | 3 | 2450 | 0 | 2450 | 122.5 | 0 | 2572.5 | 1029 | 127.1844 | 0 | 1156.1844 | 7717.5 | 3468.5532 | 11186.0532 | 10 | 3 | 735 | 0 | 735 | 36.75 | 0 | 771.75 | 308.7 | 38.1553 | 0 | 346.8553 | 1118.6053
5.6 | 501040000 | 1500 mm dia circular type (2300 mm deep) | [8 empty] | No. | 1 | 15680 | 0 | 15680 | 784 | 0 | 16464 | 4631 | 572.3916 | 0 | 5203.3916 | 16464 | 5203.3916 | 21667.3916 | 10 | 1 | 1568 | 0 | 1568 | 78.4 | 0 | 1646.4 | 463.1 | 57.2392 | 0 | 520.3392 | 2166.7392
5.7 | 501040000 | Extra depth for (5.3) above 150cm & above | [8 empty] | RM | 3 | 3185 | 0 | 3185 | 159.25 | 0 | 3344.25 | 1029 | 127.1844 | 0 | 1156.1844 | 10032.75 | 3468.5532 | 13501.3032 | 10 | 3 | 955.5 | 0 | 955.5 | 47.775 | 0 | 1003.275 | 308.7 | 38.1553 | 0 | 346.8553 | 1350.1303
6 | 501040000 | Providing & fixing Ductile Iron Manhole cover with frame: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6.1 | 501040000 | For 600 x 900 mm MH | [8 empty] | No. | 1 | 11270 | 0 | 11270 | 563.5 | 0 | 11833.5 | 515 | 63.654 | 0 | 578.654 | 11833.5 | 578.654 | 12412.154 | 10 | 1 | 1127 | 0 | 1127 | 56.35 | 0 | 1183.35 | 51.5 | 6.3654 | 0 | 57.8654 | 1241.2154
6.1.1 | 501040000 | 500 x 450 mm, Medium Duty (B-125) Wt - 45 kg | [8 empty] | No. | 5 | 4165 | 0 | 4165 | 208.25 | 0 | 4373.25 | 515 | 63.654 | 0 | 578.654 | 21866.25 | 2893.27 | 24759.52 | 10 | 5 | 2082.5 | 0 | 2082.5 | 104.125 | 0 | 2186.625 | 257.5 | 31.827 | 0 | 289.327 | 2475.952
6.2 | 501040000 | For 1500 mm Circular MH | [8 empty] | No. | 1 | 15680 | 0 | 15680 | 784 | 0 | 16464 | 1029 | 127.1844 | 0 | 1156.1844 | 16464 | 1156.1844 | 17620.1844 | 10 | 1 | 1568 | 0 | 1568 | 78.4 | 0 | 1646.4 | 102.9 | 12.7184 | 0 | 115.6184 | 1762.0184
6.2.1 | 501040000 | 600 mm dia, Heavy Duty (C-250), Wt : 85 kg | [8 empty] | No. | 1 | 8034 | 0 | 8034 | 401.7 | 0 | 8435.7 | 515 | 63.654 | 0 | 578.654 | 8435.7 | 578.654 | 9014.354 | 10 | 1 | 803.4 | 0 | 803.4 | 40.17 | 0 | 843.57 | 51.5 | 6.3654 | 0 | 57.8654 | 901.4354
7 | 501040000 | Supply and installing Rain Water Percolation pits - 1500 mm in diameter up to 3200 mm deep, bottom 500 mm filled with boulders 150 - 230 mm size, over which one no. UPVC 160 mm dia (4.0 kg/cm2) perforated pipe with 8 mm dia perforations protected by a cowl on upper end 2100 mm long, surrounding filled with broken bricks up to 1000 mm, pebbles 40 to 50 mm up to 400 mm, Gravel 15 to 25 mm up to 400 mm and upper most layer of 300 mm with coarse sand of 3 to 5 mm. The top 600 mm shall be left open, with RCC grated cover on top. | [8 empty] | No. | 9 | 62040 | 0 | 62040 | 3102 | 0 | 65142 | 24300 | 3003.48 | 0 | 27303.48 | 586278 | 245731.32 | 832009.32 | 10 | 9 | 55836 | 0 | 55836 | 2791.8 | 0 | 58627.8 | 21870 | 2703.132 | 0 | 24573.132 | 83200.932
8 | 501040000 | Providing and excuting reverse bore for rain water recharing comprising of rain water harvesting pit as per plumbing site plan drawing complete with PVC (6 kg / sqcm) 160 mm dia slotted pipehaving 3 mm slot, adequate size of bore filled with 3 - 6 mm gravels, complete with bail plug at bottom. The reverse bore shall be 30 meter in depth from the natural ground level and the execution of some shall be in accordance to RWH & conservation manual of CPWD, Govt. of India. | [8 empty] | Job | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5145000 | 635922 | 0 | 5780922 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 501040000 | Providing and fixing SEWER TRAP with vent cum Air inlet with MICA flap valve complete with inspection cover with frame for Municipal connection. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.1 | 501040000 | Size 150 mm | [8 empty] | No. | 1 | 2205 | 0 | 2205 | 110.25 | 0 | 2315.25 | 257.25 | 31.7961 | 0 | 289.0461 | 2315.25 | 289.0461 | 2604.2961 | 10 | 1 | 220.5 | 0 | 220.5 | 11.025 | 0 | 231.525 | 25.725 | 3.1796 | 0 | 28.9046 | 260.4296
10 | 501040000 | Making connection to existing or new Municipal sewer / storm water drain including necessary excavation and breaking the wall of municipal manhole and making good the same with Cement mortar 1:3, finished with a floating coat of neat cement and making drains etc. complete. Removing the excavated surplus material. This also includes the contractor for liasoning work such as filling necessary applications, submission of forms for approval to the municipal authorities, depositing and making channels for the necessary fees and other amounts as required for getting the premises / installations inspected and approved and all other formalities required till the sewer / storm water connection is obtained. All the expenses incurred in this regard shall be borne by the Contractor, except for the payments to be made for any security deposits which will be reimbursed on production of original voucher. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10.1 | 501040000 | For Sewer Connection | [8 empty] | Job | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 147000 | 18169.2 | 0 | 165169.2 | 0 | 165169.2 | 165169.2 | 10 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 14700 | 1816.92 | 0 | 16516.92 | 16516.92
10.2 | 501040000 | For Storm Water Connection | [8 empty] | Job | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 122500 | 15141 | 0 | 137641 | 0 | 137641 | 137641 | 10 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 12250 | 1514.1 | 0 | 13764.1 | 13764.1
F | 501060000 | CIVIL WORKS / MISCELLANEOUS ITEMS: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 501060000 | Providing and fixing 600 mm long MS hot dip galvanized PUDDLE FLANGES fabricated out of 6 mm thick MS plates of suitable size and IS:1239 heavy class pipes properly fixed in walls & top slab of tanks. The entire fittings shall be hot dipped galvanized after fabrication. Length shall be minimum 600 mm or wall thickness plus 200 mm on either side (which ever is more). | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.1 | 501060000 | 20 mm dia (screwed ends) | [8 empty] | Nos. | 0 | 552 | 0 | 552 | 27.6 | 0 | 579.6 | 84 | 10.3824 | 0 | 94.3824 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.2 | 501060000 | 25 mm dia (screwed ends) | [8 empty] | Nos. | 0 | 619 | 0 | 619 | 30.95 | 0 | 649.95 | 84 | 10.3824 | 0 | 94.3824 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.3 | 501060000 | 32 mm dia (screwed ends) | [8 empty] | Nos. | 0 | 706 | 0 | 706 | 35.3 | 0 | 741.3 | 109 | 13.4724 | 0 | 122.4724 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.4 | 501060000 | 40 mm dia (screwed ends) | [8 empty] | Nos. | 0 | 1065 | 0 | 1065 | 53.25 | 0 | 1118.25 | 134 | 16.5624 | 0 | 150.5624 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.5 | 501060000 | 50 mm dia (flanged ends) | [8 empty] | Nos. | 0 | 1195 | 0 | 1195 | 59.75 | 0 | 1254.75 | 168 | 20.7648 | 0 | 188.7648 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.6 | 501060000 | 80 mm dia (flanged ends) | [8 empty] | Nos. | 0 | 1838 | 0 | 1838 | 91.9 | 0 | 1929.9 | 269 | 33.2484 | 0 | 302.2484 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.7 | 501060000 | 100 mm dia (flanged ends) | [8 empty] | Nos. | 0 | 2659 | 0 | 2659 | 132.95 | 0 | 2791.95 | 336 | 41.5296 | 0 | 377.5296 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.8 | 501060000 | 150 mm dia (flanged ends) | [8 empty] | Nos. | 0 | 3528 | 0 | 3528 | 176.4 | 0 | 3704.4 | 504 | 62.2944 | 0 | 566.2944 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.9 | 501060000 | 200 mm dia (flanged ends) | [8 empty] | Nos. | 0 | 5218 | 0 | 5218 | 260.9 | 0 | 5478.9 | 672 | 83.0592 | 0 | 755.0592 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.1 | 501060000 | 250 mm dia (flanged ends) | [8 empty] | Nos. | 0 | 6500 | 0 | 6500 | 325 | 0 | 6825 | 840 | 103.824 | 0 | 943.824 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.11 | 501060000 | 300 mm dia (flanged ends) | [8 empty] | Nos. | 0 | 8719 | 0 | 8719 | 435.95 | 0 | 9154.95 | 1008 | 124.5888 | 0 | 1132.5888 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 501060000 | Providing and fixing blank flanges, making flanged joints with bolts, nuts, washers and rubber insertion 3 mm thick, testing the flange and joints etc. complete for pipes of following diameter. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.1 | 501060000 | 50 mm diaa | [8 empty] | Pair | 1 | 666 | 0 | 666 | 33.3 | 0 | 699.3 | 123 | 15.2028 | 0 | 138.2028 | 699.3 | 138.2028 | 837.5028 | 10 | 1 | 66.6 | 0 | 66.6 | 3.33 | 0 | 69.93 | 12.3 | 1.5203 | 0 | 13.8203 | 83.7503
2.2 | 501060000 | 80 mm dia | [8 empty] | Pair | 3 | 1421 | 0 | 1421 | 71.05 | 0 | 1492.05 | 195 | 24.102 | 0 | 219.102 | 4476.15 | 657.306 | 5133.456 | 10 | 3 | 426.3 | 0 | 426.3 | 21.315 | 0 | 447.615 | 58.5 | 7.2306 | 0 | 65.7306 | 513.3456
2.3 | 501060000 | 100 mm diaaa | [8 empty] | Pair | 5 | 2038 | 0 | 2038 | 101.9 | 0 | 2139.9 | 247 | 30.5292 | 0 | 277.5292 | 10699.5 | 1387.646 | 12087.146 | 10 | 5 | 1019 | 0 | 1019 | 50.95 | 0 | 1069.95 | 123.5 | 15.2646 | 0 | 138.7646 | 1208.7146
2.4 | 501060000 | 150 mm diam | [8 empty] | Pair | 2 | 3361 | 0 | 3361 | 168.05 | 0 | 3529.05 | 370 | 45.732 | 0 | 415.732 | 7058.1 | 831.464 | 7889.564 | 10 | 2 | 672.2 | 0 | 672.2 | 33.61 | 0 | 705.81 | 74 | 9.1464 | 0 | 83.1464 | 788.9564
3 | 501060000 | Providing and fixing in position the UPVC SLEEVES each to be embedded in RCC walls / beams. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.1 | 501060000 | 250 mm dia (600 mm long) | [8 empty] | No. | 1 | 3626 | 0 | 3626 | 181.3 | 0 | 3807.3 | 206 | 25.4616 | 0 | 231.4616 | 3807.3 | 231.4616 | 4038.7616 | 10 | 1 | 362.6 | 0 | 362.6 | 18.13 | 0 | 380.73 | 20.6 | 2.5462 | 0 | 23.1462 | 403.8762
3.2 | 501060000 | 150 mm dia (600 mm long) | [8 empty] | No. | 5 | 1979 | 0 | 1979 | 98.95 | 0 | 2077.95 | 128 | 15.8208 | 0 | 143.8208 | 10389.75 | 719.104 | 11108.854 | 10 | 5 | 989.5 | 0 | 989.5 | 49.475 | 0 | 1038.975 | 64 | 7.9104 | 0 | 71.9104 | 1110.8854
3.3 | 501060000 | 100 mm dia (600 mm long) | [8 empty] | No. | 5 | 1176 | 0 | 1176 | 58.8 | 0 | 1234.8 | 103 | 12.7308 | 0 | 115.7308 | 6174 | 578.654 | 6752.654 | 10 | 5 | 588 | 0 | 588 | 29.4 | 0 | 617.4 | 51.5 | 6.3654 | 0 | 57.8654 | 675.2654
4 | 501060000 | Providing and fixing DI Grating (Grade A-15) with 40 x 40 mm angle frame with hold fasts welded at intervals of 600 mm setting with cement mortar 1:3 (1 cement : 3 sand) true to levels as required (for Plant Room & Car Parking Areas) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4.1 | 501060000 | 300 mm wide x 600 mm length (wt : 12 Kg) | [8 empty] | No. | 0 | 1876 | 0 | 1876 | 93.8 | 0 | 1969.8 | 210 | 25.956 | 0 | 235.956 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4.2 | 501060000 | 450 mm wide x 600 mm length (wt : 16 kg) | [8 empty] | No. | 0 | 3125 | 0 | 3125 | 156.25 | 0 | 3281.25 | 315 | 38.934 | 0 | 353.934 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4.3 | 501060000 | Internal size 600 x 600 Pre Cast/ SFRC Grating with frame | [8 empty] | No. | 0 | 5500 | 0 | 5500 | 275 | 0 | 5775 | 473 | 58.4628 | 0 | 531.4628 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 501060000 | Providing & fixing GI Waste pipe for upper basement drainage. Cost shall be inclusive of providing, jointing & fixing GI heavy class pipe, including all necessary fittings and especial such as bends, elbows, unions, socket, connection with waste puddle flange at ceiling slabs etc. Fixing at wall / ceiling / clamping at color with galvanized steel clamps & hangers etc. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.1 | 501060000 | 100 mm dia | [8 empty] | RM. | 0 | 1750 | 0 | 1750 | 87.5 | 0 | 1837.5 | 420 | 51.912 | 0 | 471.912 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.2 | 501060000 | 80 mm diam | [8 empty] | RM. | 250 | 764 | 0 | 764 | 38.2 | 0 | 802.2 | 329 | 40.6644 | 0 | 369.6644 | 200550 | 92416.1 | 292966.1 | 10 | 250 | 19100 | 0 | 19100 | 955 | 0 | 20055 | 8225 | 1016.61 | 0 | 9241.61 | 29296.61
6 | 501060000 | Providing and fixing 6 mm thick CP brass hinged grating with rim of approved design including setting floor with cement mortar (as per approved by Project Manager design). | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6.1 | 501060000 | For 100 mm dia pipe | [8 empty] | Nos. | 25 | 465 | 0 | 465 | 23.25 | 0 | 488.25 | 103 | 12.7308 | 0 | 115.7308 | 12206.25 | 2893.27 | 15099.52 | 10 | 25 | 1162.5 | 0 | 1162.5 | 58.125 | 0 | 1220.625 | 257.5 | 31.827 | 0 | 289.327 | 1509.952
7 | 501060000 | Providing & fixing Planter Top / Bottom grating including GI hopper. Cost shall be inclusive of providing SS / Bronze grating with connection to GI socket / waste pipe. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7.1 | 501060000 | 50 mm diam | [8 empty] | Nos. | 15 | 1225 | 0 | 1225 | 61.25 | 0 | 1286.25 | 154 | 19.0344 | 0 | 173.0344 | 19293.75 | 2595.516 | 21889.266 | 10 | 15 | 1837.5 | 0 | 1837.5 | 91.875 | 0 | 1929.375 | 231 | 28.5516 | 0 | 259.5516 | 2188.9266
7.2 | 501060000 | 65 mm dia | [8 empty] | Nos. | 0 | 1772 | 0 | 1772 | 88.6 | 0 | 1860.6 | 158 | 19.5288 | 0 | 177.5288 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7.3 | 501060000 | 80 asas diaaa | [8 empty] | Nos. | 10 | 1842 | 0 | 1842 | 92.1 | 0 | 1934.1 | 206 | 25.4616 | 0 | 231.4616 | 19341 | 2314.616 | 21655.616 | 10 | 10 | 1842 | 0 | 1842 | 92.1 | 0 | 1934.1 | 206 | 25.4616 | 0 | 231.4616 | 2165.5616
7.4 | 501060000 | 100 mm dia | [8 empty] | Nos. | 10 | 2303 | 0 | 2303 | 115.15 | 0 | 2418.15 | 257 | 31.7652 | 0 | 288.7652 | 24181.5 | 2887.652 | 27069.152 | 10 | 10 | 2303 | 0 | 2303 | 115.15 | 0 | 2418.15 | 257 | 31.7652 | 0 | 288.7652 | 2706.9152
8 | 501060000 | Providing and fixing 600 mm dia ductile iron (heavy duty) water tank circular cover with frame (as per EN-124) with lockable arrangement complete in all regards (Total WT of cover and frame tobe not less than 85 kg). | [8 empty] | No. | 0 | 15000 | 0 | 15000 | 750 | 0 | 15750 | 525 | 64.89 | 0 | 589.89 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8.1 | 501060000 | Providing laying, jointing & testing perforated PVC (class III) pipes with 6 to 8 mm holes on the ¾ circumference of the pipe for sub soil drainage of the courtyard. Provision of geo textile wrapping on the pipe & 10 to 15 mm pebble to prevent ingress of fine particles, shall also be made & the installation shall be to the direction of the landscape consultant & made good to the satisfaction of the Project Manager. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8.2 | 501060000 | 110 mm dia | [8 empty] | RM | 25 | 499 | 0 | 499 | 24.95 | 0 | 523.95 | 123 | 15.2028 | 0 | 138.2028 | 13098.75 | 3455.07 | 16553.82 | 10 | 25 | 1247.5 | 0 | 1247.5 | 62.375 | 0 | 1309.875 | 307.5 | 38.007 | 0 | 345.507 | 1655.382
8.3 | 501060000 | 160 mm dia | [8 empty] | RM | 25 | 1357 | 0 | 1357 | 67.85 | 0 | 1424.85 | 206 | 25.4616 | 0 | 231.4616 | 35621.25 | 5786.54 | 41407.79 | 10 | 25 | 3392.5 | 0 | 3392.5 | 169.625 | 0 | 3562.125 | 515 | 63.654 | 0 | 578.654 | 4140.779
9 | 501060000 | Providing and fixing electronic type level indicator for water tanks mounting in panel with the following features, level display, alarm when water level is low or high, full range from one level to four level display and manual reset for alarm etc. with electrical wiring conduit supports from wall & ceiling probs and all other accessories complete as required.(6 Tanks) | [8 empty] | Set | 1 | 22050 | 0 | 22050 | 1102.5 | 0 | 23152.5 | 1544 | 190.8384 | 0 | 1734.8384 | 23152.5 | 1734.8384 | 24887.3384 | 10 | 1 | 2205 | 0 | 2205 | 110.25 | 0 | 2315.25 | 154.4 | 19.0838 | 0 | 173.4838 | 2488.7338
9.1 | 501060000 | Providing and fixing in position G.I. vent with brass mosquito proof coupling and air filter including return bend, complete as required. The entire fitting shall be hot dip galvanised. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.2 | 501060000 | 50 asas dia | [8 empty] | No. | 6 | 1666 | 0 | 1666 | 83.3 | 0 | 1749.3 | 206 | 25.4616 | 0 | 231.4616 | 10495.8 | 1388.7696 | 11884.5696 | 10 | 6 | 999.6 | 0 | 999.6 | 49.98 | 0 | 1049.58 | 123.6 | 15.277 | 0 | 138.877 | 1188.457
9.3 | 501060000 | 80 mm dia | [8 empty] | No. | 0 | 2700 | 0 | 2700 | 135 | 0 | 2835 | 315 | 38.934 | 0 | 353.934 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.4 | 501060000 | 100 mm dia | [8 empty] | No. | 12 | 2940 | 0 | 2940 | 147 | 0 | 3087 | 360 | 44.496 | 0 | 404.496 | 37044 | 4853.952 | 41897.952 | 10 | 12 | 3528 | 0 | 3528 | 176.4 | 0 | 3704.4 | 432 | 53.3952 | 0 | 485.3952 | 4189.7952
10 | 501060000 | Providing and fixing M.S. structural work fabricated from structural steel sections M.S. rounds, angles, channels, tees, square bars, plates including cutting to size, drilling, welding fixing and welding to insert plates in RCC structural works, as directed by Architects. M.S. ladders and tank covers & frame etc. cutting and making good the wall and floor where ever required including two coats of synthetic enamel paint/epoxy paint over a coat of primer. | [8 empty] | Kg | 600 | 75 | 0 | 75 | 3.75 | 0 | 78.75 | 20 | 2.472 | 0 | 22.472 | 47250 | 13483.2 | 60733.2 | 10 | 600 | 4500 | 0 | 4500 | 225 | 0 | 4725 | 1200 | 148.32 | 0 | 1348.32 | 6073.32
11 | 501060000 | Providing and fixing 22 gauge GI tray (drip tray) of standard design with necessary fabrication, hanger and support under the horizontal suspended soil / waste header. Tray shall be installed in slop with drain connection at end. The installation shall be to the satisfaction / approval of Project Manager | [8 empty] | Sqm | 0 | 1500 | 0 | 1500 | 75 | 0 | 1575 | 53 | 6.5508 | 0 | 59.5508 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 501060000 | Providing and fixing truck fill point consisting of 100 mm dia water filling point having 100 mm dia brass plug (Truck fill point shall be housed in suitable lockable chamber) | [8 empty] | No. | 1 | 11760 | 0 | 11760 | 588 | 0 | 12348 | 515 | 63.654 | 0 | 578.654 | 12348 | 578.654 | 12926.654 | 10 | 1 | 1176 | 0 | 1176 | 58.8 | 0 | 1234.8 | 51.5 | 6.3654 | 0 | 57.8654 | 1292.6654
13 | 501060000 | Providing and fixing sump pump covers of G.I. Chequered plate 7 mm thick with openable handles on to M.S. Hot Dip Galvanized angle frame. | [8 empty] | Sq.m | 10 | 6321 | 0 | 6321 | 316.05 | 0 | 6637.05 | 360 | 44.496 | 0 | 404.496 | 66370.5 | 4044.96 | 70415.46 | 10 | 10 | 6321 | 0 | 6321 | 316.05 | 0 | 6637.05 | 360 | 44.496 | 0 | 404.496 | 7041.546
14 | 501060000 | Providing and fixing Mosquito proff S.S. netting & Aluminium frame with double leaf door for water tank side manholes with pad lock arrangement | [8 empty] | Sq.m | 5 | 1470 | 0 | 1470 | 73.5 | 0 | 1543.5 | 103 | 12.7308 | 0 | 115.7308 | 7717.5 | 578.654 | 8296.154 | 10 | 5 | 735 | 0 | 735 | 36.75 | 0 | 771.75 | 51.5 | 6.3654 | 0 | 57.8654 | 829.6154
15 | 501060000 | Making core cuts in RCC slab for drainage pipe in Guest room & public area as per qty. mention below.(Please refer structural drawing for exact slab thickness) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15.1 | 501060000 | 80 mm Dias | [8 empty] | Nos | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 1183 | 146.2188 | 0 | 1329.2188 | 0 | 33230.47 | 33230.47 | 10 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 2957.5 | 365.547 | 0 | 3323.047 | 3323.047
15.2 | 501060000 | 100 mm Dia. | [8 empty] | Nos. | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 1311 | 162.0396 | 0 | 1473.0396 | 0 | 331433.91 | 331433.91 | 10 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 29497.5 | 3645.891 | 0 | 33143.391 | 33143.391
15.3 | 501060000 | 150 mm Dia. | [8 empty] | Nos. | 425 | 0 | 0 | 0 | 0 | 0 | 0 | 1646 | 203.4456 | 0 | 1849.4456 | 0 | 786014.38 | 786014.38 | 10 | 425 | 0 | 0 | 0 | 0 | 0 | 0 | 69955 | 8646.438 | 0 | 78601.438 | 78601.438
G | 501050000 | WATER SUPPLY, DRAINAGE, PUMPS & EQUIPMENT: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 501050000 | Hydropneumatic System:Supply, Installation, Testing And Commissioning Of Compact Self Contained Skid Mounted Hydropneumatic System As Follows:In-Line, Multisage, centrifugal pumps with SS-304 casing and impeller and SS-316 shaft, CI base & head TEFC motor (with mechanical seal)(Vendor to submit performance curves and technical catalog of the proposed model for review & information)The pump shall be selected for performance at best efficiency point. However, the pump selection shall be suitable for performance with set point @ + 20% of the rated head. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.1 | 501050000 | Hydropneumatic systems: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.1.1 | 501050000 | Lower zone- Domestic water supplyNos. of Pumps : 3 (2 Working + 1 Stand by)Water Flow Rate : 3.5 LPS Each pumpHead : 60 M | [8 empty] | Set | 1 | 741760 | 0 | 741760 | 37088 | 0 | 778848 | 46305 | 5723.298 | 0 | 52028.298 | 778848 | 52028.298 | 830876.298 | 10 | 1 | 74176 | 0 | 74176 | 3708.8 | 0 | 77884.8 | 4630.5 | 572.3298 | 0 | 5202.8298 | 83087.6298
1.1.2 | 501050000 | Upper zone- Domestic water supplyNos. of Pumps : 3 (2 Working + 1 Standby)Water Flow Rate : 6.0 LPS Each pumpHead : 110 M | [8 empty] | Set | 1 | 1134770 | 0 | 1134770 | 56738.5 | 0 | 1191508.5 | 46305 | 5723.298 | 0 | 52028.298 | 1191508.5 | 52028.298 | 1243536.798 | 10 | 1 | 113477 | 0 | 113477 | 5673.85 | 0 | 119150.85 | 4630.5 | 572.3298 | 0 | 5202.8298 | 124353.6798
1.1.3 | 501050000 | Lower & Upper zone Flushing water supplyNos. of Pumps : 3 (2 Working +1 Standby)Water Flow Rate : 6 LPS Each pumpHead : 110M | [8 empty] | Set | 1 | 1134770 | 0 | 1134770 | 56738.5 | 0 | 1191508.5 | 46305 | 5723.298 | 0 | 52028.298 | 1191508.5 | 52028.298 | 1243536.798 | 10 | 1 | 113477 | 0 | 113477 | 5673.85 | 0 | 119150.85 | 4630.5 | 572.3298 | 0 | 5202.8298 | 124353.6798
2 | 501050000 | Submersiable Pumps: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.1 | 501050000 | Submersiable Centrifugal Non-clog Drainage Pumps | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.2 | 501050000 | Supply, installation, testing and commissioning of continuous duty submersible centrifugal non-clogging drainage pumps complete with 3 phase motor with all necessary protection and mechanical seal etc. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.3 | 501050000 | Vendor to submit proposed pump model with duty curve. The pump selection shall be on the middle of the curve or on LHS. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.3.1 | 501050000 | Flow rate : 2 LPS Each pumpHead : 10 Mts Solid Handling : 30 - 38 MMNos. of Pumps : 2 ( 1 working + 1 standby )Location : Plumbing plant room & HVAC Plant roomPurpose : Plant Room DrainageMOC : Stainless steel | [8 empty] | Sets | 2 | 86000 | 0 | 86000 | 4300 | 0 | 90300 | 10290 | 1271.844 | 0 | 11561.844 | 180600 | 23123.688 | 203723.688 | 10 | 2 | 17200 | 0 | 17200 | 860 | 0 | 18060 | 2058 | 254.3688 | 0 | 2312.3688 | 20372.3688
2.3.2 | 501050000 | Flow rate : 5 LPS Each pumpHead : 25 Mts Solid Handling : 30 - 38 MMNos. of Pumps : 2 ( 1 working + 1 standby )Location : Car parking areaPurpose : Car parking area drainageMOC : Stainless steel | [8 empty] | Set | 1 | 115022 | 0 | 115022 | 5751.1 | 0 | 120773.1 | 10290 | 1271.844 | 0 | 11561.844 | 120773.1 | 11561.844 | 132334.944 | 10 | 1 | 11502.2 | 0 | 11502.2 | 575.11 | 0 | 12077.31 | 1029 | 127.1844 | 0 | 1156.1844 | 13233.4944
2.3.3 | 501050000 | Flow rate : 2 LPSHead : 10 Mts Solid Handling : 30 - 38 MMNos. of Pumps : 2 ( 1 working + 1 standby )Location : In hot water plantroomPurpose : Boiler blow down dischargeMOC : CI body / impeller & shaft | [8 empty] | Set | 1 | 131752 | 0 | 131752 | 6587.6 | 0 | 138339.6 | 10290 | 1271.844 | 0 | 11561.844 | 138339.6 | 11561.844 | 149901.444 | 10 | 1 | 13175.2 | 0 | 13175.2 | 658.76 | 0 | 13833.96 | 1029 | 127.1844 | 0 | 1156.1844 | 14990.1444
4 | 501050000 | PIPING, VALVES & ACCESSORIES | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4.1 | 501050000 | Providing, fixing, jointing and testing in position the C.I. class LA pipe for (Sump Riser) confirming to IS:1536. Cut to required lengths including painting and all necessary fittings and specials such as bends, junctions, offsets, access pieces (plain or door) fixing at wall / ceiling level supported by galvanised steel clamps & hangers etc. Making proper connection to the satisfaction of the Project Manager and making good the same after pipe have been duly laid and testing complete. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4.1.1 | 501050000 | 80 mm dia (Ty-ton joint for pressure pumping) | [8 empty] | RM | 0 | 1502 | 0 | 1502 | 75.1 | 0 | 1577.1 | 336 | 41.5296 | 0 | 377.5296 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4.1.2 | 501050000 | 100 mm dia (Ty-ton joint for pressure pumping) | [8 empty] | RM | 0 | 1865 | 0 | 1865 | 93.25 | 0 | 1958.25 | 420 | 51.912 | 0 | 471.912 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 501050000 | Providing and fixing in position Class C M.S. Galvanised pipe work for all pump suction / discharge line with common header complete with all fittings like elbow, tee, reducer, flange, union etc. conforming to IS:1239 (Part 1) for pipes and IS : 1879 (Part 1 to 10) for fittings including fixing in wall / ceiling / floor level, supported by galvanized clamps, hangers, vertical pipe support etc. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.1 | 501050000 | 65 mm dias | [8 empty] | RM | 10 | 770 | 0 | 770 | 38.5 | 0 | 808.5 | 267 | 33.0012 | 0 | 300.0012 | 8085 | 3000.012 | 11085.012 | 10 | 10 | 770 | 0 | 770 | 38.5 | 0 | 808.5 | 267 | 33.0012 | 0 | 300.0012 | 1108.5012
5.2 | 501050000 | 80 mm dias | [8 empty] | RM | 10 | 930 | 0 | 930 | 46.5 | 0 | 976.5 | 329 | 40.6644 | 0 | 369.6644 | 9765 | 3696.644 | 13461.644 | 10 | 10 | 930 | 0 | 930 | 46.5 | 0 | 976.5 | 329 | 40.6644 | 0 | 369.6644 | 1346.1644
5.3 | 501050000 | 100 mm dia | [8 empty] | RM | 20 | 1400 | 0 | 1400 | 70 | 0 | 1470 | 412 | 50.9232 | 0 | 462.9232 | 29400 | 9258.464 | 38658.464 | 10 | 20 | 2800 | 0 | 2800 | 140 | 0 | 2940 | 824 | 101.8464 | 0 | 925.8464 | 3865.8464
5.4 | 501050000 | 150 mm dias | [8 empty] | RM | 20 | 1988 | 0 | 1988 | 99.4 | 0 | 2087.4 | 617 | 76.2612 | 0 | 693.2612 | 41748 | 13865.224 | 55613.224 | 10 | 20 | 3976 | 0 | 3976 | 198.8 | 0 | 4174.8 | 1234 | 152.5224 | 0 | 1386.5224 | 5561.3224
5.5 | 501050000 | 200 mm dias | [8 empty] | RM | 20 | 2058 | 0 | 2058 | 102.9 | 0 | 2160.9 | 627 | 77.4972 | 0 | 704.4972 | 43218 | 14089.944 | 57307.944 | 10 | 20 | 4116 | 0 | 4116 | 205.8 | 0 | 4321.8 | 1254 | 154.9944 | 0 | 1408.9944 | 5730.7944
6 | 501050000 | Providing & fixing M.S. (Heavy Class) header complete for submersiable pump discharge header comprising of flanges, unions, check nuts, Tee, Elbow etc. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6.1 | 501050000 | 80 mm dia | [8 empty] | RM | 0 | 780 | 0 | 780 | 39 | 0 | 819 | 336 | 41.5296 | 0 | 377.5296 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6.2 | 501050000 | 100 mm dia | [8 empty] | RM | 85 | 1112 | 0 | 1112 | 55.6 | 0 | 1167.6 | 412 | 50.9232 | 0 | 462.9232 | 99246 | 39348.472 | 138594.472 | 10 | 85 | 9452 | 0 | 9452 | 472.6 | 0 | 9924.6 | 3502 | 432.8472 | 0 | 3934.8472 | 13859.4472
7 | 501050000 | Providing and fixing C.I. Butterfly valve (Body : Grey Cast Iron, shaft : SS, Disc : SG Iron (nickel plated), Liner : HT - EPDM) of approved make with flange, washer, nuts & bolts and PN 10 pressure rating including rubber gasket & painting complete. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7.1 | 501050000 | 40 mm dia | [8 empty] | No. | 0 | 1720 | 0 | 1720 | 86 | 0 | 1806 | 210 | 25.956 | 0 | 235.956 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7.2 | 501050000 | 50 mm dia | [8 empty] | No. | 0 | 2800 | 0 | 2800 | 140 | 0 | 2940 | 263 | 32.5068 | 0 | 295.5068 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7.3 | 501050000 | 65 asas dia | [8 empty] | No. | 12 | 3047 | 0 | 3047 | 152.35 | 0 | 3199.35 | 334 | 41.2824 | 0 | 375.2824 | 38392.2 | 4503.3888 | 42895.5888 | 10 | 12 | 3656.4 | 0 | 3656.4 | 182.82 | 0 | 3839.22 | 400.8 | 49.5389 | 0 | 450.3389 | 4289.5589
7.4 | 501050000 | 80 asas dia | [8 empty] | No. | 12 | 3626 | 0 | 3626 | 181.3 | 0 | 3807.3 | 412 | 50.9232 | 0 | 462.9232 | 45687.6 | 5555.0784 | 51242.6784 | 10 | 12 | 4351.2 | 0 | 4351.2 | 217.56 | 0 | 4568.76 | 494.4 | 61.1078 | 0 | 555.5078 | 5124.2678
7.5 | 501050000 | 100 mm d ia | [8 empty] | No. | 2 | 4753 | 0 | 4753 | 237.65 | 0 | 4990.65 | 515 | 63.654 | 0 | 578.654 | 9981.3 | 1157.308 | 11138.608 | 10 | 2 | 950.6 | 0 | 950.6 | 47.53 | 0 | 998.13 | 103 | 12.7308 | 0 | 115.7308 | 1113.8608
7.6 | 501050000 | 150 mm dia | [8 empty] | No. | 5 | 7056 | 0 | 7056 | 352.8 | 0 | 7408.8 | 772 | 95.4192 | 0 | 867.4192 | 37044 | 4337.096 | 41381.096 | 10 | 5 | 3528 | 0 | 3528 | 176.4 | 0 | 3704.4 | 386 | 47.7096 | 0 | 433.7096 | 4138.1096
7.7 | 501050000 | 200 mm dia | [8 empty] | No. | 0 | 14000 | 0 | 14000 | 700 | 0 | 14700 | 1050 | 129.78 | 0 | 1179.78 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 501050000 | Providing & fixing C.I. wafer type check valve of PN 1.6 rating, including rubber gasket, flanges, union, nuts, bolts, washers & painting complete as required. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8.1 | 501050000 | 50 mm dia | [8 empty] | No. | 6 | 3136 | 0 | 3136 | 156.8 | 0 | 3292.8 | 257 | 31.7652 | 0 | 288.7652 | 19756.8 | 1732.5912 | 21489.3912 | 10 | 6 | 1881.6 | 0 | 1881.6 | 94.08 | 0 | 1975.68 | 154.2 | 19.0591 | 0 | 173.2591 | 2148.9391
8.2 | 501050000 | 65 mm dia | [8 empty] | No. | 6 | 3626 | 0 | 3626 | 181.3 | 0 | 3807.3 | 334 | 41.2824 | 0 | 375.2824 | 22843.8 | 2251.6944 | 25095.4944 | 10 | 6 | 2175.6 | 0 | 2175.6 | 108.78 | 0 | 2284.38 | 200.4 | 24.7694 | 0 | 225.1694 | 2509.5494
8.3 | 501050000 | 80 mm dia | [8 empty] | No. | 5 | 4331 | 0 | 4331 | 216.55 | 0 | 4547.55 | 412 | 50.9232 | 0 | 462.9232 | 22737.75 | 2314.616 | 25052.366 | 10 | 5 | 2165.5 | 0 | 2165.5 | 108.275 | 0 | 2273.775 | 206 | 25.4616 | 0 | 231.4616 | 2505.2366
8.4 | 501050000 | 100 mm dia | [8 empty] | No. | 0 | 6615 | 0 | 6615 | 330.75 | 0 | 6945.75 | 525 | 64.89 | 0 | 589.89 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 501050000 | Providing & fixing NRV (B-System with Ball) for Sewage Pump application. The NRV shall have synthetic resin ball (Self cleaning type) in CI casing & NBR seal (Make : Danfoss) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.1 | 501050000 | 100 mm dia | [8 empty] | Nos. | 0 | 8850 | 0 | 8850 | 442.5 | 0 | 9292.5 | 525 | 64.89 | 0 | 589.89 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 501050000 | Providing & Fixing dual flange CI Y Strainer (flanged) with stainless steel fine wire mesh perforated sheet basket with necessary flange / unions, nuts, bolts and wahsers complete as required. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10.1 | 501050000 | 65 mm dia | [8 empty] | No. | 0 | 3732 | 0 | 3732 | 186.6 | 0 | 3918.6 | 341 | 42.1476 | 0 | 383.1476 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10.2 | 501050000 | 80 mm dia | [8 empty] | No. | 0 | 4542 | 0 | 4542 | 227.1 | 0 | 4769.1 | 420 | 51.912 | 0 | 471.912 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10.3 | 501050000 | 100 mm dia | [8 empty] | No. | 0 | 6936 | 0 | 6936 | 346.8 | 0 | 7282.8 | 525 | 64.89 | 0 | 589.89 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10.4 | 501050000 | 150 mm dia | [8 empty] | No. | 2 | 12559 | 0 | 12559 | 627.95 | 0 | 13186.95 | 772 | 95.4192 | 0 | 867.4192 | 26373.9 | 1734.8384 | 28108.7384 | 10 | 2 | 2511.8 | 0 | 2511.8 | 125.59 | 0 | 2637.39 | 154.4 | 19.0838 | 0 | 173.4838 | 2810.8738
11 | 501050000 | Providing, testing and commissioning of 100 mm dia dial type pressure gauge with pressure scale of 0 to 15 Kg / sqm. Provision of isolation ball valve shall also be included in the cost. | [8 empty] | No. | 4 | 1764 | 0 | 1764 | 88.2 | 0 | 1852.2 | 155 | 19.158 | 0 | 174.158 | 7408.8 | 696.632 | 8105.432 | 10 | 4 | 705.6 | 0 | 705.6 | 35.28 | 0 | 740.88 | 62 | 7.6632 | 0 | 69.6632 | 810.5432
H | 502000000 | FIRE PROTECTION SYSTEM: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.1 | 502010000 | Supply, installation, testing and commissioning of electrically driven high pressure centrifugal fire hydrant / sprinkler pump, suitable for automatic operation consisting of the following: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
a. | 502010000 | Horizontal end suction / high pressure single stage, centrifugal pump, suitable for operation on 415 volts ± 6%, 3 phase, 50 HZ A.C supply. The installation shall be complete with flexible coupling and coupling guard as required. Fire pump shall have C.I. casing, CS diffusers, bronze impeller (hard finished and dynamically balanced) and S.S. (304) Shaft with mechanical seal, capable for delivering 47.5 LPS at outlet head of 120 mts to ensure a minimum pressure of 3.5 Kg/Sqcm at the farthest or topmost hydrant / sprinkler. The installation shall be complete with necessary pressure gauge with gun metal shut off cock on delivery side. (The pump should be tested for bench mark at factory and shall be gotten approved by the Local fire Authority).Pump shall be capable of furnishing not less than 150% of rated capacity at a head of not less than 65% of the rated head. The shut off head shall not exceed 120% of rated head. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
b. | 502010000 | Squirrel cage induction motor, TEFC type suitable for operation on 415 volts, 3 phase 50 HZ A.C supply, for the above pump with synchronous speed of 2900 RPM, conforming to IP 55 protection & class F insulation. The motor shall conform to IS 325-1978 (up to date) with flexible coupling and coupling guard, complete as required. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
c. | 502010000 | Common base plate for (a) and (b) from M.S. Channel for required size. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
d. | 502010000 | Suitable cement concrete foundation with cement concrete plaster (design and drawing to be provided by the Contractor while the foundation will be done by others) complete with anti-vibration arrangement of cushy foot mountings. | [8 empty] | Set | 2 | 447770 | 0 | 447770 | 22388.5 | 0 | 470158.5 | 25725 | 3179.61 | 0 | 28904.61 | 940317 | 57809.22 | 998126.22 | 10 | 2 | 89554 | 0 | 89554 | 4477.7 | 0 | 94031.7 | 5145 | 635.922 | 0 | 5780.922 | 99812.622
e. | 502010000 | Quote for UL -FM approved fire pumps as optional | [8 empty] | Nil | 0 | 3336000 | 0 | 3336000 | 166800 | 0 | 3502800 | 47250 | 5840.1 | 0 | 53090.1 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
f. | 502010000 | Pumps selection shall be on the Middle of the curve or on LHS. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.2 | 502010000 | Supply, installation, testing and commissioning of Diesel Engine driven fire pump suitable for automatic operation comprising of the following and conforming to BS 649/IS 10002 all amended upto date. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
a. | 502010000 | Horizontal, split casing, high pressure singel/ multistage centrifugal pump, The installation shall be complete with flexible coupling and coupling guard as required. Fire pump shall have C.I. casing, CS diffusers, bronze impeller (hard finished and dynamically balanced) and SS (304) shaft with mechanical seal, capable for delivering 47.5 LPS at outlet head of 120 mts to ensure a minimum pressure of 3.5 Kg/Sqcm at the farthest or topmost hydrant / sprinkler. The installation shall be complete with necessary pressure gauge with gun metal shut off cock on delivery side (The pump should be tested for bench mark at factory and shall be gotten approved by the Local fire Authority).Pump shall be capable of furnishing not less than 150% of rated capacity at a head of not less than 65% of the rated head. The shut off head shall not exceed 120% of rated head. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
b. | 502010000 | Heat exchanger cooled (secondary cooling) diesel engine of speed 1500 RPM suitable for the above pump with automatic starting mechanism and other accessories including fuel tank (fabricated from 3mm MS sheet, painted with two coats of synthetic enamel paint over a coat of primer) of capacity adequate to sustain pump operation for 8 hours continuous working. The tank shall be fitted with Magnetic oil level indicator, MH with cover, drain valve, air vent including structural supports (painted with approved shade), 2 Nos. x 12 volt battery with battery charger, heat exchanger with necessary piping connections & fittings, flexible coupling, coupling guard & exhaust pipe connection complete as required. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
c. | 502010000 | Common base plate for (a) and (b) from M.S. channel of required size. | [8 empty] | Set | 1 | 1025535 | 0 | 1025535 | 51276.75 | 0 | 1076811.75 | 36015 | 4451.454 | 0 | 40466.454 | 1076811.75 | 40466.454 | 1117278.204 | 10 | 1 | 102553.5 | 0 | 102553.5 | 5127.675 | 0 | 107681.175 | 3601.5 | 445.1454 | 0 | 4046.6454 | 111727.8204
d. | 502010000 | Suitable cement concrete foundation with plaster, (design and drawing to be provided by the Contractor while the foundation will be done by others) complete with antivibration arrangement of cushy foot mountings. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
e. | 502010000 | Quote for UL -FM approved fire pumps as optional | [8 empty] | Nil | 0 | 4346000 | 0 | 4346000 | 217300 | 0 | 4563300 | 63000 | 7786.8 | 0 | 70786.8 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
f. | 502010000 | Pumps selection shall be on the Middle of the curve or on LHS. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
g | 502010000 | Engine BHP tobe 30% higher than the pump shaft BHP. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
h | 502010000 | Engine shall be water cooled with prefitted circulation pump instead of radiators and the circulated water shall go to the Fire tank. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.3 | 502010000 | Supply, installation, testing and commissioning of jockey pump (pressurisation pump) comprising of the following: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
a. | 502010000 | Vertical Multistage centrifugal pump, suitable for operation on 415 volts ± 6%, 3 phase, 50 HZ A.C supply. The installation shall be complete with Flexible coupling and coupling guard, complete as required. Jockey pump shall be of stainless steel construction.The pump head and base shall be CI construction and impellers, diffusers, shaft sleeve, seal bush & pump shaft shall be in SS 304 material. The pump shall be provided with mechanical seal The system shall be complete with necessary pressure gauge with gun metal shut off cock on delivery side (The pump should meet the condition and shall be gotten approved by the Local fire Authority). | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
b. | 502010000 | Squirrel cage induction motor TEFC type for operation on 415 V, 3 phase 50 HZ AC supply for the above pump with a synchronous speed of 2900 R.P.M. with flexible coupling and coupling guard etc. as required. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
c. | 502010000 | Common base plate for (a) and (b) from M.S. channel as required size. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
d. | 502010000 | Suitable cement concrete foundation with plaster, (design and drawing to be provided by the Contractor while the foundation will be done by others) complete with Antivibration arrangement of cushy foot mounting. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
e. | 502010000 | Quote for UL -FM approved fire pumps as optional | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
f. | 502010000 | Pumps selection shall be on the Middle of the curve or on LHS.For pump defined above & of duty as follows : | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.3.1 | 502010000 | Hydrant SystemFlow : 180 LPMHead : 120 mts | [8 empty] | Set | 1 | 90357 | 0 | 90357 | 4517.85 | 0 | 94874.85 | 15435 | 1907.766 | 0 | 17342.766 | 94874.85 | 17342.766 | 112217.616 | 10 | 1 | 9035.7 | 0 | 9035.7 | 451.785 | 0 | 9487.485 | 1543.5 | 190.7766 | 0 | 1734.2766 | 11221.7616
1.3.2 | 502010000 | Sprinkler SystemFlow : 180 LPMHead : 120 mts | [8 empty] | Set | 1 | 90357 | 0 | 90357 | 4517.85 | 0 | 94874.85 | 15435 | 1907.766 | 0 | 17342.766 | 94874.85 | 17342.766 | 112217.616 | 10 | 1 | 9035.7 | 0 | 9035.7 | 451.785 | 0 | 9487.485 | 1543.5 | 190.7766 | 0 | 1734.2766 | 11221.7616
1.4 | 502010000 | Supply, installation, testing and commissioning of terrace fire pump comprising of the following: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
a. | 502010000 | Horizontal mono-block centrifugal pump, suitable for operation on 415 volts ± 6%, 3 phase, 50 HZ A.C supply.The pump casing shall be CI, shaft shall be CS & impeller / shaft sleeve / casing wearing ring shall be bronze. The system shall be complete with necessary pressure gauge with gun metal shut off cock on delivery side. (The pump should meet the condition and shall be gotten approved by the Local fire Authority). | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
b. | 502010000 | Squirrel cage induction motor TEFC type for operation on 415 V, 3 phase 50 HZ AC supply for the above pump with speed of 2900 R.P.M. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
c. | 502010000 | Suitable cement concrete foundation with plaster, (design and drawing to be provided by the Contractor while the foundation will be done by others) complete with Antivibration arrangement of cushy foot mounting. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
d. | 502010000 | For pump defined above & of duty as follows : | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.4.1 | 502010000 | Flow : 900 LPM | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.4.2 | 502010000 | Head :35 mts | [8 empty] | Set | 1 | 44025 | 0 | 44025 | 2201.25 | 0 | 46226.25 | 10290 | 1271.844 | 0 | 11561.844 | 46226.25 | 11561.844 | 57788.094 | 10 | 1 | 4402.5 | 0 | 4402.5 | 220.125 | 0 | 4622.625 | 1029 | 127.1844 | 0 | 1156.1844 | 5778.8094
1.5 | 502010000 | Providing & fixing MS Class C diesel engine exhaust pipe (including all fittings, clamps, steel support) of suitable dia for the engine. The pipe shall be provided with 12 mm thick supercera ceramic fibre rope. | [8 empty] | RM | 20 | 1470 | 0 | 1470 | 73.5 | 0 | 1543.5 | 494 | 61.0584 | 0 | 555.0584 | 30870 | 11101.168 | 41971.168 | 10 | 20 | 2940 | 0 | 2940 | 147 | 0 | 3087 | 988 | 122.1168 | 0 | 1110.1168 | 4197.1168
1.6 | 502010000 | Providing, fixing, testing and commissioning of precharged air vessel (size 450 mm dia & 2000 mm height) for pressurization of hydrant / sprinkler system complete with adequate pressure switches (as per design / requirement) with valves to operate as per operating sequences including 25 mm dia drain valve, air release valve with stop cock on the top, minimum 50 mm dia inlet with isolating valve duly painted from inside and outside with two coats of synthetic enamel paint over a coat of primer complete as required. (Vessel should be suitable for rated working pressure. The air vessel shall be without diaphragm). | [8 empty] | Set | 2 | 40180 | 0 | 40180 | 2009 | 0 | 42189 | 2058 | 254.3688 | 0 | 2312.3688 | 84378 | 4624.7376 | 89002.7376 | 10 | 2 | 8036 | 0 | 8036 | 401.8 | 0 | 8437.8 | 411.6 | 50.8738 | 0 | 462.4738 | 8900.2738
1.7 | 502010000 | Providing, fixing, testing & commissioning of MS air cushion tank on top of each riser fabricated from 6mm thick MS plate, 200 mm in diameter and 1.2 m in height with dished ends fabricated from 6 mm thick MS plate with Air release valve & stop cock, flanged inlet connection with all accessories as required and conforming to IS 4736-1968. (The cushion tank should be suitable for rated working pressure. | [8 empty] | Set | 3 | 15484 | 0 | 15484 | 774.2 | 0 | 16258.2 | 1286 | 158.9496 | 0 | 1444.9496 | 48774.6 | 4334.8488 | 53109.4488 | 10 | 3 | 4645.2 | 0 | 4645.2 | 232.26 | 0 | 4877.46 | 385.8 | 47.6849 | 0 | 433.4849 | 5310.9449
1.8 | 502010000 | Providing & fixing dial type (100 mm) pressure gauge with isolation ball valve suitable for working pressure of 250 PSI. Cost shall be inclusive of providing any short pieces, nipples, elbows etc as required. | [8 empty] | Nos | 3 | 1960 | 0 | 1960 | 98 | 0 | 2058 | 257 | 31.7652 | 0 | 288.7652 | 6174 | 866.2956 | 7040.2956 | 10 | 3 | 588 | 0 | 588 | 29.4 | 0 | 617.4 | 77.1 | 9.5296 | 0 | 86.6296 | 704.0296
1.9 | 502010000 | Supply, installation, testing and commissioning of sight tube (of 3.5 to 4 m length) with isolation valve at top / bottom, demarcation on tube for making the installation of level indication on the RCC water tank complete. | [8 empty] | Nos | 2 | 9310 | 0 | 9310 | 465.5 | 0 | 9775.5 | 515 | 63.654 | 0 | 578.654 | 19551 | 1157.308 | 20708.308 | 10 | 2 | 1862 | 0 | 1862 | 93.1 | 0 | 1955.1 | 103 | 12.7308 | 0 | 115.7308 | 2070.8308
Note: i. | 502010000 | Contractor shall include in his rates for providing level controllers, pressure switches, wiring, cabling from level controller / pressure switch to panel etc. complete as required to operate the system automatic/manual. Pump shall be protected against running dry. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 502020000 | Hydrants, Piping & Accessories: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.1 | 502020000 | Providing, laying, jointing, testing and commissioning of following sizes of pipes conforming to IS-1239 with all accessories like all fittings (standard MS fitting with welded joint shall be used on the pipes) including tees, elbows, reducers, union, flanges, rubber gaskets, GI nuts bolts, washer including supporting/fixing the pipe on floor / wall /ceiling with clamps, hangers (using anchor fastners) as per specification. UPVC pipe sleeve of suitable higher size shall be provided wherever the pipes are crossing the walls/floors and sealing the sleeves with glass wool in between & fire sealent compound at either end all as per Project Managers / Consultants requirements including cutting holes and chases in brick, R.C.C work and making good the same to original conditions complete in all respects. All hangers, clamps, brackets etc. shall be of galvanized iron unless specified otherwire and then supply of the same shall also be included for rates under this head.. Welding of any kind on the galvanized support / hanger shall not be permitted. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.1.1 | 502020000 | For wet riser System - M.S.C Heavy class pipe | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.1.2 | 502020000 | 150 mm dia | [8 empty] | RM | 770 | 1675 | 0 | 1675 | 83.75 | 0 | 1758.75 | 494 | 61.0584 | 0 | 555.0584 | 1354237.5 | 427394.968 | 1781632.468 | 10 | 770 | 128975 | 0 | 128975 | 6448.75 | 0 | 135423.75 | 38038 | 4701.4968 | 0 | 42739.4968 | 178163.2468
2.1.3 | 502020000 | 250 mm diat | [8 empty] | RM | 5 | 3332 | 0 | 3332 | 166.6 | 0 | 3498.6 | 823 | 101.7228 | 0 | 924.7228 | 17493 | 4623.614 | 22116.614 | 10 | 5 | 1666 | 0 | 1666 | 83.3 | 0 | 1749.3 | 411.5 | 50.8614 | 0 | 462.3614 | 2211.6614
2.1.4 | 502020000 | 300 mm diau | [8 empty] | RM | 10 | 3332 | 0 | 3332 | 166.6 | 0 | 3498.6 | 875 | 108.15 | 0 | 983.15 | 34986 | 9831.5 | 44817.5 | 10 | 10 | 3332 | 0 | 3332 | 166.6 | 0 | 3498.6 | 875 | 108.15 | 0 | 983.15 | 4481.75
2.2 | 502020000 | Providing two coats of synthetic enamel paint of approved shade over a coat of primer. Prior to application of primer the surface should be cleaned for any dirt, rusts, rough substance etc. Including painting of legends both direction arrow as per the approval of the Project Manager | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.2.1 | 502020000 | 80 mm dia | [8 empty] | RM | 25 | 29 | 0 | 29 | 1.45 | 0 | 30.45 | 15 | 1.854 | 0 | 16.854 | 761.25 | 421.35 | 1182.6 | 10 | 25 | 72.5 | 0 | 72.5 | 3.625 | 0 | 76.125 | 37.5 | 4.635 | 0 | 42.135 | 118.26
2.2.2 | 502020000 | 100 mm diai | [8 empty] | RM | 50 | 39 | 0 | 39 | 1.95 | 0 | 40.95 | 20 | 2.472 | 0 | 22.472 | 2047.5 | 1123.6 | 3171.1 | 10 | 50 | 195 | 0 | 195 | 9.75 | 0 | 204.75 | 100 | 12.36 | 0 | 112.36 | 317.11
2.2.3 | 502020000 | 150 mm diao | [8 empty] | RM | 825 | 58 | 0 | 58 | 2.9 | 0 | 60.9 | 31 | 3.8316 | 0 | 34.8316 | 50242.5 | 28736.07 | 78978.57 | 10 | 825 | 4785 | 0 | 4785 | 239.25 | 0 | 5024.25 | 2557.5 | 316.107 | 0 | 2873.607 | 7897.857
2.2.4 | 502020000 | 250 mm diap | [8 empty] | RM | 5 | 98 | 0 | 98 | 4.9 | 0 | 102.9 | 51 | 6.3036 | 0 | 57.3036 | 514.5 | 286.518 | 801.018 | 10 | 5 | 49 | 0 | 49 | 2.45 | 0 | 51.45 | 25.5 | 3.1518 | 0 | 28.6518 | 80.1018
2.2.5 | 502020000 | 300 mm dial | [8 empty] | RM | 10 | 93 | 0 | 93 | 4.65 | 0 | 97.65 | 61 | 7.5396 | 0 | 68.5396 | 976.5 | 685.396 | 1661.896 | 10 | 10 | 93 | 0 | 93 | 4.65 | 0 | 97.65 | 61 | 7.5396 | 0 | 68.5396 | 166.1896
2.3 | 502020000 | Providing, laying, jointing and testing in trenches the following sizes of MS class C (heavy class) pipes conforming to IS:1239 with accessories like fittings including tees, elbows, reducers, flanges, rubber gaskets, G.I. nuts, bolts and washers including excavation in all kind of soil, refilling, ramming, shoring, removing the excavated surplus material, providing adequate support to the pipe and making good the same complete as required. Rate shall include for dewatering necessary to execute the work. The pipe shall not be less than 1.0 m below ground level at any point. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.3.1 | 502020000 | 80 mm diak | [8 empty] | RM | 25 | 839 | 0 | 839 | 41.95 | 0 | 880.95 | 277 | 34.2372 | 0 | 311.2372 | 22023.75 | 7780.93 | 29804.68 | 10 | 25 | 2097.5 | 0 | 2097.5 | 104.875 | 0 | 2202.375 | 692.5 | 85.593 | 0 | 778.093 | 2980.468
2.3.2 | 502020000 | 100 mm dim | [8 empty] | RM | 30 | 1217 | 0 | 1217 | 60.85 | 0 | 1277.85 | 370 | 45.732 | 0 | 415.732 | 38335.5 | 12471.96 | 50807.46 | 10 | 30 | 3651 | 0 | 3651 | 182.55 | 0 | 3833.55 | 1110 | 137.196 | 0 | 1247.196 | 5080.746
2.3.3 | 502020000 | 150 mm a | [8 empty] | RM | 350 | 1795 | 0 | 1795 | 89.75 | 0 | 1884.75 | 556 | 68.7216 | 0 | 624.7216 | 659662.5 | 218652.56 | 878315.06 | 10 | 350 | 62825 | 0 | 62825 | 3141.25 | 0 | 65966.25 | 19460 | 2405.256 | 0 | 21865.256 | 87831.506
2.4 | 502020000 | Providing protection to embedded M.S. pipes and fittings by applying protective primer (@ 100 gm/sqm) thereafter wrapping 4 mm thick protection coating by thermo fusion process. Overlap shall be maintained at 15 mm. The application process shall be strictly according to manufacturers specification. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.4.1 | 502020000 | 80 mm diaam | [8 empty] | RM | 15 | 106 | 0 | 106 | 5.3 | 0 | 111.3 | 30 | 3.708 | 0 | 33.708 | 1669.5 | 505.62 | 2175.12 | 10 | 15 | 159 | 0 | 159 | 7.95 | 0 | 166.95 | 45 | 5.562 | 0 | 50.562 | 217.512
2.4.2 | 502020000 | 100mm | [8 empty] | RM | 30 | 14 | 0 | 14 | 0.7 | 0 | 14.7 | 41 | 5.0676 | 0 | 46.0676 | 441 | 1382.028 | 1823.028 | 10 | 30 | 42 | 0 | 42 | 2.1 | 0 | 44.1 | 123 | 15.2028 | 0 | 138.2028 | 182.3028
2.4.3 | 502020000 | 150mm | [8 empty] | RM | 350 | 211 | 0 | 211 | 10.55 | 0 | 221.55 | 61 | 7.5396 | 0 | 68.5396 | 77542.5 | 23988.86 | 101531.36 | 10 | 350 | 7385 | 0 | 7385 | 369.25 | 0 | 7754.25 | 2135 | 263.886 | 0 | 2398.886 | 10153.136
2.5 | 502020000 | Providing & fixing of butterfly valve (PN 16) with flanges, nut bolts, gaskets and necessary pad locking arrangement complete required. | [8 empty] | Nil | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.5.1 | 502020000 | 65 mm dia m | [8 empty] | No. | 3 | 3656 | 0 | 3656 | 182.8 | 0 | 3838.8 | 334 | 41.2824 | 0 | 375.2824 | 11516.4 | 1125.8472 | 12642.2472 | 10 | 3 | 1096.8 | 0 | 1096.8 | 54.84 | 0 | 1151.64 | 100.2 | 12.3847 | 0 | 112.5847 | 1264.2247
2.5.2 | 502020000 | 80 mm dia m | [8 empty] | No. | 3 | 4351 | 0 | 4351 | 217.55 | 0 | 4568.55 | 412 | 50.9232 | 0 | 462.9232 | 13705.65 | 1388.7696 | 15094.4196 | 10 | 3 | 1305.3 | 0 | 1305.3 | 65.265 | 0 | 1370.565 | 123.6 | 15.277 | 0 | 138.877 | 1509.442
2.5.3 | 502020000 | 100 mm dia m | [8 empty] | No. | 5 | 5704 | 0 | 5704 | 285.2 | 0 | 5989.2 | 515 | 63.654 | 0 | 578.654 | 29946 | 2893.27 | 32839.27 | 10 | 5 | 2852 | 0 | 2852 | 142.6 | 0 | 2994.6 | 257.5 | 31.827 | 0 | 289.327 | 3283.927
2.5.4 | 502020000 | 150 mm dia m | [8 empty] | No. | 15 | 8467 | 0 | 8467 | 423.35 | 0 | 8890.35 | 772 | 95.4192 | 0 | 867.4192 | 133355.25 | 13011.288 | 146366.538 | 10 | 15 | 12700.5 | 0 | 12700.5 | 635.025 | 0 | 13335.525 | 1158 | 143.1288 | 0 | 1301.1288 | 14636.6538
2.5.5 | 502020000 | 200 mm dia | [8 empty] | No. | 4 | 16464 | 0 | 16464 | 823.2 | 0 | 17287.2 | 900 | 111.24 | 0 | 1011.24 | 69148.8 | 4044.96 | 73193.76 | 10 | 4 | 6585.6 | 0 | 6585.6 | 329.28 | 0 | 6914.88 | 360 | 44.496 | 0 | 404.496 | 7319.376
2.5.6 | 502020000 | 250 mm dia m | [8 empty] | No. | 2 | 26460 | 0 | 26460 | 1323 | 0 | 27783 | 1029 | 127.1844 | 0 | 1156.1844 | 55566 | 2312.3688 | 57878.3688 | 10 | 2 | 5292 | 0 | 5292 | 264.6 | 0 | 5556.6 | 205.8 | 25.4369 | 0 | 231.2369 | 5787.8369
2.6 | 502020000 | Providing and fixing tamper switch on butterfly valve / sluice valve / isolation valve for remote mointing of the valve open / close position. The tamper switch shall be provided with potential free contact with 2 nos. NONC. The valve shall also be provided with manual lock & chain arrangement. | [8 empty] | Set | 0 | 5000 | 0 | 5000 | 250 | 0 | 5250 | 263 | 32.5068 | 0 | 295.5068 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.7 | 502020000 | Providing & fixing C.I. wafer type check valve of rating PN 16 rating including rubber gasket, flanges, union, nuts, bolts, washers & painting complete as required. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.7.1 | 502020000 | 65mm | [8 empty] | No | 2 | 3626 | 0 | 3626 | 181.3 | 0 | 3807.3 | 334 | 41.2824 | 0 | 375.2824 | 7614.6 | 750.5648 | 8365.1648 | 10 | 2 | 725.2 | 0 | 725.2 | 36.26 | 0 | 761.46 | 66.8 | 8.2565 | 0 | 75.0565 | 836.5165
2.7.2 | 502020000 | 80 mm dia | [8 empty] | No. | 0 | 4420 | 0 | 4420 | 221 | 0 | 4641 | 420 | 51.912 | 0 | 471.912 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.7.3 | 502020000 | 100 mm | [8 empty] | No. | 1 | 5635 | 0 | 5635 | 281.75 | 0 | 5916.75 | 515 | 63.654 | 0 | 578.654 | 5916.75 | 578.654 | 6495.404 | 10 | 1 | 563.5 | 0 | 563.5 | 28.175 | 0 | 591.675 | 51.5 | 6.3654 | 0 | 57.8654 | 649.5404
2.7.4 | 502020000 | 150mm dia m | [8 empty] | No. | 3 | 7722 | 0 | 7722 | 386.1 | 0 | 8108.1 | 618 | 76.3848 | 0 | 694.3848 | 24324.3 | 2083.1544 | 26407.4544 | 10 | 3 | 2316.6 | 0 | 2316.6 | 115.83 | 0 | 2432.43 | 185.4 | 22.9154 | 0 | 208.3154 | 2640.7454
2.7.5 | 502020000 | 200 mmd | [8 empty] | No. | 1 | 14210 | 0 | 14210 | 710.5 | 0 | 14920.5 | 823 | 101.7228 | 0 | 924.7228 | 14920.5 | 924.7228 | 15845.2228 | 10 | 1 | 1421 | 0 | 1421 | 71.05 | 0 | 1492.05 | 82.3 | 10.1723 | 0 | 92.4723 | 1584.5223
2.8 | 502020000 | Providing, fixing and commissioning of spring loaded relief valve suitable for pressure of 15 Kg / sq.cm including flanges, nuts, bolts, washers etc. complete as required. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.8.1 | 502020000 | 80 mmd | [8 empty] | No. | 2 | 16587 | 0 | 16587 | 829.35 | 0 | 17416.35 | 515 | 63.654 | 0 | 578.654 | 34832.7 | 1157.308 | 35990.008 | 10 | 2 | 3317.4 | 0 | 3317.4 | 165.87 | 0 | 3483.27 | 103 | 12.7308 | 0 | 115.7308 | 3599.0008
2.9 | 502020000 | Providing & fixing heavy duty double flanged flexicon rubber expansion joint (suitable for system test pressure) of standard length as per manufacturers specs including rubber gaskets, flanges, nuts, bolts and washers complete as required. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.9.1 | 502020000 | 65 mmd | [8 empty] | No. | 2 | 3733 | 0 | 3733 | 186.65 | 0 | 3919.65 | 257 | 31.7652 | 0 | 288.7652 | 7839.3 | 577.5304 | 8416.8304 | 10 | 2 | 746.6 | 0 | 746.6 | 37.33 | 0 | 783.93 | 51.4 | 6.353 | 0 | 57.753 | 841.683
2.9.2 | 502020000 | 80 mm di\ | [8 empty] | No. | 2 | 4395 | 0 | 4395 | 219.75 | 0 | 4614.75 | 309 | 38.1924 | 0 | 347.1924 | 9229.5 | 694.3848 | 9923.8848 | 10 | 2 | 879 | 0 | 879 | 43.95 | 0 | 922.95 | 61.8 | 7.6385 | 0 | 69.4385 | 992.3885
2.9.3 | 502020000 | 100 m,m | [8 empty] | No. | 3 | 5576 | 0 | 5576 | 278.8 | 0 | 5854.8 | 412 | 50.9232 | 0 | 462.9232 | 17564.4 | 1388.7696 | 18953.1696 | 10 | 3 | 1672.8 | 0 | 1672.8 | 83.64 | 0 | 1756.44 | 123.6 | 15.277 | 0 | 138.877 | 1895.317
2.9.4 | 502020000 | 150 mm | [8 empty] | No. | 3 | 6517 | 0 | 6517 | 325.85 | 0 | 6842.85 | 618 | 76.3848 | 0 | 694.3848 | 20528.55 | 2083.1544 | 22611.7044 | 10 | 3 | 1955.1 | 0 | 1955.1 | 97.755 | 0 | 2052.855 | 185.4 | 22.9154 | 0 | 208.3154 | 2261.1704
2.9.5 | 502020000 | 200 mm diam | [8 empty] | No. | 3 | 7315 | 0 | 7315 | 365.75 | 0 | 7680.75 | 823 | 101.7228 | 0 | 924.7228 | 23042.25 | 2774.1684 | 25816.4184 | 10 | 3 | 2194.5 | 0 | 2194.5 | 109.725 | 0 | 2304.225 | 246.9 | 30.5168 | 0 | 277.4168 | 2581.6418
2.1 | 502020000 | Providing and fixing C.I.Y strainer with bronze perforated sheet basket including rubber gasket, flanges, nuts, bolts and washers, complete as required. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.10.1 | 502020000 | 65 mm diam | [8 empty] | No. | 2 | 3439 | 0 | 3439 | 171.95 | 0 | 3610.95 | 257 | 31.7652 | 0 | 288.7652 | 7221.9 | 577.5304 | 7799.4304 | 10 | 2 | 687.8 | 0 | 687.8 | 34.39 | 0 | 722.19 | 51.4 | 6.353 | 0 | 57.753 | 779.943
2.10.2 | 502020000 | 100 mm diam | [8 empty] | No. | 1 | 6428 | 0 | 6428 | 321.4 | 0 | 6749.4 | 412 | 50.9232 | 0 | 462.9232 | 6749.4 | 462.9232 | 7212.3232 | 10 | 1 | 642.8 | 0 | 642.8 | 32.14 | 0 | 674.94 | 41.2 | 5.0923 | 0 | 46.2923 | 721.2323
2.10.3 | 502020000 | 150 mm diaa | [8 empty] | No. | 1 | 11799 | 0 | 11799 | 589.95 | 0 | 12388.95 | 618 | 76.3848 | 0 | 694.3848 | 12388.95 | 694.3848 | 13083.3348 | 10 | 1 | 1179.9 | 0 | 1179.9 | 58.995 | 0 | 1238.895 | 61.8 | 7.6385 | 0 | 69.4385 | 1308.3335
2.10.4 | 502020000 | 200 mm diaa | [8 empty] | No. | 3 | 27910 | 0 | 27910 | 1395.5 | 0 | 29305.5 | 823 | 101.7228 | 0 | 924.7228 | 87916.5 | 2774.1684 | 90690.6684 | 10 | 3 | 8373 | 0 | 8373 | 418.65 | 0 | 8791.65 | 246.9 | 30.5168 | 0 | 277.4168 | 9069.0668
2.11 | 502020000 | Providing and Fixing non rising sprindle type sluice valve PN 16 rating of following dia complete with flanges, nuts, bolts etc. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.11.1 | 502020000 | 150 mmd | [8 empty] | Nos. | 3 | 19560 | 0 | 19560 | 978 | 0 | 20538 | 618 | 76.3848 | 0 | 694.3848 | 61614 | 2083.1544 | 63697.1544 | 10 | 3 | 5868 | 0 | 5868 | 293.4 | 0 | 6161.4 | 185.4 | 22.9154 | 0 | 208.3154 | 6369.7154
2.11.2 | 502020000 | 250 mm dia | [8 empty] | Nos. | 0 | 69800 | 0 | 69800 | 3490 | 0 | 73290 | 1050 | 129.78 | 0 | 1179.78 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.12 | 502020000 | Providing & fixing gun metal fire hydrant double landing valve with 100 mm N.B. flanged inlet, brass spindle controlled 63 mm dia female instantaneous outlet type. G.M. coupling, blank cap, chain, twist release type lug & all accessories Conforming to IS:5290. Including fixing with anchor fastner and flanged tapping from wet riser and providing pressure gauge with gun metal ball valve complete as required. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.12.1 | 502020000 | Double head landing valve | [8 empty] | Nos. | 50 | 16500 | 0 | 16500 | 825 | 0 | 17325 | 412 | 50.9232 | 0 | 462.9232 | 866250 | 23146.16 | 889396.16 | 10 | 50 | 82500 | 0 | 82500 | 4125 | 0 | 86625 | 2060 | 254.616 | 0 | 2314.616 | 88939.616
2.12.2 | 502020000 | Single head landing valve | [8 empty] | Nos. | 9 | 7920 | 0 | 7920 | 396 | 0 | 8316 | 309 | 38.1924 | 0 | 347.1924 | 74844 | 3124.7316 | 77968.7316 | 10 | 9 | 7128 | 0 | 7128 | 356.4 | 0 | 7484.4 | 278.1 | 34.3732 | 0 | 312.4732 | 7796.8732
2.13 | 502020000 | Providing & fixing gun metal controlled pressure hydrant valve (Class F Hose pressure regulator) with 2 1/2 " instantaneous female coupling to BS: 336. Inlet pressure range 4.8 to 20.7 bar; outlet pressure range 4.1 - 8.3 bar. The pressure regulator shall incorporate spring loaded balanced PRV combined with a hydrant slop valve. Cost shall be inclusive of fixing with anchor fastner and flanged tapping from wet riser and providing pressure gauge with gun metal ball valve complete as required. | [8 empty] | Nos. | 0 | 20300 | 0 | 20300 | 1015 | 0 | 21315 | 788 | 97.3968 | 0 | 885.3968 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.14 | 502020000 | Providing & fixing swinging type First Aid hose reel in red colour drum with 36 mts long and 20 mm dia heavy duty rubber water hose, 20 mm dia gate valve stop cock, (IS:778, class - II) terminating with G.M. coupling & nozzle of 6mm outlet with shut off valve confirming to IS 8090 - 1976 complete with MS socket for tap-off, drum and brackets (including painting) for fixing on wall with anchor fastner, bolts & nuts conforming to IS:884-1985 (Reaffirmed 2000) complete as required. | [8 empty] | No. | 50 | 7815 | 0 | 7815 | 390.75 | 0 | 8205.75 | 515 | 63.654 | 0 | 578.654 | 410287.5 | 28932.7 | 439220.2 | 10 | 50 | 39075 | 0 | 39075 | 1953.75 | 0 | 41028.75 | 2575 | 318.27 | 0 | 2893.27 | 43922.02
2.15 | 502020000 | Providing & fixing non-percolating rubber reinforced lined fire hose pipe (as per IS : 636) type-B of 63 mm dia and length as described below. The hose shall be rated for brust pressure of 35.7 Kg/sqcm. Hose shall be complete with ISI marked brass male & female coupling (IS:903) bound & rivetted to hose pipe with copper rivets & 1.5 mm copper wire (Location : Internal fire hydrant) (with S.S. Coupling.) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.15.1 | 502020000 | 15 m length | [8 empty] | Nos. | 100 | 4700 | 0 | 4700 | 235 | 0 | 4935 | 128 | 15.8208 | 0 | 143.8208 | 493500 | 14382.08 | 507882.08 | 10 | 100 | 47000 | 0 | 47000 | 2350 | 0 | 49350 | 1280 | 158.208 | 0 | 1438.208 | 50788.208
2.16 | 502020000 | Providing & fixing controlled percolation fire hose pipe (as per IS:8423) of 63 mm dia and 15 meter length rated for brust pressure of 35.7 Kg/sqcm. The hose shall be tested for flame resistance test in accordance to IS:8423. Hose shall be complete with ISI marked brass male & female coupling (IS:903) bound & riveted to hose pipe with copper rivets & 1.5 mm copper wire (Location : External fire hydrant) ( with S.S. couplings) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.16.1 | 502020000 | 15 m lengt | [8 empty] | Nos. | 18 | 5310 | 0 | 5310 | 265.5 | 0 | 5575.5 | 154 | 19.0344 | 0 | 173.0344 | 100359 | 3114.6192 | 103473.6192 | 10 | 18 | 9558 | 0 | 9558 | 477.9 | 0 | 10035.9 | 277.2 | 34.2619 | 0 | 311.4619 | 10347.3619
2.17 | 502020000 | Providing and Fixing 63 mm dia instantaneous pattern branch short Stainless Steel pipe, 20 mm dia nozzle conforming to IS 903, suitable for inter connection to hose pipe coupling complete as required. | [8 empty] | Nos. | 109 | 2468 | 0 | 2468 | 123.4 | 0 | 2591.4 | 103 | 12.7308 | 0 | 115.7308 | 282462.6 | 12614.6572 | 295077.2572 | 10 | 109 | 26901.2 | 0 | 26901.2 | 1345.06 | 0 | 28246.26 | 1122.7 | 138.7657 | 0 | 1261.4657 | 29507.7257
2.18 | 502020000 | Providing and fixing standard firemans axe with heavy rubber handle. | [8 empty] | Nos. | 30 | 1142 | 0 | 1142 | 57.1 | 0 | 1199.1 | 103 | 12.7308 | 0 | 115.7308 | 35973 | 3471.924 | 39444.924 | 10 | 30 | 3426 | 0 | 3426 | 171.3 | 0 | 3597.3 | 309 | 38.1924 | 0 | 347.1924 | 3944.4924
2.19 | 502020000 | Providing and fixing weather proof lockable cabinet of size not less than 0.9 x 0.6 x 0.45 mtr made out of SS304 sheet of 16 gauge thickness having central opening and 4 mm thick glazed glass doors (Two nos.) suitably marked on the outside with the letters "FIRE HOSE" including necessary locking arrangement and shall be painted with one coat of primer and two coats of synthetic enamel paint of approved shade.The cabinet shall be suitable to accommodate 2 nos. or 4 nos 15 mtr long Hose pipe & 2 Nos branch pipe nozzle. It shall be mounted on raised Brick platform complete as required.(Cost shall be inclusive of providing break glass box containing key for the cabinet along with hammer). | [8 empty] | Nos. | 9 | 4474 | 0 | 4474 | 223.7 | 0 | 4697.7 | 360 | 44.496 | 0 | 404.496 | 42279.3 | 3640.464 | 45919.764 | 10 | 9 | 4026.6 | 0 | 4026.6 | 201.33 | 0 | 4227.93 | 324 | 40.0464 | 0 | 364.0464 | 4591.9764
2.2 | 502020000 | Providing & fixing lockable indoor type fire hose cabinet frames fabricated from 40 x 40 x 5 angle iron sections and 16 gauge MS sheet with full front glass door and locking arrangement, suitable to accommodate landing valves, 2 nos. 15 m long hoses, first-aid hose reel and branch pipe nozzle & fire mans axe. The cabinet frame shall be painted with one coat of primer and two or more coats of synthetic enamel paint of approved make and shade of as required (Approx 2.1 m (high) x 0.9 m (wide) x 0.6 m (deep) ). The item shall be complete of MS housing with front door.(Cost shall be inclusive of providing break glass box containing key for the cabinet along with hammer). | [8 empty] | Nos. | 0 | 11400 | 0 | 11400 | 570 | 0 | 11970 | 1050 | 129.78 | 0 | 1179.78 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.21 | 502020000 | Providing & fixing gun-metal fire brigade inlet connection (suction collecting head) consisting of 4 Nos. 63 mm dia instantaneous type male couplings with built-in check valves, 1 No. 150 mm dia sluice valve, and 150 mm dia flanged outlet complete with bolts, nuts and rubber insertions as required and as per IS:904-1963. | [8 empty] | No. | 1 | 28050 | 0 | 28050 | 1402.5 | 0 | 29452.5 | 2058 | 254.3688 | 0 | 2312.3688 | 29452.5 | 2312.3688 | 31764.8688 | 10 | 1 | 2805 | 0 | 2805 | 140.25 | 0 | 2945.25 | 205.8 | 25.4369 | 0 | 231.2369 | 3176.4869
2.22 | 502020000 | Providing & fixing SS cabinet (to enclose above FB connection) fabricated from 16g SS 304 sheet with full front glass door and locking arrangement duly painted with one coat of primer and two or more coats of synthetic enamel paint of approved make and shade and suitably mounted on a raised masonry platform as required (Approx 0.6m x 0.6m x 0.45m) | [8 empty] | No. | 0 | 18000 | 0 | 18000 | 900 | 0 | 18900 | 368 | 45.4848 | 0 | 413.4848 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.23 | 502020000 | Providing & fixing gun-metal fire brigade suction hose coupling (draw-out connection) with nut for female coupling as per IS: 902-1992 (Reaffirmed 2007) complete with 100 mm dia GI suction pipe and 100 mm dia foot valve (to be connected to static tank). Provision of GI drop pipe and foot valve shall be made in all the fire water static storage tanks (2 Nos) (GI pipe to be paid separately through appropriate item while cost of foot valve to be included). | [8 empty] | Set | 1 | 18430 | 0 | 18430 | 921.5 | 0 | 19351.5 | 1029 | 127.1844 | 0 | 1156.1844 | 19351.5 | 1156.1844 | 20507.6844 | 10 | 1 | 1843 | 0 | 1843 | 92.15 | 0 | 1935.15 | 102.9 | 12.7184 | 0 | 115.6184 | 2050.7684
2.24 | 502020000 | Providing & fixing SS cabinet (to enclose draw-out connection as per Item above) fabricated from 16 g SS 304 sheet with full front glass door and locking arrangement duly painted with one coat of primer and two or more coats of synthetic enamel paint of approved make and shade and suitably mounted on a raised masonry paltform as required (Approx 0.6 m x 0.6 m x 0.45 m) | [8 empty] | Nos. | 0 | 18000 | 0 | 18000 | 900 | 0 | 18900 | 368 | 45.4848 | 0 | 413.4848 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.25 | 502020000 | Providing and fixing 5 mm thick glass door (with M.S. frame) of size 1.5m x 0.9 m with center opening for fire hose cabinet. Suitably marked on the outside with the letters "FIRE HOSE" including locking arrangement. All M.S. work to be in Red P.O. colour over appropriate primer. The above item is only for masonary fire station. | [8 empty] | No. | 50 | 6321 | 0 | 6321 | 316.05 | 0 | 6637.05 | 772 | 95.4192 | 0 | 867.4192 | 331852.5 | 43370.96 | 375223.46 | 10 | 50 | 31605 | 0 | 31605 | 1580.25 | 0 | 33185.25 | 3860 | 477.096 | 0 | 4337.096 | 37522.346
2.26 | 502020000 | Providing and fixing heavy class MS suction & delivery headers of required length conforming to IS:3589 with welded joints standard MS Fittings and with end flange connections having inlet & outlet flanged connections including MS supports from wall/ floors & ceiling complete as required. Cost should be inclusive of all supports / clamps / brackets, anchor fastner etc. as required (all in M.S.). | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.26.1 | 502020000 | 150 mm dia (C Class) | [8 empty] | RM | 8 | 1675 | 0 | 1675 | 83.75 | 0 | 1758.75 | 494 | 61.0584 | 0 | 555.0584 | 14070 | 4440.4672 | 18510.4672 | 10 | 8 | 1340 | 0 | 1340 | 67 | 0 | 1407 | 395.2 | 48.8467 | 0 | 444.0467 | 1851.0467
2.26.2 | 502020000 | 200 mm dia (6 mm thick) | [8 empty] | RM | 8 | 2499 | 0 | 2499 | 124.95 | 0 | 2623.95 | 658 | 81.3288 | 0 | 739.3288 | 20991.6 | 5914.6304 | 26906.2304 | 10 | 8 | 1999.2 | 0 | 1999.2 | 99.96 | 0 | 2099.16 | 526.4 | 65.063 | 0 | 591.463 | 2690.623
2.26.3 | 502020000 | 250 mm dia (6 mm thick) | [8 empty] | RM | 5 | 3577 | 0 | 3577 | 178.85 | 0 | 3755.85 | 823 | 101.7228 | 0 | 924.7228 | 18779.25 | 4623.614 | 23402.864 | 10 | 5 | 1788.5 | 0 | 1788.5 | 89.425 | 0 | 1877.925 | 411.5 | 50.8614 | 0 | 462.3614 | 2340.2864
2.26.4 | 502020000 | 300 mm dia (6 mm thick) | [8 empty] | RM | 0 | 4800 | 0 | 4800 | 240 | 0 | 5040 | 893 | 110.3748 | 0 | 1003.3748 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.27 | 502020000 | Providing two coats of synthetic enamel paint of approved shade over a coat of primer. Prior to application of primer the surface should be cleaned for any dirt, rusts, rough substance etc. Including painting of legends both direction arrow as per the approval of the Project Manager | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.27.1 | 502020000 | 150 mm da | [8 empty] | RM | 8 | 58 | 0 | 58 | 2.9 | 0 | 60.9 | 31 | 3.8316 | 0 | 34.8316 | 487.2 | 278.6528 | 765.8528 | 10 | 8 | 46.4 | 0 | 46.4 | 2.32 | 0 | 48.72 | 24.8 | 3.0653 | 0 | 27.8653 | 76.5853
2.27.2 | 502020000 | 200 mm di | [8 empty] | RM | 8 | 78 | 0 | 78 | 3.9 | 0 | 81.9 | 41 | 5.0676 | 0 | 46.0676 | 655.2 | 368.5408 | 1023.7408 | 10 | 8 | 62.4 | 0 | 62.4 | 3.12 | 0 | 65.52 | 32.8 | 4.0541 | 0 | 36.8541 | 102.3741
2.27.3 | 502020000 | 250 mm di | [8 empty] | RM | 5 | 98 | 0 | 98 | 4.9 | 0 | 102.9 | 52 | 6.4272 | 0 | 58.4272 | 514.5 | 292.136 | 806.636 | 10 | 5 | 49 | 0 | 49 | 2.45 | 0 | 51.45 | 26 | 3.2136 | 0 | 29.2136 | 80.6636
2.27.4 | 502020000 | 300 mm dia | [8 empty] | RM | 0 | 120 | 0 | 120 | 6 | 0 | 126 | 63 | 7.7868 | 0 | 70.7868 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.28 | 502020000 | Constructing brick masonary chamber (for housing valve) in brick work with bricks of class 75 in cement mortar 1:5 (1 cement:5 fine sand) 12 mm thick plaster on inside with a floating coat of neat cement &rough plaster on external faces with cement mortar 1:3 (1 cement : 3 coarse sand) with 150 mm thick PCC (1:4:8). Including providing 100 mm thick R.C.C. top slab complete in all respect. Cost shall be inclusive of excavation in earth, shoring, dewatering, support to valve and access rungs as required to complete the work. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.28.1 | 502020000 | Size 1200 x 900 x 1000 mm deep | [8 empty] | No. | 3 | 10290 | 0 | 10290 | 514.5 | 0 | 10804.5 | 1544 | 190.8384 | 0 | 1734.8384 | 32413.5 | 5204.5152 | 37618.0152 | 10 | 3 | 3087 | 0 | 3087 | 154.35 | 0 | 3241.35 | 463.2 | 57.2515 | 0 | 520.4515 | 3761.8015
2.29 | 502020000 | Providing & fixing DI medium duty manhole cover with frame of 560 mm internal dia for valve chamber (total weight of cover and frame to be not less than 70 kg for CI). | [8 empty] | No. | 3 | 5390 | 0 | 5390 | 269.5 | 0 | 5659.5 | 515 | 63.654 | 0 | 578.654 | 16978.5 | 1735.962 | 18714.462 | 10 | 3 | 1617 | 0 | 1617 | 80.85 | 0 | 1697.85 | 154.5 | 19.0962 | 0 | 173.5962 | 1871.4462
2.3 | 502020000 | Providing and laying Cement concrete for anchor / thrust blocks of 1:2:4 [1 cement : 2 fine aggregate : 4 coarse aggregate, 40 mm nomional size as per standard design. | [8 empty] | Cum | 2 | 5390 | 0 | 5390 | 269.5 | 0 | 5659.5 | 515 | 63.654 | 0 | 578.654 | 11319 | 1157.308 | 12476.308 | 10 | 2 | 1078 | 0 | 1078 | 53.9 | 0 | 1131.9 | 103 | 12.7308 | 0 | 115.7308 | 1247.6308
2.31 | 502020000 | Providing, Laying, Testing & Jointing RCC NP3 class pipes with collars jointed with stiff mixture of cement mortar in the proportion of 1:2 (1 cement :2 fine sand) including testing of joints etc. complete. Cost shall be inclusive of excavation in earth, trench works dewatering and shoring complete. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.31.1 | 502020000 | 350 mm dia | [8 empty] | RM | 0 | 975 | 0 | 975 | 48.75 | 0 | 1023.75 | 315 | 38.934 | 0 | 353.934 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.32 | 502020000 | Providing & laying cement concrete 1:2:4 (1 cement: 2 sand: 4 graded stone aggregate 40 mm nominal size) upto haunch of RCC pipes including minimum 150 mm thick and 750 mm wide bed concrete, complete as per standard design. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.32.1 | 502020000 | 350 mm dia | [8 empty] | RM | 0 | 1170 | 0 | 1170 | 58.5 | 0 | 1228.5 | 158 | 19.5288 | 0 | 177.5288 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.33 | 502020000 | Providing & fixing brass/ SS mosquito proof grating in elbow with necessary GI vent pipe with fittings | [8 empty] | Nos. | 2 | 2026 | 0 | 2026 | 101.3 | 0 | 2127.3 | 206 | 25.4616 | 0 | 231.4616 | 4254.6 | 462.9232 | 4717.5232 | 10 | 2 | 405.2 | 0 | 405.2 | 20.26 | 0 | 425.46 | 41.2 | 5.0923 | 0 | 46.2923 | 471.7523
2.34 | 502020000 | Providing & fixing mosquito proof brass/ SS overflow grating for tanks | [8 empty] | Nos. | 2 | 2026 | 0 | 2026 | 101.3 | 0 | 2127.3 | 206 | 25.4616 | 0 | 231.4616 | 4254.6 | 462.9232 | 4717.5232 | 10 | 2 | 405.2 | 0 | 405.2 | 20.26 | 0 | 425.46 | 41.2 | 5.0923 | 0 | 46.2923 | 471.7523
i | 502020000 | Note: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii | 502020000 | Core cut markings & cutting shall be done by services vendor. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 502030000 | Sprinkler, Piping & Accessories: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.1 | 502030000 | Providing, laying, jointing and testing of following sizes of pipes conforming to IS-1239 with all accessories like all fittings ( all pipes & fittings upto 50mm dia threaded & for pipes above 50 mm dia MS fitting with welded joint shall be used) including tees, elbows, reducers, union, flanges, rubber gaskets, GI nuts bolts, washer including supporting/fixing the pipe on wall /ceiling with clamps, hangers (using anchor fastners) as per specification. MS pipe sleeve of suitable higher size shall be provided wherever the pipes are crossing the walls/floors and sealing the sleeves with glass wool in between & fire sealent compound at either end all as per Project Managers requirements including cutting holes and chases in brick, R.C.C work and making good the same to original conditions complete in all respects. All hangers, clamps, brackets etc. shall be of galvanized iron unless specified otherwise and the supply of the same shall also be included in rates under this head. Welding of any kind on the galvanized support / hanger shall not be permitted.For Sprinkler system - MS C Heavy class pipe | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.1.1 | 502030000 | 25 mm | [8 empty] | RM | 4100 | 276 | 0 | 276 | 13.8 | 0 | 289.8 | 82 | 10.1352 | 0 | 92.1352 | 1188180 | 377754.32 | 1565934.32 | 10 | 4100 | 113160 | 0 | 113160 | 5658 | 0 | 118818 | 33620 | 4155.432 | 0 | 37775.432 | 156593.432
3.1.2 | 502030000 | 32 mm dia | [8 empty] | RM | 600 | 324 | 0 | 324 | 16.2 | 0 | 340.2 | 103 | 12.7308 | 0 | 115.7308 | 204120 | 69438.48 | 273558.48 | 10 | 600 | 19440 | 0 | 19440 | 972 | 0 | 20412 | 6180 | 763.848 | 0 | 6943.848 | 27355.848
3.1.3 | 502030000 | 40 mm dia | [8 empty] | RM | 425 | 395 | 0 | 395 | 19.75 | 0 | 414.75 | 123 | 15.2028 | 0 | 138.2028 | 176268.75 | 58736.19 | 235004.94 | 10 | 425 | 16787.5 | 0 | 16787.5 | 839.375 | 0 | 17626.875 | 5227.5 | 646.119 | 0 | 5873.619 | 23500.494
3.1.4 | 502030000 | 50 mm dia e | [8 empty] | RM | 450 | 537 | 0 | 537 | 26.85 | 0 | 563.85 | 164 | 20.2704 | 0 | 184.2704 | 253732.5 | 82921.68 | 336654.18 | 10 | 450 | 24165 | 0 | 24165 | 1208.25 | 0 | 25373.25 | 7380 | 912.168 | 0 | 8292.168 | 33665.418
3.1.5 | 502030000 | 65 mm dia c | [8 empty] | RM | 530 | 620 | 0 | 620 | 31 | 0 | 651 | 206 | 25.4616 | 0 | 231.4616 | 345030 | 122674.648 | 467704.648 | 10 | 530 | 32860 | 0 | 32860 | 1643 | 0 | 34503 | 10918 | 1349.4648 | 0 | 12267.4648 | 46770.4648
3.1.6 | 502030000 | 80 mm dia b | [8 empty] | RM | 625 | 849 | 0 | 849 | 42.45 | 0 | 891.45 | 247 | 30.5292 | 0 | 277.5292 | 557156.25 | 173455.75 | 730612 | 10 | 625 | 53062.5 | 0 | 53062.5 | 2653.125 | 0 | 55715.625 | 15437.5 | 1908.075 | 0 | 17345.575 | 73061.2
3.1.7 | 502030000 | 100 mm dia a | [8 empty] | RM | 300 | 1230 | 0 | 1230 | 61.5 | 0 | 1291.5 | 329 | 40.6644 | 0 | 369.6644 | 387450 | 110899.32 | 498349.32 | 10 | 300 | 36900 | 0 | 36900 | 1845 | 0 | 38745 | 9870 | 1219.932 | 0 | 11089.932 | 49834.932
3.1.8 | 502030000 | 150 mm dia e | [8 empty] | RM | 850 | 1750 | 0 | 1750 | 87.5 | 0 | 1837.5 | 494 | 61.0584 | 0 | 555.0584 | 1561875 | 471799.64 | 2033674.64 | 10 | 850 | 148750 | 0 | 148750 | 7437.5 | 0 | 156187.5 | 41990 | 5189.964 | 0 | 47179.964 | 203367.464
3.2 | 502030000 | Providing, fixing, jointing and testing in position the for drainage purpose following heavy class (Class C) MS pipes conforming to IS:1239 cut to required lengths including all necessary fittings (All fittings shall confirm to IS:1879 (part 1 to 10) and specials such as bends, tees, unions, Reducers, flanges & plugs etc. fixing at wall / ceiling level supported by clamps, hangers (using anchor fastners) etc, as per specification. Threading, jointing, and making proper connections, cutting hole in wall / floor / slab and making good the same. GI pipe sleeves suitable higher size shall be provided wherever the pipes are crossing the fire rated walls / floors slab and sealing the sleeves with glass wool in between and fire sealent compound at either end all as per Project Managers / Consultant requirement. All hangers, clamps, brackets etc. shall be of galvanized iron unless specified otherwise and the supply of the same shall also be included in rates under this head. Welding of any kind on the galvanized support / hanger shall not be permitted. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.2.1 | 502030000 | 50 mm dia d | [8 empty] | RM | 25 | 538 | 0 | 538 | 26.9 | 0 | 564.9 | 164 | 20.2704 | 0 | 184.2704 | 14122.5 | 4606.76 | 18729.26 | 10 | 25 | 1345 | 0 | 1345 | 67.25 | 0 | 1412.25 | 410 | 50.676 | 0 | 460.676 | 1872.926
3.2.2 | 502030000 | 65 mm dia g | [8 empty] | RM | 10 | 620 | 0 | 620 | 31 | 0 | 651 | 206 | 25.4616 | 0 | 231.4616 | 6510 | 2314.616 | 8824.616 | 10 | 10 | 620 | 0 | 620 | 31 | 0 | 651 | 206 | 25.4616 | 0 | 231.4616 | 882.4616
3.2.3 | 502030000 | 80 mm dia f | [8 empty] | RM | 150 | 855 | 0 | 855 | 42.75 | 0 | 897.75 | 247 | 30.5292 | 0 | 277.5292 | 134662.5 | 41629.38 | 176291.88 | 10 | 150 | 12825 | 0 | 12825 | 641.25 | 0 | 13466.25 | 3705 | 457.938 | 0 | 4162.938 | 17629.188
3.2.4 | 502030000 | 100 mm dia e | [8 empty] | RM | 50 | 1230 | 0 | 1230 | 61.5 | 0 | 1291.5 | 329 | 40.6644 | 0 | 369.6644 | 64575 | 18483.22 | 83058.22 | 10 | 50 | 6150 | 0 | 6150 | 307.5 | 0 | 6457.5 | 1645 | 203.322 | 0 | 1848.322 | 8305.822
3.2.5 | 502030000 | 150 mm dia | [8 empty] | RM | 0 | 1750 | 0 | 1750 | 87.5 | 0 | 1837.5 | 494 | 61.0584 | 0 | 555.0584 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.3 | 502030000 | Providing two coats of synthetic enamel paint of approved shade over a coat of primer. Prior to application of primer the surface should be cleaned for any dirt, rusts, rough substance etc. Including painting of legends both direction arrow as per the approval of the Project Manager | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.3.1 | 502030000 | 25 mmdia | [8 empty] | RM | 4100 | 9 | 0 | 9 | 0.45 | 0 | 9.45 | 6 | 0.7416 | 0 | 6.7416 | 38745 | 27640.56 | 66385.56 | 10 | 4100 | 3690 | 0 | 3690 | 184.5 | 0 | 3874.5 | 2460 | 304.056 | 0 | 2764.056 | 6638.556
3.3.2 | 502030000 | 32 mm dia d | [8 empty] | RM | 600 | 11 | 0 | 11 | 0.55 | 0 | 11.55 | 8 | 0.9888 | 0 | 8.9888 | 6930 | 5393.28 | 12323.28 | 10 | 600 | 660 | 0 | 660 | 33 | 0 | 693 | 480 | 59.328 | 0 | 539.328 | 1232.328
3.3.3 | 502030000 | 40 mmf | [8 empty] | RM | 425 | 14 | 0 | 14 | 0.7 | 0 | 14.7 | 9 | 1.1124 | 0 | 10.1124 | 6247.5 | 4297.77 | 10545.27 | 10 | 425 | 595 | 0 | 595 | 29.75 | 0 | 624.75 | 382.5 | 47.277 | 0 | 429.777 | 1054.527
3.3.4 | 502030000 | 50 mmd | [8 empty] | RM | 450 | 19 | 0 | 19 | 0.95 | 0 | 19.95 | 11 | 1.3596 | 0 | 12.3596 | 8977.5 | 5561.82 | 14539.32 | 10 | 450 | 855 | 0 | 855 | 42.75 | 0 | 897.75 | 495 | 61.182 | 0 | 556.182 | 1453.932
3.3.5 | 502030000 | 65 mm dia n | [8 empty] | RM | 530 | 24 | 0 | 24 | 1.2 | 0 | 25.2 | 14 | 1.7304 | 0 | 15.7304 | 13356 | 8337.112 | 21693.112 | 10 | 530 | 1272 | 0 | 1272 | 63.6 | 0 | 1335.6 | 742 | 91.7112 | 0 | 833.7112 | 2169.3112
3.3.6 | 502030000 | 80 mm dia b | [8 empty] | RM | 625 | 29 | 0 | 29 | 1.45 | 0 | 30.45 | 16 | 1.9776 | 0 | 17.9776 | 19031.25 | 11236 | 30267.25 | 10 | 625 | 1812.5 | 0 | 1812.5 | 90.625 | 0 | 1903.125 | 1000 | 123.6 | 0 | 1123.6 | 3026.725
3.3.7 | 502030000 | 100 mm dia b | [8 empty] | RM | 300 | 39 | 0 | 39 | 1.95 | 0 | 40.95 | 21 | 2.5956 | 0 | 23.5956 | 12285 | 7078.68 | 19363.68 | 10 | 300 | 1170 | 0 | 1170 | 58.5 | 0 | 1228.5 | 630 | 77.868 | 0 | 707.868 | 1936.368
3.3.8 | 502030000 | 150 mm dia b | [8 empty] | RM | 1200 | 58 | 0 | 58 | 2.9 | 0 | 60.9 | 32 | 3.9552 | 0 | 35.9552 | 73080 | 43146.24 | 116226.24 | 10 | 1200 | 6960 | 0 | 6960 | 348 | 0 | 7308 | 3840 | 474.624 | 0 | 4314.624 | 11622.624
3.4 | 502030000 | Designing, providing and fixing Orifice plate made out of stainless stand plate (thickness as per specification) for following size of pipe to reduce pressure upto 3.5 Kg/sqcm complete in all respects. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.4.1 | 502030000 | 65 mm dia | [8 empty] | No | 0 | 700 | 0 | 700 | 35 | 0 | 735 | 53 | 6.5508 | 0 | 59.5508 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.4.2 | 502030000 | 80 mm dia | [8 empty] | No. | 0 | 700 | 0 | 700 | 35 | 0 | 735 | 53 | 6.5508 | 0 | 59.5508 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.4.3 | 502030000 | 100 mm diaa | [8 empty] | No. | 7 | 686 | 0 | 686 | 34.3 | 0 | 720.3 | 53 | 6.5508 | 0 | 59.5508 | 5042.1 | 416.8556 | 5458.9556 | 10 | 7 | 480.2 | 0 | 480.2 | 24.01 | 0 | 504.21 | 37.1 | 4.5856 | 0 | 41.6856 | 545.8956
3.5 | 502030000 | Providing and fixing forged brass ball valve with forged brass ball (suitable for test pressure of 30 Kg / sqm of the following size including providing necessary union / flange. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.5.1 | 502030000 | 25 mm diaa | [8 empty] | No. | 40 | 650 | 0 | 650 | 32.5 | 0 | 682.5 | 103 | 12.7308 | 0 | 115.7308 | 27300 | 4629.232 | 31929.232 | 10 | 40 | 2600 | 0 | 2600 | 130 | 0 | 2730 | 412 | 50.9232 | 0 | 462.9232 | 3192.9232
3.6 | 502030000 | Providing & fixing of butterfly valve of PN 16 rating with flanges, nut bolts & gaskets complete required. Butterfly valve shall be with pad locking arrangement. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.6.1 | 502030000 | 80 mm | [8 empty] | No. | 35 | 3626 | 0 | 3626 | 181.3 | 0 | 3807.3 | 412 | 50.9232 | 0 | 462.9232 | 133255.5 | 16202.312 | 149457.812 | 10 | 35 | 12691 | 0 | 12691 | 634.55 | 0 | 13325.55 | 1442 | 178.2312 | 0 | 1620.2312 | 14945.7812
3.6.2 | 502030000 | 100 mm | [8 empty] | No. | 11 | 4753 | 0 | 4753 | 237.65 | 0 | 4990.65 | 515 | 63.654 | 0 | 578.654 | 54897.15 | 6365.194 | 61262.344 | 10 | 11 | 5228.3 | 0 | 5228.3 | 261.415 | 0 | 5489.715 | 566.5 | 70.0194 | 0 | 636.5194 | 6126.2344
3.6.3 | 502030000 | 150 mm | [8 empty] | No. | 0 | 7900 | 0 | 7900 | 395 | 0 | 8295 | 788 | 97.3968 | 0 | 885.3968 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.7 | 502030000 | Providing & Fixing of Installation Control Valve with turbine type automatic Alarm Gong to be connected with control valve, drain & test valve and all other necessary components as per manufacturers specifications complete as required. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.7.1 | 502030000 | 150 mm diaam | [8 empty] | No. | 3 | 44100 | 0 | 44100 | 2205 | 0 | 46305 | 3087 | 381.5532 | 0 | 3468.5532 | 138915 | 10405.6596 | 149320.6596 | 10 | 3 | 13230 | 0 | 13230 | 661.5 | 0 | 13891.5 | 926.1 | 114.466 | 0 | 1040.566 | 14932.066
3.8 | 502030000 | Providing & fixing brass quartzoid sprinklers (UL listed) of 15 mm dia size, suitable for sustaining the pressure on the seat & water hammer effect. The type & temperature rating shall be as follows : | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.8.1 | 502030000 | Sidewall extended coverage (68 deg.C) sprinkler quick response type for Guest room area | [8 empty] | Nos | 215 | 520 | 0 | 520 | 26 | 0 | 546 | 53 | 6.5508 | 0 | 59.5508 | 117390 | 12803.422 | 130193.422 | 10 | 215 | 11180 | 0 | 11180 | 559 | 0 | 11739 | 1139.5 | 140.8422 | 0 | 1280.3422 | 13019.3422
3.8.2 | 502030000 | Sidewall extended coverage (79 deg.C) sprinkler quick response type for Car Parking | [8 empty] | Nos | 115 | 645 | 0 | 645 | 32.25 | 0 | 677.25 | 53 | 6.5508 | 0 | 59.5508 | 77883.75 | 6848.342 | 84732.092 | 10 | 115 | 7417.5 | 0 | 7417.5 | 370.875 | 0 | 7788.375 | 609.5 | 75.3342 | 0 | 684.8342 | 8473.2092
3.8.3 | 502030000 | Recessed pendent type quick responsetype sprinkler (20 mm adjustable) (68 deg.c) for Guest room area | [8 empty] | Nos | 720 | 255 | 0 | 255 | 12.75 | 0 | 267.75 | 53 | 6.5508 | 0 | 59.5508 | 192780 | 42876.576 | 235656.576 | 10 | 720 | 18360 | 0 | 18360 | 918 | 0 | 19278 | 3816 | 471.6576 | 0 | 4287.6576 | 23565.6576
3.8.4 | 502030000 | Recessed pendent type quick responsetype sprinkler (20 mm adjustable) (79 deg.c) for BOH area | [8 empty] | Nos | 240 | 275 | 0 | 275 | 13.75 | 0 | 288.75 | 53 | 6.5508 | 0 | 59.5508 | 69300 | 14292.192 | 83592.192 | 10 | 240 | 6600 | 0 | 6600 | 330 | 0 | 6930 | 1272 | 157.2192 | 0 | 1429.2192 | 8359.2192
3.8.5 | 502030000 | Side wall extended coverage quick response sprinkler (141 deg.C) for lift machine room. | [8 empty] | Nos | 10 | 825 | 0 | 825 | 41.25 | 0 | 866.25 | 72 | 8.8992 | 0 | 80.8992 | 8662.5 | 808.992 | 9471.492 | 10 | 10 | 825 | 0 | 825 | 41.25 | 0 | 866.25 | 72 | 8.8992 | 0 | 80.8992 | 947.1492
3.8.6 | 502030000 | Quick response Pendent type (79) deg.C) sprinkler For Car parking Areas. | [8 empty] | Nos. | 300 | 437 | 0 | 437 | 21.85 | 0 | 458.85 | 53 | 6.5508 | 0 | 59.5508 | 137655 | 17865.24 | 155520.24 | 10 | 300 | 13110 | 0 | 13110 | 655.5 | 0 | 13765.5 | 1590 | 196.524 | 0 | 1786.524 | 15552.024
3.8.7 | 502030000 | Upright (79 deg. C) sprinkler for service floor, car parking and non A/c areas. | [8 empty] | Nos. | 400 | 437 | 0 | 437 | 21.85 | 0 | 458.85 | 53 | 6.5508 | 0 | 59.5508 | 183540 | 23820.32 | 207360.32 | 10 | 400 | 17480 | 0 | 17480 | 874 | 0 | 18354 | 2120 | 262.032 | 0 | 2382.032 | 20736.032
3.8.8 | 502030000 | Pendent (141 deg.C) sprinkler for Boiler room / DG set room, fire pump rom & lift machine room) | [8 empty] | Nos. | 8 | 864 | 0 | 864 | 43.2 | 0 | 907.2 | 53 | 6.5508 | 0 | 59.5508 | 7257.6 | 476.4064 | 7734.0064 | 10 | 8 | 691.2 | 0 | 691.2 | 34.56 | 0 | 725.76 | 42.4 | 5.2406 | 0 | 47.6406 | 773.4006
3.8.9 | 502030000 | Quick response dry pendent sprinkler for cold store rooms (68 deg.c) | [8 empty] | Nos. | 10 | 10000 | 0 | 10000 | 500 | 0 | 10500 | 225 | 27.81 | 0 | 252.81 | 105000 | 2528.1 | 107528.1 | 10 | 10 | 10000 | 0 | 10000 | 500 | 0 | 10500 | 225 | 27.81 | 0 | 252.81 | 10752.81
3.8.10 | 502030000 | Automatic spray nozzle, deep fat fryer (for kitchen hoods) sprinkler | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
a. | 502030000 | 175 deg.C | [8 empty] | Nos. | 0 | 1230 | 0 | 1230 | 61.5 | 0 | 1291.5 | 105 | 12.978 | 0 | 117.978 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
b. | 502030000 | 250 deg.C | [8 empty] | Nos. | 0 | 1500 | 0 | 1500 | 75 | 0 | 1575 | 105 | 12.978 | 0 | 117.978 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
c. | 502030000 | 325 deg.C | [8 empty] | Nos. | 0 | 1680 | 0 | 1680 | 84 | 0 | 1764 | 105 | 12.978 | 0 | 117.978 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.8.11 | 502030000 | Multi spray sprinkler system for window / issue counter suitable for providing water curtain effect. | [8 empty] | Set | 0 | 690 | 0 | 690 | 34.5 | 0 | 724.5 | 53 | 6.5508 | 0 | 59.5508 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i | 502030000 | All sprinkler shall be chrome finish except for the concealed ones. The concealed sprinkler shall be of brass finish. The cover plates of the concealed sprinkler shall be factory painted at manufacturers work and the shade shall be confirmed prior to application on the cover plate. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii | 502030000 | Core cut markings & cutting shall be done by services vendor. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.9 | 502030000 | Providing and Fixing electrically operated water flow switches (Vane type) including tamper switch and accessories, complete with tap off socket arrangement as required, with potential free contact with 2 Nos. NONC. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.9.1 | 502030000 | 65 mm diaa | [8 empty] | No. | 2 | 4214 | 0 | 4214 | 210.7 | 0 | 4424.7 | 200 | 24.72 | 0 | 224.72 | 8849.4 | 449.44 | 9298.84 | 10 | 2 | 842.8 | 0 | 842.8 | 42.14 | 0 | 884.94 | 40 | 4.944 | 0 | 44.944 | 929.884
3.9.2 | 502030000 | 80 mm diaa | [8 empty] | No. | 33 | 4214 | 0 | 4214 | 210.7 | 0 | 4424.7 | 200 | 24.72 | 0 | 224.72 | 146015.1 | 7415.76 | 153430.86 | 10 | 33 | 13906.2 | 0 | 13906.2 | 695.31 | 0 | 14601.51 | 660 | 81.576 | 0 | 741.576 | 15343.086
3.9.3 | 502030000 | 100 mmd | [8 empty] | No. | 11 | 4214 | 0 | 4214 | 210.7 | 0 | 4424.7 | 200 | 24.72 | 0 | 224.72 | 48671.7 | 2471.92 | 51143.62 | 10 | 11 | 4635.4 | 0 | 4635.4 | 231.77 | 0 | 4867.17 | 220 | 27.192 | 0 | 247.192 | 5114.362
3.9.4 | 502030000 | 150 mm di | [8 empty] | No. | 1 | 4214 | 0 | 4214 | 210.7 | 0 | 4424.7 | 200 | 24.72 | 0 | 224.72 | 4424.7 | 224.72 | 4649.42 | 10 | 1 | 421.4 | 0 | 421.4 | 21.07 | 0 | 442.47 | 20 | 2.472 | 0 | 22.472 | 464.942
3.1 | 502030000 | Providing and fixing inspectors test assembly complete with test valve, sight glass sectional drain valve, union; necessary piping, threading, jointing & with corrosion resistant orifice all complete strictly as per drawing. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.10.1 | 502030000 | 50 mm | [8 empty] | No. | 40 | 3283 | 0 | 3283 | 164.15 | 0 | 3447.15 | 257 | 31.7652 | 0 | 288.7652 | 137886 | 11550.608 | 149436.608 | 10 | 40 | 13132 | 0 | 13132 | 656.6 | 0 | 13788.6 | 1028 | 127.0608 | 0 | 1155.0608 | 14943.6608
i | 502030000 | Cost shall be inclusive for approval of fire hydrant & sprinkler system from local fire authority and any other relevant statutory authority at initial & various other stages of works, including preparation of report / drawings as per fire authority. Contractor shall include cost of all liaison works which are not explicitly mentioned above but are mandatory to have fire authority approval (any statutory charges will be reimbursed as per actual upon production of the invoice / challan). | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 502040000 | Portable Chemical Fire Extinguishers:Supply, installation, testing and commissioning of following types of extinguisher with provision of wall bracket (fixed with anchor fastner). | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4.1 | 502040000 | ISI marked (IS:940) portable fire extinguisher, water (gas pressure) type capacity 9 litres with gun metal cap and nozzle and complete in all respects including initial fill and wall suspension brackets | [8 empty] | Each | 45 | 2058 | 0 | 2058 | 102.9 | 0 | 2160.9 | 53 | 6.5508 | 0 | 59.5508 | 97240.5 | 2679.786 | 99920.286 | 10 | 45 | 9261 | 0 | 9261 | 463.05 | 0 | 9724.05 | 238.5 | 29.4786 | 0 | 267.9786 | 9992.0286
4.2 | 502040000 | ISI marked (IS:2878) portable CO2 type fire extinguisher type. Including valve, discharge hose of not less than 10 mm dia & 1 M long complete in all respects including initial filled with CO2 gas confirming to IS:307-1966 & filled to a filling rate of not more than 0.667 and wall suspension bracket. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4.2.1 | 502040000 | 4.5kg capacity | [8 empty] | Each | 0 | 6500 | 0 | 6500 | 325 | 0 | 6825 | 53 | 6.5508 | 0 | 59.5508 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4.3 | 502040000 | ISI marked (IS:2171) Portable Dry Chemical Power Type Fire Extinguisher with Gun Metal cap and nozzle complete in all respects including initial fill of power and wall suspension bracket | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4.3.1 | 502040000 | 5 Kgg | [8 empty] | Each | 15 | 2468 | 0 | 2468 | 123.4 | 0 | 2591.4 | 53 | 6.5508 | 0 | 59.5508 | 38871 | 893.262 | 39764.262 | 10 | 15 | 3702 | 0 | 3702 | 185.1 | 0 | 3887.1 | 79.5 | 9.8262 | 0 | 89.3262 | 3976.4262
4.4 | 502040000 | ABC (Powder Type) Fire Extinguisher. In HP Mild Steel Cylinders ISI marked/ TAC approved fitted with pressure indicating gauge, internal tube, squeeze lever type valve fully charged with ABC powder (Mono Ammonium Phosphate) pressured by Nitrogen complete in all respects including wall suspension bracket and confoming to IS:1349-1993 | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4.4.1 | 502040000 | 5 Kg | [8 empty] | Each | 0 | 2350 | 0 | 2350 | 117.5 | 0 | 2467.5 | 53 | 6.5508 | 0 | 59.5508 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4.4.2 | 502040000 | 10 Kg | [8 empty] | Each | 20 | 2695 | 0 | 2695 | 134.75 | 0 | 2829.75 | 53 | 6.5508 | 0 | 59.5508 | 56595 | 1191.016 | 57786.016 | 10 | 20 | 5390 | 0 | 5390 | 269.5 | 0 | 5659.5 | 106 | 13.1016 | 0 | 119.1016 | 5778.6016
4.5 | 502040000 | Supplying and installing at approved location approved make fire buckets of 24 gauge galvanized steel sheet, standard 9 litre capacity and of round bottom shape, painted white inside and red outside and black on the bottom, inscribed with letters “FIRE” in black and gold. Cost shall be inclusive of providing MS stand duly painted over a coat of primer. | [8 empty] | Nos. | 15 | 240 | 0 | 240 | 12 | 0 | 252 | 53 | 6.5508 | 0 | 59.5508 | 3780 | 893.262 | 4673.262 | 10 | 15 | 360 | 0 | 360 | 18 | 0 | 378 | 79.5 | 9.8262 | 0 | 89.3262 | 467.3262
5 | 502060000 | Permits / Inspections and Approval of Systems | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.1 | 502060000 | Obtaining composite approval for the entire fire protection system including fire fighting, fire detection, fire doors etc. and all other related works which fall under the purview of the local statutory authority / Chief Fire Officer and making payments / liaisoning / incidental charges for the portion of works carried out by the Contractor. Drawings and other submittal for works done by other agencies as per the regulations will be furnished to the Contractor for obtaining such approval. All the expenses incurred in this regard including incidentals shall be borne by the Contractor. However all Statutory payments against challans shall be paid by client. | [8 empty] | Job | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 245000 | 30282 | 0 | 275282 | 0 | 275282 | 275282 | 10 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 24500 | 3028.2 | 0 | 27528.2 | 27528.2
I | 502050000 | ELECTRICAL INSTALLATION FOR PLUMBING | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 502050000 | Electrical panel for Plumbing System | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.1 | 502050000 | Design, fabrication, assembling, wiring, supply, installation, testing and commissioning of motor control centre shall be fabricated out of 14 gauge CRCA sheet steel in form in 3b formation with reinforcement of suitable size angle iron, channel T sections irons and/or flats wherever necessary. Cable gland plates shall be provided on top as well as at the bottom of the panels. Panels shall be treated with all anticorrosive process before painting as per specifications with 2 coats of red oxide primer and final approved shade of powder coated paint. 2 Nos. earthing terminals shall be provided for 3 phase, 4 wire, 50 Hz supply system. Lifting hooks shall also be provided in case of large panels. Approval shall be taken for each panel before fabrication. Cadmium Plated hardware shall be used in fabrication of panels. MCC for Plumbing systemIncoming200 amps TPN MCCB (25KA) with the following accessories: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
a. | 502050000 | a. 0-500 volts 96 x 96 mm square digital electronic voltmeter with selector switch protected by 2 amps TP MCB. 1 Set | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
b. | 502050000 | b. 0-200 amps 96 x 96 mm square digital electronic ammeter with selector switch and 3 nos 200/5 amps 5 VA CL:1 CTs. 1 Set | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
c. | 502050000 | Phase indicating lamps protected by 2 amp SP MCB 3 Sets | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
d. | 502050000 | Digital electronic KWH meter with RS 485 port.Bus Bar200 amps TPN (25KA) copper bus bar with heat shrinkable insulation sleeves. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 502050000 | Outgoings | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
a. | 502050000 | 1 Nos. 40 amps TPN MCCB outgoing feeder to Lower zone Domestic water Hydropneumatic system panel. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
b. | 502050000 | 1 No. 100 amps TPN MCCB outgoing to upper zone domestic water Hydropneumatic system panel | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
c. | 502050000 | 1 No. 100 amps TPN MCCB outgoing to flushing water Hydropneumatic system panel | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
d. | 502050000 | 25 amps TPN MCCB for plant room sump pump control panel | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
e | 502050000 | 3 nos 25 amps TPN MCCB for car park sump pump control panel | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
f | 502050000 | 1 Nos. suitable rating TPN MPCB for 7.5 HP/5.5 KW DOL starter and outgoing feeder to Plant room Exhaust fan motor. Each compartment shall contain CT operated digital electronic ammeter suitable range with auto/manual selector switch and indicating lamps with MCBs and ON/OFF/TRIP status of motor | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
g. | 502050000 | 1 Nos. suitable rating TPN MPCB for 7.5 HP/5.5 KW DOL starter and outgoing feeder to Plant room Supply fan motor. Each compartment shall contain CT operated digital electronic ammeter suitable range with auto/manual selector switch and indicating lamps with MCBs and ON/OFF/TRIP status of motor | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
h. | 502050000 | c. 2 Nos. suitable rating TPN MPCB for 2.5 HP/ 1.8 KW DOL starter and outgoing feeder to Filter Feed pump (1 working + 1 standby). Each compartment shall contain direct operated digital electronic ammeter of suitable range with auto/manual selector switch and indicating lamps with MCBs and ON/OFF/TRIP status of motor | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i | 502050000 | Spare MCCBs of following capacities: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
j | 502050000 | 63 amps TPN MCCB 2 Nos. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 502050000 | Necessary cable alleys, internal wiring, and interlocking, earthing for all equipment shall also included | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
a. | 502050000 | All MCCBs shall be of 25 KA breaking capacity and suitable for motor duty application. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
b. | 502050000 | Provision shall be made for providing potential free contacts to all pumps starters for connection to BAS | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
c. | 502050000 | Provision shall be made to ensure system protection from dry running of the pump | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
d. | 502050000 | MCCB/MPCB shall be Type 2 Co-ordinated with the Motor starter. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 502050000 | MCC for Plumbing system System as described above. | [8 empty] | Set | 1 | 313983 | 0 | 313983 | 15699.15 | 0 | 329682.15 | 25725 | 3179.61 | 0 | 28904.61 | 329682.15 | 28904.61 | 358586.76 | 10 | 1 | 31398.3 | 0 | 31398.3 | 1569.915 | 0 | 32968.215 | 2572.5 | 317.961 | 0 | 2890.461 | 35858.676
2 | 502050000 | Control Panel For Drainage Sump Pump | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.1 | 502050000 | Incoming25 Amps 4 pole MCB with the following accessories:a. 0-500 volts 96 x 96 mm square digital electronic voltmeter with selector switch protected by 2 amps TP MCB. 1 Setb. 0-25 amps 96 x 96 mm square digital electronic ammeter with selector switch and 3 nos 25/5 amps 5 VA CL:1 CTs. 1 Setc. Phase indicating lamps protected by 2 amp SP MCB 3 SetsBus Bar25 Amps TPN copper bus bar with heat shrinkable insulation sleeves.Outgoingsa. 2 Nos. 16 amps 4 Pole MCB for 2 Nos. 4 HP/3 KW direct on line starter and outgoing feeders to Sump pump motor . Each compartment shall contain direct operated digital electronic ammeter of 0-16amps range with auto/manual selector switch and indicating lamps with MCBs and ON/OFF/TRIP status of motorb. Necessary cable alleys, internal wiring, and interlocking, earthing for all equipment shall also includedNotesa. All MCBs shall be of 10 kA breaking capacity. b. All motor starter shall be provided with Automatic float type level controllerc. Provision of high high level alarm shall also be maded. It shall be ensured that all pumps operate during high high level in the sumpe. Sequence timer for pump operation shall be providedf. Provision shall be made for providing potential free contacts to all pumps starters for connection to BASg. MCB shall be of type “C” characteristic | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 502050000 | Control Panel for Drainage Pumps as described above | [8 empty] | Nos. | 5 | 40250 | 0 | 40250 | 2012.5 | 0 | 42262.5 | 2573 | 318.0228 | 0 | 2891.0228 | 211312.5 | 14455.114 | 225767.614 | 10 | 5 | 20125 | 0 | 20125 | 1006.25 | 0 | 21131.25 | 1286.5 | 159.0114 | 0 | 1445.5114 | 22576.7614
3.1 | 502050000 | Control Panel for Swimming Pool : | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.2 | 502050000 | Design, fabrication, assembling, wiring, supply, installation, testing and commissioning of motor control centre shall be fabricated out of 14 gauge CRCA sheet steel in form in 3b formation with reinforcement of suitable size angle iron, channel T sections irons and/or flats wherever necessary. Cable gland plates shall be provided on top as well as at the bottom of the panels. Panels shall be treated with all anticorrosive process before painting as per specifications with 2 coats of red oxide primer and final approved shade of powder coated paint. 2 Nos. earthing terminals shall be provided for 3 phase, 4 wire, 50 Hz supply system. Lifting hooks shall also be provided in case of large panels. Approval shall be taken for each panel before fabrication. Cadimium plated hardware shall be used in fabrication of panels | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.3 | 502050000 | MCC Swimming Pool | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.4 | 502050000 | Incoming63 amps TPN MCCB with the following accessories:0-500 volts 96 x 96 mm square digital electronic voltmeter with selector switch protected by 2 amps TP MCB. 1 Set0-63 amps 96 x 96 mm square digital electronic ammeter with selector switch and 3 nos 63/5 amps 5 VA CL:1 CTs. 1 SetPhase indicating lamps protected by 2 amp SP MCB 3 SetsBus Bar63 amps TPN copper bus bar with heat shrinkable insulation sleeves.Outgoings2Nos suitable rating TPN MPCB with 2Nos. 12.5 HP/ 9.3 KW star delta starter and outgoing feeder to swimming pool pump. Each compartment shall contain CT operated digital electronic ammeter of suitable amps range with auto/manual selector switch and indicating lamps with MCBs and ON/OFF/TRIP status of motor1 nos. 25 amps DP MCBs for dosing pumps1 nos. 16 amps DP MCBs for UV unitSpare MCCBs of following capacities:25 amps TPN MCB 2 NosNecessary cable alleys, internal wiring, and interlocking, earthing for all equipment shall also included.All MCCBs shall be of 25 KA breaking capacity.Provision shall be made for providing potential free contacts to all pumps starters for connection to BASMPCB shall be Type 2 Co-ordinated with the Motor starter. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.5 | 502050000 | MCC for swimming pool as described above | [8 empty] | No. | 1 | 62830 | 0 | 62830 | 3141.5 | 0 | 65971.5 | 5145 | 635.922 | 0 | 5780.922 | 65971.5 | 5780.922 | 71752.422 | 10 | 1 | 6283 | 0 | 6283 | 314.15 | 0 | 6597.15 | 514.5 | 63.5922 | 0 | 578.0922 | 7175.2422
J | 502050000 | ELECTRICAL WORK FOR FIRE PROTECTION SYSTEM: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 502050000 | Control Panel for Fire protection system: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.1 | 502050000 | Control Panel for fire fighting equipment in pump room :- | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.2 | 502050000 | Design, manufacture, supply, installation, testing and commissioning of the following integrated, cubicle type, dead front, extensible, sheet steel control panel anchoring the panel to the foundation. The panel shall be duly powder coated and suitable for 500 volts, 50 cycles, 4 wire supply. Quoted price shall include 1100 volts grade rubber mats over 50mm thick teak wood platform, control wiring. The panel shall have separate compartments for bus bar and cable alleys. The following components and accessories shall be mounted within each control panel. (IP 55) a. One No. 630 amps TPN incoming MCCB complete with the following:i. 0-500 volts 96 x 96mm square digital electronic voltmeter with selector switch protected by 2 amps TP MCB 1 Setii. 0-630 amps 96 x 96 mm square digital electronic ammeter with 3 nos 630/5 amps 15 VA CL:1 CTs and selector switch 1 Setiii. Phase indicating lamps protected by 2 amps SP MCB 3 Setsb. Copper bus bar with heat shrinkable sleeves, rated at 630amps(25KA) for three phase & neutral phase bus bar shall have maximum current density of 0.8 amps per sq.mm. and the neutral bus bar of not less than 50% capacity. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.3 | 502050000 | Outgoing:c. 1 Nos. 250 amps TPN MCCB with 125 HP/ 90 KW Star Delta starters & out going feeders to Fire Hydrant pump motor. The compartment shall contain CT operated digital electronic ammeter of 0-250 amps range with selector switch and indicating lamp with MCBs for ON/OFFTRIP status of motor.d. 1 Nos. 250 amps TPN MCCB with 125 HP/ 90 KW Star Delta starters & out going feeders to Fire sprinkler pump motor. The compartment shall contain CT operated digital electronic ammeter of 0-25 amps range with selector switch and indicating lamp with MCBs for ON/OFFTRIP status of motor.e. 1 Nos. suitable rating TPN MPCB with 10 HP/7.5 KW DOL starter with single phase preventer and outgoing feeder to hydrant jockey pump motor. The compartment shall contain CT operated digital electronic ammeter of suitable range and indicating lamps with MCBs for ON/OFFTRIP status of pump motors.f. 1 Nos.suitable range TPN MPCB, with 10HP/7.5 KW DOL starter with single phase preventer and outgoing feeder to sprinkler jockey pump motor. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0.1236 | 1 | 1.1236 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.4 | 502050000 | The compartment shall contain CT operated digital electronic ammeter suitable range and indicating lamps with MCBs for ON/OFFTRIP status of pump motors.g. 1 Nos. 25 Amps TPN Motor duty MCCB for hydrant booster pump motor control panel on terrace floor With ON/OFF Push button and indicating lamps with Mcbs for ON/OFFTRIP status of pump motors including necessary control wiring.h. 1 No. 63 amps TPN MCCB as sparei. Necessary cable alleys space for spare switches, internal wiring and earthing of all equipment shall also be included. All switch gears/control gears shall be motor duty rating.j. Providing and fixing 1 No. auto start panel activated with pressure switch for diesel engine complete with all accessories, batteries, battery charger of suitable rating, MCB timers, push buttons, microprocessor based alarm annunciator, wiring and cabling including connection to diesel engine complete as required ready for working.NoteAll MCCBs to be suitable for motor duty and shall be of 25 kA breaking capacity.Provision shall be made for providing potential free contacts to all pumps starters for connection to building automation system.MCCB shall be Type 2 Co-ordinated with the Motor starter. | [8 empty] | Nil | 0 | [13 empty] | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.5 | 502050000 | Motor control panel-FF as described above | [8 empty] | Set | 1 | 530000 | 0 | 530000 | 26500 | 0 | 556500 | 25725 | 3179.61 | 0 | 28904.61 | 556500 | 28904.61 | 585404.61 | 10 | 1 | 53000 | 0 | 53000 | 2650 | 0 | 55650 | 2572.5 | 317.961 | 0 | 2890.461 | 58540.461
2 | 502050000 | CONTROL PANEL FOR TERRACE BOOSTER PUMP MOTOR. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.1 | 502050000 | Design, manufacture, supply, installation, testing and commissioning of the following cubicle type, dead front, sheet steel, wall mounted control panels, including anchoring into the wall, incoming cable wiring terminating into MCCB and copper earthing, to the starter panel. Starter control panel shall be provided with Stop /Manual /Auto selector switch to facilitate operation through BAS. starters shall be provided with potential free Contact for Connections to Building Automation System.All wiring and copper earthing of motors from the panel shall be included.The panel shall include the following components & accessories. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
a. | 502050000 | MCCB/MPCB as per the ratings given below, suitable for motor duty and able to withstand fault level of 25 KA. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
b. | 502050000 | SD starter as per HP gratings given. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
c. | 502050000 | Terminal block for power distribution as required. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
d. | 502050000 | Contactor, over load relay with built in single phasing protection. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
e | 502050000 | Phase indicating lights and indicating light for ON status. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
f | 502050000 | 144 mm x 144 mm voltmeter and digital ammeter. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
g. | 502050000 | Time delay relay for delayed automatic restart of motor. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
h. | 502050000 | For on/off/remote and local operation, 3 pole single throw switch shall be provided to facilitate override of the automatic operation. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i | 502050000 | Starters control panel shall be provided with suitable potential free contract for connections to the Building Automation System. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
j | 502050000 | MCCB/MPCB shall be Type 2 Co-ordinated with the Motor starter. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
k | 502050000 | Degree of Protection for the starter panel shall be IP 55. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 502050000 | CONTROL PANEL FOR TERRACE BOOSTER PUMP MOTOR as described above | [8 empty] | No. | 1 | 14700 | 0 | 14700 | 735 | 0 | 15435 | 3087 | 381.5532 | 0 | 3468.5532 | 15435 | 3468.5532 | 18903.5532 | 10 | 1 | 1470 | 0 | 1470 | 73.5 | 0 | 1543.5 | 308.7 | 38.1553 | 0 | 346.8553 | 1890.3553
3.1 | 502050000 | Cable & Cable Trays for Plumbing & Fire Protection System | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.1.1 | 502050000 | Supplying & laying of following 1100 volt grade XLPE insulated PVC inner sheathed & FRLS PVC outer sheathed aluminium/copper conductor armoured cables as per specification buried, in existing , cable trays, ducts, clamped to wall with suitable clamps, saddles fixing bolts including connecting testing and commissioning. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.1.2 | 502050000 | 3 core 70 sq. mm Aluminium cable | [8 empty] | RM | 100 | 292 | 0 | 292 | 14.6 | 0 | 306.6 | 52 | 6.4272 | 0 | 58.4272 | 30660 | 5842.72 | 36502.72 | 10 | 100 | 2920 | 0 | 2920 | 146 | 0 | 3066 | 520 | 64.272 | 0 | 584.272 | 3650.272
3.1.3 | 502050000 | 3.5 core 50 sq. mm Aluminium cable | [8 empty] | RM | 50 | 244 | 0 | 244 | 12.2 | 0 | 256.2 | 52 | 6.4272 | 0 | 58.4272 | 12810 | 2921.36 | 15731.36 | 10 | 50 | 1220 | 0 | 1220 | 61 | 0 | 1281 | 260 | 32.136 | 0 | 292.136 | 1573.136
3.1.4 | 502050000 | 4 core 25 sq. mm Aluminium cable | [8 empty] | RM | 50 | 164 | 0 | 164 | 8.2 | 0 | 172.2 | 41 | 5.0676 | 0 | 46.0676 | 8610 | 2303.38 | 10913.38 | 10 | 50 | 820 | 0 | 820 | 41 | 0 | 861 | 205 | 25.338 | 0 | 230.338 | 1091.338
3.1.5 | 502050000 | 4 core 4 sq. mm copper cable | [8 empty] | RM | 50 | 216 | 0 | 216 | 10.8 | 0 | 226.8 | 41 | 5.0676 | 0 | 46.0676 | 11340 | 2303.38 | 13643.38 | 10 | 50 | 1080 | 0 | 1080 | 54 | 0 | 1134 | 205 | 25.338 | 0 | 230.338 | 1364.338
3.1.6 | 502050000 | 3 core 6 sq. mm copper cable | [8 empty] | RM | 75 | 245 | 0 | 245 | 12.25 | 0 | 257.25 | 36 | 4.4496 | 0 | 40.4496 | 19293.75 | 3033.72 | 22327.47 | 10 | 75 | 1837.5 | 0 | 1837.5 | 91.875 | 0 | 1929.375 | 270 | 33.372 | 0 | 303.372 | 2232.747
3.1.7 | 502050000 | 3 core 4 sq. mm copper cable | [8 empty] | RM | 100 | 170 | 0 | 170 | 8.5 | 0 | 178.5 | 36 | 4.4496 | 0 | 40.4496 | 17850 | 4044.96 | 21894.96 | 10 | 100 | 1700 | 0 | 1700 | 85 | 0 | 1785 | 360 | 44.496 | 0 | 404.496 | 2189.496
3.2 | 502050000 | Cable end termination of the following XLPE insulated FRLS PVC outer sheathed aluminium/copper conductor armoured cables of 1100 volt grade including supplying and fixing of bimettalic crimping lugs, double compression glands with earthing. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.2.1 | 502050000 | 3 core 70 sq. mm Aluminium cabl | [8 empty] | Nos | 10 | 441 | 0 | 441 | 22.05 | 0 | 463.05 | 82 | 10.1352 | 0 | 92.1352 | 4630.5 | 921.352 | 5551.852 | 10 | 10 | 441 | 0 | 441 | 22.05 | 0 | 463.05 | 82 | 10.1352 | 0 | 92.1352 | 555.1852
3.2.2 | 502050000 | MPCB suitable for 11 KW booster pump motor with star delta Starter as described above | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.2.3 | 502050000 | 3.5 core 50 sq. mm Aluminium cabl | [8 empty] | Nos | 6 | 318 | 0 | 318 | 15.9 | 0 | 333.9 | 61 | 7.5396 | 0 | 68.5396 | 2003.4 | 411.2376 | 2414.6376 | 10 | 6 | 190.8 | 0 | 190.8 | 9.54 | 0 | 200.34 | 36.6 | 4.5238 | 0 | 41.1238 | 241.4638
3.2.4 | 502050000 | 4 core 25 sq. mm Aluminium cabl | [8 empty] | Nos | 2 | 240 | 0 | 240 | 12 | 0 | 252 | 52 | 6.4272 | 0 | 58.4272 | 504 | 116.8544 | 620.8544 | 10 | 2 | 48 | 0 | 48 | 2.4 | 0 | 50.4 | 10.4 | 1.2854 | 0 | 11.6854 | 62.0854
3.2.5 | 502050000 | 4 core 4 sq. mm copper cabl | [8 empty] | Nos | 6 | 196 | 0 | 196 | 9.8 | 0 | 205.8 | 31 | 3.8316 | 0 | 34.8316 | 1234.8 | 208.9896 | 1443.7896 | 10 | 6 | 117.6 | 0 | 117.6 | 5.88 | 0 | 123.48 | 18.6 | 2.299 | 0 | 20.899 | 144.379
3.2.6 | 502050000 | 3 core 6 sq. mm copper cabl | [8 empty] | Nos | 10 | 171 | 0 | 171 | 8.55 | 0 | 179.55 | 31 | 3.8316 | 0 | 34.8316 | 1795.5 | 348.316 | 2143.816 | 10 | 10 | 171 | 0 | 171 | 8.55 | 0 | 179.55 | 31 | 3.8316 | 0 | 34.8316 | 214.3816
3.2.7 | 502050000 | 3 core 4 sq. mm copper cabl | [8 empty] | Nos | 12 | 156 | 0 | 156 | 7.8 | 0 | 163.8 | 31 | 3.8316 | 0 | 34.8316 | 1965.6 | 417.9792 | 2383.5792 | 10 | 12 | 187.2 | 0 | 187.2 | 9.36 | 0 | 196.56 | 37.2 | 4.5979 | 0 | 41.7979 | 238.3579
3.3 | 502050000 | Supply and fixing of factory fabricated Hot dip galvanized GI ladder type cable trays, with radial bends, suspenders and supports as per specification and of the following sizes. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.3.1 | 502050000 | 450 mm wide | [8 empty] | RM | 100 | 343 | 0 | 343 | 17.15 | 0 | 360.15 | 154 | 19.0344 | 0 | 173.0344 | 36015 | 17303.44 | 53318.44 | 10 | 100 | 3430 | 0 | 3430 | 171.5 | 0 | 3601.5 | 1540 | 190.344 | 0 | 1730.344 | 5331.844
3.4 | 502050000 | Supply and fixing of perforated type Hot dip galvanized GI cable trays with supports, hangers, fastners of the following sizes as per specification. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.4.1 | 502050000 | 150 mm wide | [8 empty] | RM | 50 | 122 | 0 | 122 | 6.1 | 0 | 128.1 | 103 | 12.7308 | 0 | 115.7308 | 6405 | 5786.54 | 12191.54 | 10 | 50 | 610 | 0 | 610 | 30.5 | 0 | 640.5 | 515 | 63.654 | 0 | 578.654 | 1219.154
3.4.2 | 502050000 | 300 mm wide | [8 empty] | RM | 50 | 245 | 0 | 245 | 12.25 | 0 | 257.25 | 154 | 19.0344 | 0 | 173.0344 | 12862.5 | 8651.72 | 21514.22 | 10 | 50 | 1225 | 0 | 1225 | 61.25 | 0 | 1286.25 | 770 | 95.172 | 0 | 865.172 | 2151.422
4 | 502050000 | Earthing for Plumbing & Fire Protection System | [8 empty] | Nil | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4.1 | 502050000 | Supply and fixing of bare GI tapes / wires including all necessary fixing accessories and effecting connections as per specifications. | [8 empty] | LOT | 1 | 24500 | 0 | 24500 | 1225 | 0 | 25725 | 5145 | 635.922 | 0 | 5780.922 | 25725 | 5780.922 | 31505.922 | 10 | 1 | 2450 | 0 | 2450 | 122.5 | 0 | 2572.5 | 514.5 | 63.5922 | 0 | 578.0922 | 3150.5922

## COP Fasheet
CHARTERED HOTELS PVT. LTD.
CERTIFICATE OF PAYMENT
COP No.:-HRL/COP/CEPL/161 |  |  |  |  | Date.:- 10/03/2015
Project Code:- |  | 006 |  |  | Not For Payment
Project:- |  | Proposed five star hotel at Lucknow
Work: | Supply, Installation, testing & commisioning of low side HVAC work |  |  | M/s CANTER ENGINEERS PVT LTD
Budget Code:- |  |  |  | 201,2ND Floor,Carnation Plaza Bldg,No.1Parijat Gardens,Ghodbunder Road,kasarwadavli Naka,Thane(west)400607
W.O. / P.O. No. & Date:- |  |  | CHPL/006/WO/14-15/0568 Dated : 19.05.2010 | PAN No.:- AACCC4796J
Original W.O. Value:- |  |  | 74567640.46 | VAT No.:- 29790851674 CST NO- Service Tax No:-
WO Amendment No.:- |  |  |  | Invoice No. dated
Amended or WO/PO Value:- |  |  | 74294634.9813
Balance Work Yet to be done |  |  | 65637037.6216
Sr. No. | Description of Work |  |  | Previous Certified Amount INR | Current Certified Amount INR | Cumulative Certified Amount INR
| Certificate Type:- |  |  |  | I
| Certificate No.:- |  |  |  | COP-R001
A | Work Done Amount
1 | Net Supply Amount (Basix + Excise) |  |  |  | 7125112.4 | 7125112.4
2 | Net Installation Amount |  |  |  | 1046839.925 | 1046839.925
3 | VAT / CST |  |  |  | 356255.62 | 356255.62
4 | Service Tax. |  |  |  | 129389.4147 | 129389.4147
5 | Other Payments -Supply and Installation |  |  |  | 0 | 0
A | Gross Amount for Work Done As per this Bill |  |  | 0 | 8657597.3597 | 8657597.3597
B | Recoveries:-
1 | Recovery of Advance (@13.333%) |  |  |  | 0
2 | Recovery of water Charges for Water Consumed |  |  |  | 0
3 | Recovery of Power ( For Electricity Consumed) |  |  |  | 0
4 | Recovery of Monthly Advance ( if any) |  |  |  | 0
5 | Recovery of unsecured Advance( Including Expired Bank Guarantee |  |  |  | 0
6 | Recovery of Insurance Premium |  |  |  | 0
7 | Debit for Non removing of debris |  |  |  | 0
8 | Retention Amount (as per Contract Conditions 5%) |  |  |  | 0
9 | Non Conformity of Concrete |  |  |  | 0
10 | Miscellaneous |  |  |  | 0
B | Total Gross Recoveries:- |  |  | 0 | 0 | 0
C | Other Payments |  |  |  | 0
1 | Mobilisation Advance |  |  |  | 0
2 | Ad-Hoc Certification |  |  |  | 0
3 | Secured Advance |  |  |  | 0
4 | Travel Reimbursement |  |  |  | 0
5 | Net Amount of Other Payments |  |  |  | 0
6 | Service Tax ON Other Payments, if any. |  |  |  | 0
C | Gross Amount for Other Payments |  |  | 0 | 0 | 0
| Gross Certified as Per This Bill A-B+C |  |  |  | 8657597.3597 | 8657597.3597
Rs. (In Words):
Mode of Payment:-
Remarks:-
Prepared By |  | Checked By |  | Approved By | Approved By
QS and Contracts |  | Asst.GM - Contracts |  | GM -Project | GM -Contracts
CHPL
CHPL
CHPL