## Order
Scenario 2
Local Supply | [22 empty] | 56562003
|  | UNIQUE IDENTIFIERS | [8 empty] | UOM | QTY | RATE (can be entered directly or summed up for totals)
Sr. No. | Item Range Code | Description | Area | Make | Model No./ Product Code | Tag/ Item No. | ITC HS Code | Country of Origin | Port of Loading | User defined column |  |  | Local supply rate
[13 empty] | Basic Rate | Excise | Subtotal = Basic + Excise | VAT/CST on Subtotal | Octroi / LBT | Insurance | Freight | Packing & Forwarding | Other | Supply Rate Total | AMOUNT
A. | 504010000 | EQUIPMENT (IMPORTED) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 504010000 | Testing and commissioning of multiple compressor SCREW WATER CHILLING UNITS each complete with 250 TR capacity (total) screw compressors with Constant speed Drive, motor, starter panel machine mounted with adaptor box consisting of tinned copper busbar suitable for termination of 2 nos 185 sqmm Al. Armoured cable , water cooled condenser, insulated chiller, flow switch at chiller and condenser, vibration isolators, integral refrigerant piping and wiring, BMS interface unit (Tracer / Microgateway / Datalink) grooved couplings for condenser and cooler water in/out connections, complete charge of refrigerant and oil, accessories as required and called for, automatic and safety controls mounted in central micro-processor based console panel and all mounted on a steel frame complete as per specifications. Motor shall be suitable for 415±10% 50 cycles. 3 phase AC supply and motor cable terminal box shall be suitable to connect Aluminium Cabling. Refrigerant used shall be Ozone friendly HFC-134a as detailed in specifications. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Chiller | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Chiller Water IN 53°F | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Chilled Water OUT 43°F | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Fouling factor 0.0005 FPS | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Condenser | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Condenser Water IN 88.4°F(Amb. Wet bulb+5.40F) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Condenser Water OUT 98.4°F(∆T of 10oF) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Fouling factor 0.001 FPS | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Maximum Power Consumed at design conditions : Not greater than 0.6 IkW/TR @100% Load | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Test Standard : 550/590-1998 | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.1 | 504010000 | Supply imported portion of above chillers CIF (Delhi). | [8 empty] | Nos. | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.2 | 504010000 | Indicate for all chillers port charges, port handling charges, other local duties, loading, transportation/insurance upto site, octroi charges and all other taxes and incidentals complete till delivered at site.l | [8 empty] | Nos. | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.3 | 504010000 | Customs duty and countervailing duty for the above imported equipment.i | [8 empty] | Nos | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.4 | 504010000 | Receiving at site above imported equipment, unloading, storing, handling hoisting, installing in position, effecting connections, anchoring, grouting testing and commissioning above equipment including supplying & installing all necessary indigenous accessories as required to complete the installation. | [8 empty] | Nos. | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 504010000 | Supplying of CENTRIFUGAL PUMPS, factory mounted on a common base with electric motor for recirculation of water for the central air conditioning system as per specifications. All pumps shall be aligned properly as required. The pump motor shall be suitable for 415 ± 10% volts, 50 cycles, 3 phase power supply. The motor selected shall be energy efficient having efficiency (EFF I) at full load ranging between 91.5% to 94% in accordance with motor rating as per specification. Minimum pump efficiency shall be 75%. The quoted price shall include cost of thermal insulation and cladding for item 2.1. Pumps with performance characteristics as given below : | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Primary Chilled water pumps | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Water flow rate = 600 USGPM | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Head = 45 Ft. of water | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Motor KW = 7.5 (10 HP). | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Quantity indicated includes one standby…. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.1 | 504010000 | Supply imported portion of above pumps CIF (Delhi) | [8 empty] | Nos | 3 | 79768 | 0 | 79768 | 3988.4 | 0 | 0 | 0 | 0 | 0 | 83756.4 | 251269
2.2 | 504010000 | Indicate for all chillers port charges, port handling charges, other local duties, loading, transportation/insurance upto site, octroi charges and all other taxes and incidentals complete till delivered at site… | [8 empty] | Nos | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.3 | 504010000 | Customs duty and countervailing duty for the above imported equipment…n | [8 empty] | Nos. | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.4 | 504010000 | Receiving at site above imported equipment, unloading, storing, handling hoisting, installing in position, effecting connections, anchoring, grouting testing and commissioning above equipment including supplying & installing all necessary indigenous accessories as required to complete the installation. | [8 empty] | Nos | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 504010000 | Supplying of CENTRIFUGAL PUMPS, factory mounted on a common base with electric motor for recirculation of cooling water for the central air conditioning system. All pumps shall be aligned properly as required as per specifications.Minimum efficiency of the pump shall be 75%. The pump motor shall be suitable for 415 ± 10% volts, 50 cycles, 3 phase power supply. The motor selected shall be energy efficient having efficiency (EFF 1) at full load ranging between 91.5% to 94% in accordance with motor rating as per specification. The performance shall be as given below : | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.1 | 504010000 | Condensing water pumps | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Water flow rate = 750 USGPM | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Head = 113 Ft. of water | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Motor KW = 30 (40 HP) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Quantity indicated includes one standby… | [8 empty] | Nos. | 3 | 154909 | 0 | 154909 | 7745.45 | 0 | 0 | 0 | 0 | 0 | 162654.45 | 487963
| 504010000 | Condensing water pumps - For Cold Storages in BOH | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Water flow rate = 300 USGPM | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Head = 80 Ft. of water | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Motor KW = 7.5 (10 HP) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Quantity indicated includes one standby.. | [8 empty] | Nos. | 2 | 92946 | 0 | 92946 | 4647.3 | 0 | 0 | 0 | 0 | 0 | 97593.3 | 195187
3.1.1 | 504010000 | Supply imported portion of above chillers CIF (Delhi) | [8 empty] | Nos | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.1.2 | 504010000 | Indicate for all chillers port charges, port handling charges, other local duties, loading, transportation/insurance upto site, octroi charges and all other taxes and incidentals complete till delivered at site. | [8 empty] | Nos | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.1.3 | 504010000 | Customs duty and countervailing duty for the above imported equipment… | [8 empty] | Nos. | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.1.4 | 504010000 | Receiving at site above imported equipment, unloading, storing, handling hoisting, installing in position, effecting connections, anchoring, grouting testing and commissioning above equipment including supplying & installing all necessary indigenous accessories as required to complete the installation. | [8 empty] | Nos | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 504010000 | Supplying of CENTRIFUGAL CASING PUMPS, factory mounted on a common base with electric motor for recirculation of water for the central air conditioning system as per specifications. Minimum pump hydraulic efficiency shall be 75%. All pumps shall be aligned properly as required. The pump motor shall be suitable for 415 + 10% volts, 50 cycles, 3 phase power supply. The motors of secondary chilled water pumps shall be suitable for operation on adjustable frequency drive. The motor selected shall be energy efficient having efficiency (Class I) at full load ranging between 91.5% to 94% in accordance with motor rating as per specification. The quoted price shall include cost of thermal insulation and cladding for item 12.1.1, 12.1.2 & 12.1.3. Pumps with performance characteristics as given below : | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4.1 | 504010000 | Supply imported portion of following pumps CIF Delhi | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4.1.1 | 504010000 | Secondary Chilled Water pumps | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Zone A | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Water flow rate = 400 USGPM | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Head = 70 Ft. of water | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Motor kW = 8.5 (12.5 HP) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Quantity indicated includes one standby.m | [8 empty] | Nos. | 3 | 94692 | 0 | 94692 | 4734.6 | 0 | 0 | 0 | 0 | 0 | 99426.6 | 298280
4.1.2 | 504010000 | Zone B | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Water flow rate = 600 USGPM | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Head = 75 Ft. of water | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Motor HP = 10 (15 HP) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Quantity indicated includes one standby. | [8 empty] | Nos. | 3 | 125291 | 0 | 125291 | 6264.55 | 0 | 0 | 0 | 0 | 0 | 131555.55 | 394667
4.2 | 504010000 | Indicate for all pumps port charges, port handling charges, other local duties, loading, transportation /insurance upto site, octroi charges and all other taxes and incidentals complete till delivered at site. | [8 empty] | Nos. | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4.3 | 504010000 | Customs duty and countervailing duty for the above imported equipment.o | [8 empty] | Nos. | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4.4 | 504010000 | Receiving at site above imported equipment, unloading, storing, handling hoisting, installing in position, effecting connections, anchoring, grouting testing and commissioning above equipment including supplying and installing all necessary indigenous accessories as required to complete the installation. | [8 empty] | Nos. | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 504010000 | Supplying of VARIABLE SPEED PUMPING SYSTEM consisting of adjustable frequency drive (AFD) for each pump, one dedicated microprocessor based pump controller per zone housed within the enclosure of one of the AFD with parallel pumping software duly down loaded and multiple differential pressure sensor / transmitters along with complete control cabling from transmitter to AFD Panel as per the site requirement. The entire system along with primary / secondary pumps as described under item 3 must be sourced from single manufacturer only, to ensure unit responsibility. Necessary factory test certificates for entire system shall be submitted along with the equipment. Sensor / Transmitters as described in specification. System shall be BMS compatible with open protocol communication port, so that complete data can be transported to remote IBMS console. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | The system shall be complete in all respects and suitable for following motor ratings : | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.1 | 504010000 | Supply Imported portion of AFD, Pump Controller & Sensor Transmitters CIF (Delhi) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.1.1 | 504010000 | 8.5 KW | [8 empty] | Nos. | 3 | 87968 | 0 | 87968 | 12315.52 | 0 | 0 | 0 | 0 | 0 | 100283.52 | 300851
5.1.2 | 504010000 | 10 KW | [8 empty] | Nos. | 3 | 98265 | 0 | 98265 | 13757.1 | 0 | 0 | 0 | 0 | 0 | 112022.1 | 336066
5.2 | 504010000 | Indicate for all equipment port charges, port handling charges, other local duties, loading, transportation/insurance upto site, octroi charges and all other taxes and incidentals complete till delivered at site. | [8 empty] | Nos. | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.3 | 504010000 | Customs duty and countervailing duty for the above imyported equipment. | [8 empty] | Nos. | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.4 | 504010000 | Receiving at site above imported equipment, unloading, storing, handling hoisting, installing in position, effecting connections, anchoring, grouting testing and commissioning above equipment including supplying & installing all necessary indigenous accessories as required to complete the installation. | [8 empty] | Nos. | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 504020000 | Installing, testing and commissioning of horizontal FAN COIL UNITS (2 PIPE SYSTEMS), blow thru type, each complete with 3 rows deep Chilled Water Coil, one or more centrifugal fans, cleanable fabric filters, main condensate extended SS drain pans, RA insulated plenum, as described in specifications, casing, coil piping connections, through copper pipes, condensate drain connections, wiring, control wiring in conduit upto thermostat boxes. Installation shall be considered with supply and installation of valve package comprising of pressure independent balancing cum control valve with integrated 2 way motorized actuator in a single body for modulating operation suitable for static pressure of 1600 kPa and actuator shall be capable of withstanding 400 kPa shut off pressure, 24 V AC incoming power supply, ball valve with Y-strainer at inlet & Ball valve at outlet and necessary copper coil piping connections. The actuator of modulating valve shall be provided with interface cards to receive 0-10V or 4-20 mA signal from Digital Thermostat. (Temporary bypass arrangement in chilled water line with related accesories to be considered to facililate flushing during precommissioning and commissioning of the system). cost shall include 4Cx10sqmm YRY cable from FCU to Thermostat (10 mtrs) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504020000 | The actuator of the valve shall have necessary torque to overcome pressure differential of 4 bars rating. All fan coil units shall be suitable for 220±6% volts, 50 cycles, single phase power supply. Fan coil units shall be of following refrigeration capacities as listed. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6.1 | 504020000 | Supply imported portion of above Fan Coil Units CIF (Delhi) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504020000 | Horizontal unit with cabinet (Ceiling Hung) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6.1.1 | 504020000 | 1.5 TR nominal capacity - 650 CFM | [8 empty] | Nos. | 246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6.1.2 | 504020000 | 2 TR nominal capacity - 850 CFM | [8 empty] | Nos. | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6.1.3 | 504020000 | 2.5 TR nominal capacity - 1050 CFM | [8 empty] | Nos. | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6.1.4 | 504020000 | 1.5 TR High Static - 650 CFM | [8 empty] | Nos. | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6.1.5 | 504020000 | 2 TR High Static - 850 CFM | [8 empty] | Nos. | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6.1.6 | 504020000 | 2.5 TR High Static - 1050 CFM | [8 empty] | Nos. | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6.2 | 504020000 | Installing in position, effecting connections, anchoring, grouting testing and commissioning above equipment including supplying & installing all necessary indigenous accessories as required to complete the installation. | [8 empty] | Nos. | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 504030000 | Supply of Electronic Self Balancing Valve pressure independent with independent type dynamic balancing valve for AHUs with integrated 2 way modulating control valves in a single body. The actuator shall be capable of accepting 2-10 VDC / 4-20 mA electric signal and shall provide similar transduced feedback output signal to control system for flow measurement. Contractor shall show actual flow measurement v/s flow indicated by valve for atleast 5% of the valves. Necessary instruments for manual flow measurement shall be included. The minimum close off pressure actuator must be 1.5 times shut off head of pump OR 5 bars whichever is maximum. The valves shall be suitable for following pipe sizes: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7.1 | 504030000 | Supply imported portion of the Electronic Self Balancing valve CIF (Delhi): | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7.1.1 | 504030000 | 100 mm dia pipes. | [8 empty] | Nos. | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7.1.2 | 504030000 | 80 mm dia pipes. | [8 empty] | Nos. | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7.1.3 | 504030000 | 65 mm dia pipes. | [8 empty] | Nos. | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7.1.4 | 504030000 | 50 mm dia pipes. | [8 empty] | Nos. | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7.1.5 | 504030000 | 40 mm dia pipes. | [8 empty] | Nos. | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7.1.6 | 504030000 | 32 mm dia pipes. | [8 empty] | Nos. | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7.2 | 504030000 | Indicate for all valves port charges, port handling charges, other local duties, loading, transportation /insurance upto site, octroi charges and all other taxes and incidentals complete till delivered at site. | [8 empty] | Nos. | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7.4 | 504030000 | Receiving at site above imported equipment, unloading, storing, handling hoisting, installing in position, effecting connections, anchoring, grouting testing and commissioning above equipment including supplying and installing all necessary indigenous accessories as required to complete the installation. | [8 empty] | Nos. | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8.1 | 504020000 | Supply imported portion of above Thermostats CIF (Delhi) for working in heating and cooling mode | [8 empty] | Nos. | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8.3 | 504020000 | Indicate for all thermostat port charges, port handling charges, other local duties, loading, transportation /insurance upto site, octroi charges and all other taxes and incidentals complete till delivered at site. | [8 empty] | Nos. | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8.5 | 504020000 | Receiving at site above imported equipment, unloading, storing, handling hoisting, installing in position, effecting connections, anchoring, grouting testing and commissioning above equipment including supplying and installing all necessary indigenous accessories as required to complete the installation. | [8 empty] | Nos. | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 504020000 | Supplying of the following PRESSURE INDEPENDENT AUTO BALANCING VALVES. For condenser and chiller | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.1 | 504020000 | Supply imported portion following automatic balancing valves CIF Delhi. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
a | 504020000 | 300 mm dia. | [8 empty] | Nos. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
b | 504020000 | 250 mm dia. | [8 empty] | Nos. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
c | 504020000 | 200 mm dia. | [8 empty] | Nos. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
d | 504020000 | 150 mm dia. | [8 empty] | Nos. | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
e | 504020000 | 125 mm dia. | [8 empty] | Nos. | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.2 | 504020000 | Indicate for all balancing valves port charges, port handling charges, other local duties, loading, transportation /insurance upto site, octroi charges and all other taxes and incidentals complete till delivered at site. | [8 empty] | Nos. | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.3 | 504020000 | Customs duty and countervailing duty for the abkove imported equipment. | [8 empty] | Nos. | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.4 | 504020000 | Receiving at site above imported equipment, unloading, storing, handling hoisting, installing in position, effecting connections, anchoring, grouting testing and commissioning above equipment including supplying & installing all necessary indigenous accessories as required to complete the installation. | [8 empty] | Nos. | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 504010000 | Supply of INDUCED DRAFT COOLING TOWERS. Fan and motor shall be suitable for VFD. Each tower shall be complete with basin, casing, distribution system, filling, louvers, ladder, fan and motor. Motor shall be suitable for 415±10% volts, 50 cycles, 3 phase power supply, Isolator panel with MCCB at cooling tower and earthing, shall also be included. Tower for airconditioning system shall be selected on the basis of ambient wet bulb 79 oF : Maximum approach accepted is 3 deg.c | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Cooling tower shall be of CTI certifed for assured thermal performace. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10.1 | 504010000 | Cooling tower (315 TR) for Water Cooled Screw chillers inlet temperature of 90°F and outlet temperature of 100 °F. | [8 empty] | Nos. | 3 | 499606 | 0 | 499606 | 69944.84 | 0 | 0 | 0 | 0 | 0 | 569550.84 | 1708653
10.2 | 504010000 | Supply imported portion of above Cooling Towers CIF (Delhi): | [8 empty] | Nos. | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10.3 | 504010000 | Indicate for all controls port charges, port handling charges, other local duties, loading, transportation /insurance upto site, octroi charges and all other taxes and incidentals complete till delivered at site. | [8 empty] | Nos. | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10.4 | 504010000 | Customs duty and countervailing duty f/or the above imported equipment. | [8 empty] | Nos. | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10.5 | 504010000 | Receiving at site above imported equipment, unloading, storing, handling hoisting, installing in position, effecting connections, anchoring, grouting testing and commissioning above equipment including supplying & installing all necessary indigenous accessories as required to complete the installation. | [8 empty] | Nos. | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 504030000 | Supply of HVAC dedicated VFDs with minimum IP 20 enclosures & disconnect, complying with the tender specifications and having: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Built-in dual 5% impedance DC link reactor (harmonic filters) on the positive and negative rails of the DC bus of the VFD. THdi shall be maintained < 5%. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Built-in EMC Filters (electromagnetic compatibility filters) for restriction of conducted emissions to comply with IEC61800: 3 (unrestricted distribution):2004 Category C 1 for 50 meters of cable length between motor & VFD, | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Automatic Energy Optimization / Load dependent flux optimization functionality for maximum energy savings. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | MODBUS RTU as the communication protocol between BMS & VFDs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11.1 | 504030000 | The system shall be complete in all respects and suitable for following motor rating: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | SPACE EQUIPMENT NO. MOTOR HP QTY | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Basement-2 Corridor B3-AH-01 5 1 | [8 empty] | Nos. | 1 | 28926 | 0 | 28926 | 4049.64 | 0 | 0 | 0 | 0 | 0 | 32975.64 | 32976
| 504030000 | Pre-Function MF-AH-02 7.5 1 | [8 empty] | Nos. | 1 | 33094 | 0 | 33094 | 4633.16 | 0 | 0 | 0 | 0 | 0 | 37727.16 | 37727
| 504030000 | Ballroom MF-AH-01 10 1 | [8 empty] | Nos. | 1 | 38117 | 0 | 38117 | 5336.38 | 0 | 0 | 0 | 0 | 0 | 43453.38 | 43453
| 504030000 | Lift Lobby / Break-out TF-AH-05 5 1 | [8 empty] | Nos. | 1 | 28926 | 0 | 28926 | 4049.64 | 0 | 0 | 0 | 0 | 0 | 32975.64 | 32976
| 504030000 | Lift Lobby / Reception TF-AH-06 5 1 | [8 empty] | Nos. | 1 | 28926 | 0 | 28926 | 4049.64 | 0 | 0 | 0 | 0 | 0 | 32975.64 | 32976
| 504030000 | Italian Restaurant TF-AH-07 7.5 1 | [8 empty] | Nos. | 1 | 33094 | 0 | 33094 | 4633.16 | 0 | 0 | 0 | 0 | 0 | 37727.16 | 37727
| 504030000 | Chiness Restaurant TF-AH-01 7.5 1 | [8 empty] | Nos. | 1 | 33094 | 0 | 33094 | 4633.16 | 0 | 0 | 0 | 0 | 0 | 37727.16 | 37727
| 504030000 | Lounge / Bar TF-AH-03 7.5 1 | [8 empty] | Nos. | 1 | 33094 | 0 | 33094 | 4633.16 | 0 | 0 | 0 | 0 | 0 | 37727.16 | 37727
| 504030000 | Regency Club PTF-AH-01 5 1 | [8 empty] | Nos. | 1 | 28926 | 0 | 28926 | 4049.64 | 0 | 0 | 0 | 0 | 0 | 32975.64 | 32976
| 504030000 | Cooling Tower 12.5 | [8 empty] | Nos. | 4 | 45277 | 0 | 45277 | 6338.78 | 0 | 0 | 0 | 0 | 0 | 51615.78 | 206463
11.2 | 504030000 | Indicate for all VFD system port charges , port handling charges, other local duties, loading, transportation / insurance upto site, octroi charges and all other taxes and incidentals complete till delivered at site | [8 empty] | Nos. | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11.3 | 504030000 | Customs duty and countervailing duty for the above imported equipment. | [8 empty] | Nos. | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11.4 | 504030000 | Receiving at site above imported equipment, unloading, storing, handling hoisting, installing in position, effecting connections, anchoring, grouting testing and commissioning above equipment including supplying & installing all necessary indigenous accessories as required to complete the installation. | [8 empty] | Nos. | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
B. | 504030000 | EQUIPMENT , | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 504030000 | Supplying of Open type chilled WATER EXPANSION TANK with outdoor weather protected insulation suitable for total volume of water in chilled water circuits along with necessary accessories such as centrifugal air separator, pumps etc. in order to keep chilled water system under (+) pressure and to prevent entrapment of pressure and to prevent entrapment of air in the system. The tank shall be precharged steel expansion tank with replaceable heavy duty butyl rubber bladder. The tank shall have 50 MM system connection and 20 mm drain and charging valve connection to facilitate the on site charging of the tank to meet system requirement. The tank shall be fitted with lifting rings and a floor mounting skirt for vertical installation. The tank and air separator must be constructed in accordance with section VIII of the ASME Boiler and pressure vessel (Unfired)code and stamped 175 PSI working pressure. The complete system shall be sourced from single manufacturer and supplied and installed with all accessories and safety fixtures and safety fixtures required for proper functioning of the complete hydronic system. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Capacity - 2.0 cu.mtr and static head of approximately 75 mtrs | [8 empty] | Nos. | 1 | 44354 | 0 | 44354 | 2217.7 | 0 | 0 | 0 | 0 | 0 | 46571.7 | 46572
2 | 504030000 | Supplying of AHU WITH INTEGRAL HEAT RECOVERY PIPE SECTION double skin construction with Thermal Break Profile as per specification. The unit shall comprise of DIDW airfoil backward curve fan with motor and drive package exhaust air, heat pipe section, internal bypass damper for non-fresh air component of return air, and exhaust air VCD for exhaust air and chilled water as per required parameters as listed below. The fan for exhaust air shall be sized for total return air quantity and shall be installed on the exhaust air side of the Heat pipes. The heat pipes shall be installed in vertical position. The exhaust air fan will draw return air from the air-conditioned area and blow it through the heat pipes where transfer of sensible and latent cooling to incoming fresh air shall take place. A bypass damper will allow the non-fresh air component of return air to re-enter the main AHU up stream of the prefilter, while the remaining quantity shall be exhausted. A second volume control damper shall be provided at the exit of heat recovery section to help control the air quantities. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | All VCDs shall be of non leak type. Heat pipes shall be complete with required charge and intercoil connecting piping. AIR HANDLING UNIT Section as per AHU specification, each complete with pre-filter section (90% down to 10 microns), min 6 Row Deep water coil of copper tube & aluminium fins construction,squirrel cage induction motor, airfoil centrifugal fan belt drive and vibration isolators, coil size shall be selected for a maximum face velocity of 500 feet/minute and static pressure shall be as indicated. The motor selected shall be energy efficient having efficiency (EFF 1) at full load ranging between 82.5% to 92% in accordance with motor rating as per specification. Motor shall be suitable for 415±10% volts, 50 cycles, 3 phase AC supply. Fan motor assembly (as whole) shall be statically and dynamically balanced to grade G 6.3 as per ISO-1940/AMCA 204-3. All units shall be complete with opposed blade volume control dampers at oulet, return and fresh air connections. Duct flexible connector (fire proof) shall be provided at outlets and return connection of AHU. For AHUs with VFD, complete equipment shall be designed to limit THDi to less than 5%. Heat pipe medium of heat trasfer shall be water only. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Design conditions shall be as follows | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Fresh Air | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1. DB - 109 deg F (Summer) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 2. WB - 79 deg F(Summer) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1. DB - 94 deg F (Monsoon) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 2. WB - 83 deg F(Monsoon) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Exhaus/Return Air Temp. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1. DB - 75 deg F | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 2. WB - 60 deg F | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Inside design Conditions | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1. DB - 72 deg F | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 2. WB - 60.1deg F | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.1 | 504030000 | AHU Tag: MF-AH-02 (PRE-FUNCTION) (With Mixing box, Thermal break profile & 25mm Panel thickness) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Dehumidified Air Quantity: 9200 CFM | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Cooling Capacity: 41 TR | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Fresh Air Qty: 4100 cfm | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | External Static Pressure: 50 mm | [8 empty] | No. | 1 | 343802 | 0 | 343802 | 48132.28 | 0 |  |  |  |  | 391934.28 | 391934
| 504030000 | Motor HP: 7.5 HP | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Floor Mounted 6 Row Deep Coil | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.1a | 504030000 | Water based heat pipe section for the item 2.1 | [8 empty] | No. | 1 |  | 0 | 0 |  | 0 |  |  |  |  | 0 | 0
2.1b | 504030000 | Indicate for all (Pre-Function MF- AH-02 Heat Pipe) port charges, port handling charges, other local duties, loading, transportation /insurance upto site, octroi charges and all other taxes and incidentals complete till delivered at site. | [8 empty] | No. | 1 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.1c | 504030000 | Customs duty and countervailing duty for the above imported equipment.- (Pre Fuction AH-02 Heat Pipe) | [8 empty] | Nos. | 1 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.2 | 504030000 | AHU Tag: MF-AH-01 (BALLROOM) (Without Mixing box and Thermal break profile & with 25mm Panel thickness) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Dehumidified Air Quantity: 14800 CFM | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Cooling Capacity: 51.0 TR | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Fresh Air Qty: 3200 cfm | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | External Static Pressure: 50mm/ | [8 empty] | No. | 1 | 509534 | 0 | 509534 | 71334.76 | 0 | 0 | 0 | 0 | 0 | 580868.76 | 580869
| 504030000 | Motor HP: 10 HP | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Floor Mounted 6 Row Deep Coil | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.2a | 504030000 | Water based heat pipe section for the item 2.2 | [8 empty] | No. | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.2b | 504030000 | Indicate for all (Ball Room MF-AH-01 Heat Pipe) port charges, port handling charges, other local duties, loading, transportation /insurance upto site, octroi charges and all other taxes and incidentals complete till delivered at site. | [8 empty] | No. | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.2c | 504030000 | Customs duty and countervailing duty for the above imported equipment.- (Ball Room AH-01 Heat Pipe) | [8 empty] | Nos. | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.3 | 504030000 | AHU Tag: TF-AH-01 (CHINESE RESTAURANT) (With Mixing box, Thermal break profile & 25mm Panel thickness) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Dehumidified Air Quantity: 8550 CFM | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Cooling Capacity: 21.0 TR | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Fresh Air Qty: 1015 cfm | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | External Static Pressure: 50mm | [8 empty] | No. | 1 | 302782 | 0 | 302782 | 42389.48 | 0 | 0 | 0 | 0 | 0 | 345171.48 | 345171
| 504030000 | Motor HP: 7.5 HP | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Floor Mounted 6 Row Deep Coil | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.3a | 504030000 | Water based heat pipe section for the item 2.3 | [8 empty] | No. | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.3b | 504030000 | Indicate for all (Chinese Restaurant TF-AH-01 Heat Pipe) port charges, port handling charges, other local duties, loading, transportation /insurance upto site, octroi charges and all other taxes and incidentals complete till delivered at site. | [8 empty] | No. | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.3c | 504030000 | Customs duty and countervailing duty for the above imported equipment.- (Chinese Restaurant AH-01 Heat Pipe) | [8 empty] | Nos. | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.4 | 504030000 | AHU Tag: TF-AH-03 (LOBBY LOUNGE & BAR) (With Mixing box, Thermal break profile & 25mm Panel thickness) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Dehumidified Air Quantity: 7600 CFM | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Cooling Capacity: 18.0 TR | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Fresh Air Qty: 800 cfm | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | External Static Pressure: 50mmm | [8 empty] | No. | 1 | 288480 | 0 | 288480 | 40387.2 | 0 | 0 | 0 | 0 | 0 | 328867.2 | 328867
| 504030000 | Motor HP: 7.5 HP | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Floor Mounted 6 Row Deep Coil | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.4a | 504030000 | Water based heat pipe section for the item 2.4 | [8 empty] | No. | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.4b | 504030000 | Indicate for all (Lobby Lounge & Bar TF-AH-03 Heat Pipe) port charges, port handling charges, other local duties, loading, transportation /insurance upto site, octroi charges and all other taxes and incidentals complete till delivered at site. | [8 empty] | No. | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.4c | 504030000 | Customs duty and countervailing duty for the above imported equipment.- (Lobby Lounge & Bar AH-03 Heat Pipe) | [8 empty] | Nos. | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.5 | 504030000 | AHU Tag: TF-AH-07 (ITALIAN RESTAURANT) (With Mixing box, Thermal break profile & 25mm Panel thickness) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Dehumidified Air Quantity: 9700 CFM | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Cooling Capacity: 28.0 TR | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Fresh Air Qty: 1800 cfm | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | External Static Pressure: 50mm2 | [8 empty] | No. | 1 | 355118 | 0 | 355118 | 49716.52 | 0 | 0 | 0 | 0 | 0 | 404834.52 | 404835
| 504030000 | Motor HP: 7.5 HP | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Floor Mounted 6 Row Deep Coil | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.5b | 504030000 | Indicate for all (Italian Restaurant & Bar TF-AH-07 Heat Pipe) port charges, port handling charges, other local duties, loading, transportation /insurance upto site, octroi charges and all other taxes and incidentals complete till delivered at site. | [8 empty] | No. | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.5c | 504030000 | Customs duty and countervailing duty for the above imported equipment.- (Italian Restaurant AH-07 Heat Pipe) | [8 empty] | Nos. | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 504030000 | Supplying of double skin construction draw thru type AIR HANDLING UNITS with Thermal Break Profile as per specification, each complete with pre-filter section (90% down to 10 microns), 6 Row Deep water coil of copper tube & aluminium fins construction , squirrel cage induction motor, airfoil centrifugal fan belt drive and vibration isolators, coil size shall be selected for a maximum face velocity of 500 feet/minute and static pressure shall be as indicated. The motor selected shall be energy efficient having efficiency (EFF I) at full load ranging between 82.5% to 92% in accordance with motor rating as per specification. Motor shall be suitable for 415±10% volts, 50 cycles, 3 phase AC supply. Fan motor assembly (as whole) shall be statically and dynamically balanced to grade G 6.3 as per ISO-1940/AMCA 204-3.All units shall be complete with opposed blade volume control dampers at oulet, return and fresh air connections. Duct flexible connector (fire proof) shall be provided at outlets and return connection of AHU. For AHUs with VFD, complete equipment shall be designed to limit THDi to less than 5%. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1EMPLOYEES CAFÉB2-AH-0130002150800403Floor Mounted 6 RD Coil, 25mm Panel thickness, No Mixing box & No Thermal break profile | [8 empty] | Nos. | 1 | 75991 | 0 | 75991 | 10638.74 | 0 | 0 | 0 | 0 | 0 | 86629.74 | 86630
| 504030000 | 2F&B OfficesB2-AH-0222003006402Floor Mounted 6 RD Coil, 25mm Panel thickness, No Mixing box & No Thermal break profile | [8 empty] | Nos. | 1 | 67504 | 0 | 67504 | 9450.56 | 0 | 0 | 0 | 0 | 0 | 76954.56 | 76955
| 504030000 | 3HR OfficesB2-AH-0325003506.5403Floor Mounted 6 RD Coil, 25mm Panel thickness, No Mixing box & No Thermal break profile | [8 empty] | Nos. | 1 | 69940 | 0 | 69940 | 9791.6 | 0 | 0 | 0 | 0 | 0 | 79731.6 | 79732
| 504030000 | 4CoridorB3-AH-015400240013405Floor Mounted 6 RD Coil, 25mm Panel thickness, No Mixing box & No Thermal break profile | [8 empty] | Nos. | 1 | 112689 | 0 | 112689 | 15776.46 | 0 | 0 | 0 | 0 | 0 | 128465.46 | 128465
| 504030000 | BASEMENT-1 | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1Commissary KitchenB1-AH-016400113017403Floor Mounted 6 RD Coil, 25mm Panel thickness, Thermal break profile & Mixing Box | [8 empty] | Nos. | 1 | 144594 | 0 | 144594 | 20243.16 | 0 | 0 | 0 | 0 | 0 | 164837.16 | 164837
| 504030000 | GROUND FLOOR | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1LoungeGF-AH-0129004007403Floor Mounted 6 RD Coil, 25mm Panel thickness, Thermal break profile & Mixing Box | [8 empty] | Nos. | 1 | 88249 | 0 | 88249 | 12354.86 | 0 | 0 | 0 | 0 | 0 | 100603.86 | 100604
| 504030000 | 2Banquet KitchenGF-TFA-013600180016403Floor Mounted 6 RD Coil, 25mm Panel thickness, Thermal break profile & Mixing Box | [8 empty] | Nos. | 1 | 99173 | 0 | 99173 | 13884.22 | 0 | 0 | 0 | 0 | 0 | 113057.22 | 113057
| 504030000 | MEZZANINE FLOOR | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1Lift LobbyTF-AH-05470095012405Floor Mounted 6 RD Coil, 25mm Panel thickness, Thermal break profile & Mixing Box | [8 empty] | Nos. | 1 | 119368 | 0 | 119368 | 16711.52 | 0 | 0 | 0 | 0 | 0 | 136079.52 | 136080
| 504030000 | 2Meeting Room 3MF-AH-03350075012505Floor Mounted 6 RD Coil, 25mm Panel thickness, Thermal break profile & Mixing Box | [8 empty] | Nos. | 1 | 98387 | 0 | 98387 | 13774.18 | 0 | 0 | 0 | 0 | 0 | 112161.18 | 112161
| 504030000 | FIRST FLOOR | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1ReceptionTF-AH-06430060010405Floor Mounted 6 RD Coil, 25mm Panel thickness, Thermal break profile & Mixing Box | [8 empty] | Nos. | 1 | 109310 | 0 | 109310 | 15303.4 | 0 | 0 | 0 | 0 | 0 | 124613.4 | 124613
| 504030000 | 2Display KitchenTF-TFA-01400090011405Floor Mounted 6 RD Coil, 25mm Panel thickness, Thermal break profile & Mixing Box | [8 empty] | Nos. | 1 | 102473 | 0 | 102473 | 14346.22 | 0 | 0 | 0 | 0 | 0 | 116819.22 | 116819
| 504030000 | 3Restaurant KitchenTF-TFA-02400090011405Floor Mounted 6 RD Coil, 25mm Panel thickness, Thermal break profile & Mixing Box | [8 empty] | Nos. | 1 | 102473 | 0 | 102473 | 14346.22 | 0 | 0 | 0 | 0 | 0 | 116819.22 | 116819
| 504030000 | SECOND FLOOR | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1Office CorridorTF-AH-04250012009303Floor Mounted 6 RD Coil, 25mm Panel thickness, Thermal break profile & Mixing Box | [8 empty] | Nos. | 1 | 81884 | 0 | 81884 | 11463.76 | 0 | 0 | 0 | 0 | 0 | 93347.76 | 93348
| 504030000 | 2SpaTF-AH-02755040013403Floor Mounted 6 RD Coil, 25mm Panel thickness, Thermal break profile & Mixing Box | [8 empty] | Nos. | 1 | 173827 | 0 | 173827 | 24335.78 | 0 | 0 | 0 | 0 | 0 | 198162.78 | 198163
| 504030000 | 3Gym / AerobicTF-AH-0837005009403Floor Mounted 6 RD Coil, 25mm Panel thickness, Thermal break profile & Mixing Box | [8 empty] | Nos. | 1 | 100037 | 0 | 100037 | 14005.18 | 0 | 0 | 0 | 0 | 0 | 114042.18 | 114042
| 504030000 | PENTHOUSE FLOOR | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1Regency ClubPTF-AH-01505095015405Floor Mounted 6 RD Coil, 50mm Panel thickness, Thermal break profile & Mixing Box | [8 empty] | Nos. | 1 | 123612 | 0 | 123612 | 17305.68 | 0 | 0 | 0 | 0 | 0 | 140917.68 | 140918
4 | 504030000 | Supplying of HEAT RECOVERY UNIT (HRU) 50mm thick double skin construction with Thermal Break Profile as per specification, each complete with pre-filter section (90% down to 10 microns), min 8 Row Deep water coil of copper tube & aluminium fins construction. The coil shall be sized for the actual capacity considering with out heat recovery unit. The unit shall comprise of filter section, heat recovery unit, fresh air inlet / exhaust air outlet, fan section with DIDW fan with motor and drive package. The unit shall be installed above main AHU and interconnected in a manner so as to receive part return air thru public area which shall be passed through HRW and transfer sensible and latent cooling to incoming fresh air. The precooled fresh air shall be let into the mixing box of the main AHU and return air is exhausted outdoors. The exhaust section of the unit shall be provided with motor actuated GSS damper duly interlocked with the fan. Minimum sensible and latent heat transfer efficiency of heat recovery unit shall be 80%. For units with VFD, complete equipment shall be designed to limit THDi to less than 5% | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Design conditions shall be as follows | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Fresh Air | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1. DB - 109 deg F | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 2. WB - 79 deg F | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Return Air Temp. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1. DB - 77.0 deg F | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 2. WB - 65.7 deg F | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Air moving capacity shall be as follows : | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | SR.SPACETAG. NO.FRESH AIRMOTOR EXHAUST MOTOR ACTUAL AIR | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | NO.CFMHP CFM HP TR | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1FOR GUEST FLOORPTF-TFA-HRW-011700012.5 5475 5 106 | [8 empty] | Nos. | 1 | 604149 | 0 | 604149 | 84580.86 | 0 | 0 | 0 | 0 | 0 | 688729.86 | 688730
| 504030000 | 2FOR GUEST FLOORPTF-TFA-HRW-021700012.5 5475 5 106 | [8 empty] | Nos. | 1 | 604149 | 0 | 604149 | 84580.86 | 0 | 0 | 0 | 0 | 0 | 688729.86 | 688730
5 | 504030000 | Supply of micro-processor controlled precision air-conditioning unit with scroll compressor(s) on HFC-134a / HFC-410a, air cooled condenser with installation stand, insulated refrigerant piping with supports, cooling coil, electrical heating coil, steam humidifier, necessary measuring and control devices, evaporator fan with motor, pre and micro-vee filters and inbuilt starter. Power will be provided by other agency near the indoor unit inbuilt starter. Power and control cabling from indoor to outdoor unit along with supports / cable trays shall be included. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.1 | 504030000 | 5 TR | [8 empty] | Nos. | 1 | 391897 | 0 | 391897 | 54865.58 | 0 | 0 | 0 | 0 | 0 | 446762.58 | 446763
| 504030000 | [9 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.2 | 504030000 | 10 TR | [8 empty] | Nos. | 1 | 516321 | 0 | 516321 | 72284.94 | 0 | 0 | 0 | 0 | 0 | 588605.94 | 588606
6 | 504030000 | Supply of wall mounted air cooled split air conditioning units as described in specifications. The unit shall be complete with decorative type fan coil unit and external condensing unit, complete in all respects, inclusive of copper refrigerant piping of 10mtr length, GI condensate drain piping, valves and insulation quoted price shall include cost of cooling thermostat, power wiring, control wiring and earthing. The unit capacities shall be as follows: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Note : Fins and copper tubes of Air Cooled Condenser alongwith copper tubing / piping with all joints and U-Bends exposed to coastal areas corrosive atmosphere / aggressive ambient, shall be painted with special corrosion prevention coating either in factory or at site. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6.1 | 504030000 | 1.5TR split air conditioning system | [8 empty] | Nos. | 1 | 38100 | 0 | 38100 | 5334 | 0 | 0 | 0 | 0 | 0 | 43434 | 43434
6.2 | 504030000 | 2TR split air conditioning system | [8 empty] | Nos. | 1 | 42100 | 0 | 42100 | 5894 | 0 | 0 | 0 | 0 | 0 | 47994 | 47994
6.3 | 504030000 | 2.5TR split air conditioning system | [8 empty] | Nos. | 1 | 68100 | 0 | 68100 | 9534 | 0 | 0 | 0 | 0 | 0 | 77634 | 77634
7 | 504030000 | Supplying of AIR HANDLING UNITS ( FAN SECTIONS ONLY)with 25mm thick double skin construction as per specificatopns, each complete with squirrel cage induction motor (mounted internally), airfoil centrifugal fan belt drive and vibrations isolators.Motors shall be suitable for 415 +- 10% volts, 50 cycles , 3 phase AC supply an static pressure shall be as indicated . Fan-motor assembly (as whole) shall be statically & dynamically balanced to grade G6.3 as per ISO-1940/AMCA 204-3. All AHUS (Fan sections) shall be suitable for outdoor duty and complete with duct flexible connections and volume control damper . In additional all supply fans (SF) shall be provided with prefilter | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Note EF- Exhaust Fan , SF - Supply Fan | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | SR. NO.SPACEFanCFMSPMotorType | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | TagmmHP | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | BASEMENT-3 | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1STPB3-EF-018400655Outdoor type mounted at terrace level | [8 empty] | Nos. | 1 | 89743 | 0 | 89743 | 12564.02 | 0 | 0 | 0 | 0 | 0 | 102307.02 | 102307
| 504030000 | 2STPB3-FF-017200405Loft Mounted | [8 empty] | Nos. | 1 | 79291 | 0 | 79291 | 11100.74 | 0 | 0 | 0 | 0 | 0 | 90391.74 | 90392
| 504030000 | 3HVAC PlantroomB3-EF-02137004010Loft Mounted | [8 empty] | Nos. | 1 | 151430 | 0 | 151430 | 21200.2 | 0 | 0 | 0 | 0 | 0 | 172630.2 | 172630
| 504030000 | 4HVAC PlantroomB3-FF-0211000407.5Loft Mounted | [8 empty] | Nos. | 1 | 112610 | 0 | 112610 | 15765.4 | 0 | 0 | 0 | 0 | 0 | 128375.4 | 128375
| 504030000 | 5Plumbing PlantroomB3-EF-0310000407.5Loft Mounted | [8 empty] | Nos. | 1 | 97915 | 0 | 97915 | 13708.1 | 0 | 0 | 0 | 0 | 0 | 111623.1 | 111623
| 504030000 | 6Plumbing PlantroomB3-FF-038700405Loft Mounted | [8 empty] | Nos. | 1 | 86678 | 0 | 86678 | 12134.92 | 0 | 0 | 0 | 0 | 0 | 98812.92 | 98813
| 504030000 | 7Hot Water Plant roomB3-FF-049800405Loft Mounted | [8 empty] | RO | 0 | 100980 | 0 | 100980 |  | 0 | 0 | 0 | 0 | 0 | 100980 | 0
| 504030000 | BASEMENT-2 | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1LaundryB2-FF-047000405Loft Mounted | [8 empty] | RO | 0 | 79291 | 0 | 79291 | 11100.74 | 0 | 0 | 0 | 0 | 0 | 90391.74 | 0
| 504030000 | 2Employees Cafe KitchenB2-FF-035000403Loft Mounted | [8 empty] | RO | 0 | 58388 | 0 | 58388 | 8174.32 | 0 | 0 | 0 | 0 | 0 | 66562.32 | 0
| 504030000 | BASEMENT-1 | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1Commissary KitchenB1-FF-019000605Loft Mounted | [8 empty] | RO | 0 | 107109 | 0 | 107109 | 14995.26 | 0 | 0 | 0 | 0 | 0 | 122104.26 | 0
| 504030000 | 2Boiler RoomB1-FF-023700403Ceiling Suspended | [8 empty] | RO | 0 | 42200 | 0 | 42200 | 5908 | 0 | 0 | 0 | 0 | 0 | 48108 | 0
| 504030000 | GROUND FLOOR | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1Banquet KitchenGF-FF-01160005010Loft Mounted | [8 empty] | RO | 0 | 160075 | 0 | 160075 | 22410.5 | 0 | 0 | 0 | 0 | 0 | 182485.5 | 0
| 504030000 | FIRST FLOOR | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1Italian KitchenTF-TFA-012400405Floor Mounted | [8 empty] | RO | 0 | 43929 | 0 | 43929 | 6150.06 | 0 | 0 | 0 | 0 | 0 | 50079.06 | 0
| 504030000 | 2All Day Dining Kitchen / TF-FF-0112000507.5Floor Mounted | [8 empty] | RO | 0 | 123062 | 0 | 123062 | 17228.68 | 0 | 0 | 0 | 0 | 0 | 140290.68 | 0
| 504030000 | Chineese Kitchen | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Transfer Floor | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1Transfer FloorTF-EF-09200003012.5Floor Mounted | [8 empty] | Nos. | 1 | 205417 | 0 | 205417 | 28758.38 | 0 | 0 | 0 | 0 | 0 | 234175.38 | 234175
| 504030000 | 2Transfer FloorTF-FF-0210000307.5Floor Mounted | [8 empty] | Nos. | 1 | 100980 | 0 | 100980 | 14137.2 | 0 | 0 | 0 | 0 | 0 | 115117.2 | 115117
| 504030000 | 3Transfer FloorTF-FF-0310000307.5Floor Mounted | [8 empty] | Nos. | 1 | 100980 | 0 | 100980 | 14137.2 | 0 | 0 | 0 | 0 | 0 | 115117.2 | 115117
8 | 504030000 | Supplying of Smoke spill fans as per specifications.Fan shall be direct driven.Fan and casing shall be suitable for smoke exhaust application.Motor and belt drive shall be mounted outside ,so that it is not exposed to smoke stream & thermally rated for 2500C for 2 hours as per [BS EN 12101-3:2002] Class-B. Motors shall be suitable for 415+10% volts, 50 cycles , 3 phase AC supply an static pressure shall be as indicated . Fans shall be activated from fire signal from fire alarm system .Fan shall be with flexible fire proof flexibel connection at inlet and outlet | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | [9 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | SR. NO.SPACEFanCFMSPMotorType | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | TagmmHP | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | BASEMENT-3 | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1Car Parking Exhaust FanB3-EF-05340004025Tube axial flow fan | [8 empty] | Nos. | 2 | 127474 | 0 | 127474 | 17846.36 | 0 | 0 | 0 | 0 | 0 | 145320.36 | 290641
| 504030000 | 2Hot Water PlantroomB3-EF-0411400407.5Loft Mounted centrifugal cabinet fan | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | BASEMENT-2 | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1Car Parking Exhaust FanB2-EF-01340004025Tube axial flow fan | [8 empty] | Nos. | 2 | 127474 | 0 | 127474 | 17846.36 | 0 | 0 | 0 | 0 | 0 | 145320.36 | 290641
| 504030000 | 2LaundryPTF-EF-018000605Loft Mounted centrifugal cabinet fan | [8 empty] | Nos. | 1 | 117600 | 0 | 117600 | 16464 | 0 | 0 | 0 | 0 | 0 | 134064 | 134064
| 504030000 | 3Employees Cafe KitchenB1-EF-056650907.5SISW Outdoor type at terrace level | [8 empty] | Nos. | 1 | 85559 | 0 | 85559 | 11978.26 | 0 | 0 | 0 | 0 | 0 | 97537.26 | 97537
| 504030000 | BASEMENT-1 | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1Car Parking Exhaust FanB1-EF-03200004015Tube axial flow fan | [8 empty] | Nos. | 2 | 77544 | 0 | 77544 | 10856.16 | 0 | 0 | 0 | 0 | 0 | 88400.16 | 176800
| 504030000 | 2Commissary KitchenB1-EF-0110000907.5SISW Outdoor type at terrace level | [8 empty] | Nos. | 1 | 110178 | 0 | 110178 | 15424.92 | 0 | 0 | 0 | 0 | 0 | 125602.92 | 125603
| 504030000 | 3Boiler RoomB1-EF-024400603Ceiling Suspended Centrifugal cabinet fan | [8 empty] | Nos. | 1 | 79429 | 0 | 79429 | 11120.06 | 0 | 0 | 0 | 0 | 0 | 90549.06 | 90549
| 504030000 | 1Chineese Display KitchenTF-FF-0310250905SISW Floor Mounted | [8 empty] | Nos. | 1 | 135566 | 0 | 135566 | 18979.24 | 0 | 0 | 0 | 0 | 0 | 154545.24 | 154545
| 504030000 | 2Italian Restaurant KitchenTF-FF-043000905SISW Floor Mounted | [8 empty] | Nos. | 1 | 51137 | 0 | 51137 | 7159.18 | 0 | 0 | 0 | 0 | 0 | 58296.18 | 58296
| 504030000 | 3All Day Dining KitchenTF-FF-0513000907.5SISW Floor Mounted | [8 empty] | Nos. | 1 | 164093 | 0 | 164093 | 22973.02 | 0 | 0 | 0 | 0 | 0 | 187066.02 | 187066
| 504030000 | 4Banquet KitchenTF-EF-02200009015SISW Outdoor type at terrace level | [8 empty] | Nos. | 1 | 197504 | 0 | 197504 | 27650.56 | 0 | 0 | 0 | 0 | 0 | 225154.56 | 225155
| 504030000 | PENTHOUSE TERRACE FLOORn | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1Smoke EvacuationPTF-EF-026800405SISW Floor Mounted | [8 empty] | Nos. | 1 | 82579 | 0 | 82579 | 11561.06 | 0 | 0 | 0 | 0 | 0 | 94140.06 | 94140
9 | 504030000 | Supplying of INLINE FANS suitable for installing in any position in vertical or horizontal ducts. The casing shall be double skin, internally acoustically lined and constructed of galvanised steel. The fan shall be DIDW with forward curve impeller fitted with maintenance free external rotor motor. The motor shall be suitable for 220±10% volt single phase 50 cycles AC supply. All units shall be complete with duct flexible connector and volume control damper. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | The fan shall have low sound level exceeding not more than 40 DBA at three metre distance. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | SR. NO.SPACEFanCFMSPMotorType | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | TagmmHP | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | BASEMENT-2 | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1Dishwash AreaB2-EF-03600301.5Ceiling Suspended | [8 empty] | Nos. | 1 | 48903 | 0 | 48903 | 6846.42 | 0 | 0 | 0 | 0 | 0 | 55749.42 | 55749
| 504030000 | 2Toilet exhaustB1-EF-06850301.5Ceiling Suspended | [8 empty] | Nos. | 1 | 49486 | 0 | 49486 | 6928.04 | 0 | 0 | 0 | 0 | 0 | 56414.04 | 56414
| 504030000 | GROUND FLOOR | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1Toilet exhaustGF-EF-02800301.5Ceiling Suspended | [8 empty] | Nos. | 1 | 48903 | 0 | 48903 | 6846.42 | 0 | 0 | 0 | 0 | 0 | 55749.42 | 55749
| 504030000 | MEZZANINE FLOOR | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1Fresh Air for UnitsMF-FF-011400301.5Ceiling Suspended | [8 empty] | Nos. | 1 | 54798 | 0 | 54798 | 7671.72 | 0 | 0 | 0 | 0 | 0 | 62469.72 | 62470
| 504030000 | 2Toilet exhaustTF-EF-011000301.5Ceiling Suspended | [8 empty] | Nos. | 1 | 48903 | 0 | 48903 | 6846.42 | 0 | 0 | 0 | 0 | 0 | 55749.42 | 55749
| 504030000 | FIRST FLOOR | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1Toilet exhaustTF-EF-06900301.5Ceiling Suspended | [8 empty] | Nos. | 1 | 48903 | 0 | 48903 | 6846.42 | 0 | 0 | 0 | 0 | 0 | 55749.42 | 55749
| 504030000 | SECOND FLOOR | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1SPA (Male) Toilet ExhaustTF-EF-07250301.5Ceiling Suspended | [8 empty] | Nos. | 1 | 25255 | 0 | 25255 | 3535.7 | 0 | 0 | 0 | 0 | 0 | 28790.7 | 28791
| 504030000 | 2SPA (Female) Toilet ExhaustTF-EF-08150301.5Ceiling Suspended | [8 empty] | Nos. | 1 | 25255 | 0 | 25255 | 3535.7 | 0 | 0 | 0 | 0 | 0 | 28790.7 | 28791
10 | 504030000 | Supplying of direct driven PROPELLER FANS for exhaust air as shown in drawings. Each fan shall be complete with permanent split capacitor or shaded pole motor, mounting plate, accessories like wire guard, bird screen and fixed louvers for weather protection as required. Fan selection arrangement and Electrical characteristics shall be as follows : | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10.1 | 504030000 | 350 mm dia 900 RPM fan suitable for 220±6% volts 50 cycles, 1 phase AC supply. | [8 empty] | Nos. | 4 | 4357 | 0 | 4357 | 609.98 | 0 | 0 | 0 | 0 | 0 | 4966.98 | 19868
10.2 | 504030000 | 300 mm dia 900 RPM fan suitable for 220±6% volts 50 cycles, 1 phase AC supply. | [8 empty] | Nos. | 1 | 4069 | 0 | 4069 | 569.66 | 0 | 0 | 0 | 0 | 0 | 4638.66 | 4639
11 | 504030000 | Supply of FANS for return air & exhaust air suitable for installing in any position in Horizontal or vertical. The motor shall be suitable for 415 V + 10% volts three phase 50cycle, AC supply.The fan shall be equipped with mounting bracket & outlet core required at discharge. The fan shall be low RPM (less than 1000 RPM) and capacities based on minimum 1.5 inch (4cm WC) static pressure or to suit the system, shall be as follows: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | The fan shall have low sound power level not exceeding 65dBA at three meter distance at both ends. To achieve these DB levels, sound attenuators of suitable length, at inlet & outlet of the fans must be included in the cost. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | SR. NO.SPACEFanCFMSPMotorType | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | TagmmHP | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | BASEMENT-3 | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1Car Parking Fresh Air FanB3-FF-05340003020Tube axial flow fan | [8 empty] | Nos. | 2 | 277152 | 0 | 277152 | 38801.28 | 0 | 0 | 0 | 0 | 0 | 315953.28 | 631907
| 504030000 | BASEMENT-2 | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1Car Parking Fresh Air FanB2-FF-01340003020Tube axial flow fan | [8 empty] | Nos. | 2 | 277152 | 0 | 277152 | 38801.28 | 0 | 0 | 0 | 0 | 0 | 315953.28 | 631907
| 504030000 | BASEMENT-1 | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1Staircase-4 PressurizationB1-FF-033000303SISW Floor Mounted | [8 empty] | Nos. | 1 | 97419 | 0 | 97419 | 13638.66 | 0 | 0 | 0 | 0 | 0 | 111057.66 | 111058
| 504030000 | PENTHOUSE FLOOR | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1Fresh Air for Smoke EvacuationPF-FF-013400303Floor Mounted | [8 empty] | Nos. | 1 | 98054 | 0 | 98054 | 13727.56 | 0 | 0 | 0 | 0 | 0 | 111781.56 | 111782
| 504030000 | PENTHOUSE TERRACE FLOOR | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1Fresh Air for Smoke EvacuationPTF-FF-013400303Floor Mounted | [8 empty] | Nos. | 1 | 98054 | 0 | 98054 | 13727.56 | 0 | 0 | 0 | 0 | 0 | 111781.56 | 111782
| 504030000 | 2Lift PressurizationPTF-FF-02140003010Floor Mounted | [8 empty] | Nos. | 1 | 133745 | 0 | 133745 | 18724.3 | 0 | 0 | 0 | 0 | 0 | 152469.3 | 152469
| 504030000 | 3Lift PressurizationPTF-FF-03140003010Floor Mounted | [8 empty] | Nos. | 1 | 133745 | 0 | 133745 | 18724.3 | 0 | 0 | 0 | 0 | 0 | 152469.3 | 152469
| 504030000 | 4Lift PressurizationPTF-FF-04140003010Floor Mounted | [8 empty] | Nos. | 1 | 133745 | 0 | 133745 | 18724.3 | 0 | 0 | 0 | 0 | 0 | 152469.3 | 152469
| 504030000 | 5Lift PressurizationPTF-FF-05140003010Floor Mounted | [8 empty] | Nos. | 1 | 133745 | 0 | 133745 | 18724.3 | 0 | 0 | 0 | 0 | 0 | 152469.3 | 152469
| 504030000 | 6Staircase-2 PressurizationPTF-FF-06170003010Floor Mounted | [8 empty] | Nos. | 1 | 158221 | 0 | 158221 | 22150.94 | 0 | 0 | 0 | 0 | 0 | 180371.94 | 180372
| 504030000 | ROOF FLOOR | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1Staircase-1 PressurizationRF-FF-01170003010Floor Mounted | [8 empty] | Nos. | 1 | 158221 | 0 | 158221 | 22150.94 | 0 | 0 | 0 | 0 | 0 | 180371.94 | 180372
| 504030000 | 2Staircase-3 PressurizationRF-FF-02170003010Floor Mounted | [8 empty] | Nos. | 1 | 158221 | 0 | 158221 | 22150.94 | 0 | 0 | 0 | 0 | 0 | 180371.94 | 180372
12 | 504030000 | Supply of Scrubber each comprising of electrostatic precipitation technology, dry type air cleaner to remove oil, smoke and fumes from exhaust air, as per the Specifications. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Electrostatic section shall be made of 16 gauge galvanised sheet, high bake epoxy powder coated, washable type aluminium mesh filters, stainless steel spiked ionizers to create high voltage DC field, aluminum collector plates which should be alternatively charged positive and negative with large collecting area with 14" deep cell, to work as magnet for charged smoke and oil particles. Average efficiency of 90-95% in single pass as per ASHRAE test method. Electrostatic Precipitator should be able to charge particles from 0.01 micron to 10 microns through solid state power supply. Collector cell should be of permanent type and incorporate slide out facility for easy removal for cleaning. Power supplies shall be 100% solid state UL Listed, Module of capacity above 3000 CFM shall be equipped with Pulse width modulating (PWM)The system should be fitted with interlock switch for safety . The system should allow connection to a fan section to achieve 500 FPM velocity across the air cleaner. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Operating Voltage : 220V, 50 Hz | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Ionizing Voltage : 12.5 to 13 KVDC | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Collector Cell Voltage : 6 to 6.5 KVDC | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Power Consumption : Not more than 50W per cell. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Air Moving Capacities shall be as follows: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | SpaceCFMQTY | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Italina Restaurant Kitchen30001 | [8 empty] | Nos. | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | All Day Dining Kitchen130001 | [8 empty] | Nos. | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Chineese Restaurant kitchen102501 | [8 empty] | Nos. | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | The unit shall be integrated & connected with exhaust fan sections for kitchen including all necessary accessories to complete the installation. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12.1 | 504030000 | Indicate for all Dry Scrubber port charges, port handling charges, other local duties, loading, transportation /insurance upto site, octroi charges and all other taxes and incidentals complete till delivered at site. | [8 empty] | Nos. | 3 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
12.2 | 504030000 | Customs duty and countervailing duty for the above imported equipment.- Dry Scrubber | [8 empty] | Nos. | 3 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
B. | 504030000 | EQUIPMENT | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 504030000 | MOTOR CONTROL CENTRES FOR AIR CONDITIONING (PLANT ROOM) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Design, manufacture, supply of the following cubicle type 2 mm thick sheet steel enclosed separate compartment for each feeder, front operated, rear connections indoor type LT motor control panel, dust and vermin proof, drawout/hinged and lockable doors, complete with internal wiring, colour coding with ferrules, cable glands, bonding to earth and painting. Quoted price for each panel & motor control centre shall include all cabling & earthing over cable trays into various equipment, all associated control wiring and interlocking circuitary. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Each MCC shall include cost of wiring, control wiring & inter locking between chillers, primary CHW pumps, condenser water pumps, motorized valves at chillers and condensers, flow meter & flow switch installed in de-coupler by-pass line, in order to execute the required sequence of operation. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | All outgoing shall be provided with Stop/Manual/ Auto/selector switch to facilitate operation through BAS. All starters shall be provided with potential free Contact for Connections to Building Automation System. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | A separate set of CTs to be provided for BAS and wiring from CT’s and voltage transducers to be brought on to separate set of terminals. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13.1 | 504030000 | Motor Control Centre 415V Bus Section-1 consisting of | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
a. | 504030000 | Incomingg | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | One No. 800 amps 4P Microprocessor based incoming MCCB with LSI protection complete with the following accessories :: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 504030000 | 0 - 500 volts 96 x 96 sq mm digital voltmeter with selector switch - 1 Set | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 504030000 | 0 - 800 amps 96 x 96 sq mm digital ammeter with 800/5 amps CT’s and selector switch - 1 Set | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 504030000 | Over voltage tripping mechanism for persistent voltage exceeding 110% of the rated voltage for more than 5 minutes - 1 Set; | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iv. | 504030000 | Phase indicating lamps, with toggle switches - 3 Sets; | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
b. | 504030000 | TPN bus bars shall be of Copper and shall be sleeved. Phase bus bars shall be rated at 800 amps (25 KA) and neutral bus bar shall be of 50% capacityl | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Maximum density of copper bus bars for current carrying capacity shall be 1.4 amp per square mm.e | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Outgoingq | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
c. | 504030000 | 2 Nos. 315 amps TPN MCCB, and outgoing feeders to. 2 nos 200 TR (140 KW) chilling unit starter panel and outgoing feeders to chilling unit compressor motors. The MCCB compartment shall contain :; | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 504030000 | 0 - 500 volts 96 x 96 sq mm digital voltmeter with selector switcha | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 504030000 | 0 - 315 amps 96 x 96 sq mm digital ammeter with 315/5 amps CT’s and selector switchq | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 504030000 | Over voltage tripping mechanism for persistent voltage exceeding 110% of the rated voltage for more than 5 minutes.z | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iv. | 504030000 | Phase indicating light shall be protected by 2 amps MCB’s. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
d. | 504030000 | 2 Nos 25 amps TPN MCCB, 10 HP DOL starters, over load relay with built in single phasing protection and outgoing feeders to primary chilled water pump motors. compartment shall contain CT operated digital ammeter of 0-25 amps range with selector switch, and an indicating lamp with MCB and toggle switch for ‘ON’ status of pump motors. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
g. | 504030000 | 3 Nos. 40 amps TPN MCCB and outgoing feeders to Variable Frequency Drive (VFD) panel and outgoing feeders to secondary chilled water pump motors. The compartments shall contain CT operated digital ammeter 0 - 40 amps range with selector switch and an indicating lamp with MCB and toggle switch for ‘ON’ status of pump motors. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
h. | 504030000 | 1 Nos. 80 amps TPN MCCB 40 HP star delta starter, over load relay with built in single phasing protection and outgoing feeders to condenser water pump motors (Working). The compartment shall contain CT operated digital ammeter of 0-80 amps range with selector switch and an indicating lamp with MCB and toggle switch for ‘ON’ status of pump motors. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 504030000 | 2 Nos. 25 amps TPN MCCB 10 HP DOL starter, over load relay with built in single phasing protection and outgoing feeders to condenser water pump motors for cold storage (1 working + 1standby). The compartment shall contain CT operated digital ammeter of suitable amps range with selector switch and an indicating lamp with MCB and toggle switch for ‘ON’ status of pump motors. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
j | 504030000 | 1 Nos. 80 amps TPN MCCBs, outgoing feed to 1 No. VFD panel at terrace floor and outgoing feeder to cooling tower fan motor (Working). The compartment shall contain an indicating lamp with MCB and toggle switch for ‘ON’ status of fan motor. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
k | 504030000 | 1 Nos. suitable amps TPN MPCB with 10 HP DOL starter, over load relay with built in single phasing protection and outgoing feeders to Supply Fan motors . Each of these compartment shall contain CT operated digital ammeter of suitable amps range with selector switch and an indicating lamp with MCB and toggle switch for ‘ON’ status of pump motors. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
l. | 504030000 | 2 Nos. suitable amps TPN MPCB with 1 HP DOL starter, over load relay with built in single phasing protection and outgoing feeders to Hot water recirculation pump (1working + 1 standby) . Each of these compartment shall contain direct operated digital ammeter of suitable amps range with selector switch and an indicating lamp with MCB and toggle switch for ‘ON’ status of pump motors. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
m. | 504030000 | 2 Nos 63 amp MCCB with space provision for star/delta (SPARE)x | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
n. | 504030000 | Necessary cable alleys, space for spare switches, internal wiring, control wiring/cabling and copper earthing of all equipment shall also be included. All switches and other components shall be motor duty ratingc | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Bus Coupler : | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 800 amps 4 pole MCCB with operating handle and with ON / OFF/Trip indicating lamps with control MCB’s, shunt trip etc. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13.2 | 504030000 | Motor Control Centre section No. 2 (415 V) consisting of : | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
a. | 504030000 | Incomingz | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | One No. 800 amps 4P Microprocessor based incoming MCCB with LSI protection complete with the following accessories : | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 504030000 | 0 - 500 volts 96 x 96 sq mm digital voltmeter with selector switch - 1 Set | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 504030000 | 0 - 800 amps 96 x 96 sq mm digital ammeter with 800/5 amps CT’s and selector switch - 1 Set | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 504030000 | Over voltage tripping mechanism for persistent voltage exceeding 110% of the rated voltage for more than 5 minutes - 1 Set | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iv. | 504030000 | Phase indicating lamps, with toggle switches - 3 Sets | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
b. | 504030000 | TPN bus bars shall be of Copper and shall be sleeved. Phase bus bars shall be rated at 800 amps (25 KA) and neutral bus bar shall be of 50% capacity. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Maximum density of copper bus bars for current carrying capacity shall be 1.4 amp per square mm. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Outgoingz | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
c. | 504030000 | 2 Nos. 315 amps TPN MCCB, and outgoing feeders to. 2 nos 200 TR (140 KW) chilling unit starter panel and outgoing feeders to chilling unit compressor motors. The MCCB compartment shall contain : | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 504030000 | 0 - 500 volts 96 x 96 sq mm digital voltmeter with selector switch. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 504030000 | 0 - 315 amps 96 x 96 sq mm digital ammeter with 315/5 amps CT’s and selector switch | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 504030000 | Over voltage tripping mechanism for persistent voltage exceeding 110% of the rated voltage for more than 5 minutes. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iv. | 504030000 | Phase indicating lightshall be protected by 2 amps MCB’s. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
d. | 504030000 | 1 Nos 25 amps TPN MCCB, 10 HP DOL starters, over load relay with built in single phasing protection and outgoing feeders to primary chilled water pump motors (Working). The compartment shall contain CT operated digital ammeter of 0-25 amps range with selector switch, and an indicating lamp with MCB and toggle switch for ‘ON’ status of pump motors. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
e. | 504030000 | 3 Nos. 40 amps TPN MCCB and outgoing feeders to Variable Frequency Drive (VFD) panel and outgoing feeders to secondary chilled water pump motors ( 2 working + 1 standby). The compartments shall contain CT operated digital ammeter 0 - 40 amps range with selector switch and an indicating lamp with MCB and toggle switch for ‘ON’ status of pump motors. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
f. | 504030000 | 2 Nos. 80 amps TPN MCCB 40 HP star delta starter, over load relay with built in single phasing protection and outgoing feeders to 2 nos condenser water pump motors (1 Working + 1standby). Each compartment shall contain CT operated digital ammeter of 0-80 amps range with selector switch and an indicating lamp with MCB and toggle switch for ‘ON’ status of pump motors. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
g. | 504030000 | 2 Nos. 80 amps TPN MCCBs, outgoing feed to 2 No. VFD panel at terrace floor and outgoing feeder to cooling tower fan motor (Both Working). The compartment shall contain an indicating lamp with MCB and toggle switch for ‘ON’ status of fan motor. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
h. | 504030000 | 1 Nos. suitable amps TPN MPCB with 10 HP DOL starter, over load relay with built in single phasing protection and outgoing feeders to Exhaust Fan motors . Each of these compartment shall contain CT operated digital ammeter of suitable amps range with selector switch and an indicating lamp with MCB and toggle switch for ‘ON’ status of pump motors. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 504030000 | 2 Nos. suitable amps TPN MPCB with 1 HP DOL starter, over load relay with built in single phasing protection and outgoing feeders to Hot water recirculation pump (1working + 1 standby) . Each of these compartment shall contain direct operated digital ammeter of suitable amps range with selector switch and an indicating lamp with MCB and toggle switch for ‘ON’ status of pump motors. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
j. | 504030000 | 2 Nos 63 amp MCCB with space provision for star/delta (SPARE) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Necessary cable alleys, space for spare switches, internal wiring, control wiring/cabling and copper earthing of all equipment shall also be included. All switches and other components shall be motor duty rating. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Motor Control Centre as described above. | [8 empty] | No. | 1 | 1499393 | 0 | 1499393 | 209915.02 | 0 | 0 | 0 | 0 | 0 | 1709308.02 | 1709308
Note | 504030000 | MCCB’s shall be motor duty type 2 co-ordinated and suitable for 25 KA (ICS) fault current. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 504030000 | CONTROL PANEL FOR AHU (WITH DOL / SD STARTER) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14.1 | 504030000 | Design, manufacture, supply of the following cubicle type, dead front, sheet steel, wall mounted control panels including anchoring into the wall, wiring, incoming cable wiring terminating into MCCB, copper earthing of suitable strip/dia & terminating into MCCB/MPCB in each panel shall be provided by the HVAC contractor. Only incoming cable upto the panel shall be in the scope of the Electrical contractor. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | All internal wiring power cabling and copper earthing of air handling unit motors from the panel shall be included. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | All outgoing shall be provided with Stop Manual /Auto selector switch to facilitate operation through BAS. All starters shall be provided with potential free Contact for Connections to Building Automation System. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | The panel shall include the following components and accessories | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
a. | 504030000 | MCCB/MPCB as per the ratings given below, suitable for motor duty and able to withstand fault level of 25 KA | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
b. | 504030000 | DOL / SD starter as per HP ratings | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
c. | 504030000 | Terminal block for power distribution | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
d. | 504030000 | Contactor, over load relay with built in single phasing protection | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
e. | 504030000 | Phase indicating lights and indicating light for ON status | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
f. | 504030000 | Digital volttmeter and digital ammeter with selector switches. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
g. | 504030000 | Time delay relay for delayed automatic restart of air handling unit motor. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
h. | 504030000 | Wiring for microswitch for rstopping the fan when fire damper closes. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 504030000 | For on/off/remote and local operation, 3 pole single throw switch shall be provided in each AHU panel to facilitate override of the automatic operation. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
j. | 504030000 | All starters shall be provided with suitable potential free contact for connections to the Building Automation System. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
k. | 504030000 | 3 Nos of Single Pole MCBs Shall be provided at the incoming section of the starter panel for DDC Panel , fire damper actuator & as a spare. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
l. | 504030000 | 220 / 24 V Transformer for Power supply to valves / damper actuators. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
m. | 504030000 | MCCB/MPCB shall be Type 2 Co-ordinated with the Motor starter. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
n. | 504030000 | Degree of Protection for the Outdoor starter panel shall be IP 55. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | The number of AHU control panels shall be as follows. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14.1.1 | 504030000 | MPCB suitable for 1.1 KW motor with DOL Starter | [8 empty] | No. | 1 | 22613 | 0 | 22613 | 3165.82 | 0 | 0 | 0 | 0 | 0 | 25778.82 | 25779
14.1.2 | 504030000 | MPCB suitable for 1.5 KW motor with DOL Starter | [8 empty] | No. | 1 | 23079 | 0 | 23079 | 3231.06 | 0 | 0 | 0 | 0 | 0 | 26310.06 | 26310
14.1.3 | 504030000 | MPCB suitable for 2.25 KW motor with DOL Starter | [8 empty] | No. | 3 | 23544 | 0 | 23544 | 3296.16 | 0 | 0 | 0 | 0 | 0 | 26840.16 | 80520
14.1.4 | 504030000 | MPCB suitable for 3.75 KW motor with DOL Starter | [8 empty] | No. | 1 | 23544 | 0 | 23544 | 3296.16 | 0 | 0 | 0 | 0 | 0 | 26840.16 | 26840
15 | 504030000 | CONTROL PANEL FOR AHU (OPERATED THROUGH VFD) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15.1 | 504030000 | Design, manufacture, supply of the following cubicle type, dead front, sheet steel, wall mounted control panels including anchoring into the wall, wiring, incoming cable wiring terminating into MCCB, copper earthing of suitable strip/dia & terminating into MCCB/MPCB in each panel shall be provided by the HVAC contractor. Only incoming cable upto the panel shall be in the scope of the Electrical contractor. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | All internal wiring power cabling and copper earthing of air handling unit motors from the panel to VFD & to the motor shall be included. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | All outgoing shall be provided with Stop / Manual /Auto selector switch to facilitate operation through BAS. All starters shall be provided with potential free Contact for Connections to Building Automation System. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | The panel shall include the following components and accessories. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
a. | 504030000 | MCCB/MPCB as per the ratings given below, suitable for motor duty and able to withstand fault level of 25 KA. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
b. | 504030000 | VFD starter as per HP ratings (Supply of VFD under item No. 11 of Imported section) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
c. | 504030000 | Terminal block for power distribution. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
d. | 504030000 | Phase indicating lights and indicating light for ON status. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
e. | 504030000 | Digital voltmeter and digital ammeter with selector switches. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
f. | 504030000 | Wiring for microswitch for stopping the fan when fire damper closes. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
g. | 504030000 | For on/off/remote and local operation, 3 pole single throw switch shall be provided in each AHU panel to facilitate override of the automatic operation. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
h. | 504030000 | All starters shall be provided with suitable potential free contact for connections to the Building Automation System. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 504030000 | 3 Nos of Single Pole MCBs Shall be provided at the incoming section of the starter panel for DDC Panel , fire damper actuator & as a spare. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
j. | 504030000 | 220 / 24 V Transformer | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
k. | 504030000 | VFD : space provision for mounting of VFD only. The quantity, unit rate and amount for VFD is appearing separately in BOQ. Hence not to be included in the cost of these control panel. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
l. | 504030000 | MCCB/MPCB shall be Type 2 Co- ordinated with the Motor starter. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
m. | 504030000 | Degree of Protection for the Outdoor starters panel shall be IP 55. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | The number of AHU control panels shall be as follows. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15.1.1 | 504030000 | 25 amps MCCB, 2 HP VFD . | [8 empty] | No. | 1 | 28458 | 0 | 28458 | 3984.12 | 0 | 0 | 0 | 0 | 0 | 32442.12 | 32442
15.1.2 | 504030000 | 25 amps MCCB, 3 HP VFD . | [8 empty] | Nos. | 7 | 28458 | 0 | 28458 | 3984.12 | 0 | 0 | 0 | 0 | 0 | 32442.12 | 227095
15.1.3 | 504030000 | 25 amps MCCB, 5 HP VFD . | [8 empty] | Nos. | 6 | 29389 | 0 | 29389 | 4114.46 | 0 | 0 | 0 | 0 | 0 | 33503.46 | 201021
15.1.4 | 504030000 | 25 amps MCCB, 7.5 HP VFD . | [8 empty] | No. | 1 | 30786 | 0 | 30786 | 4310.04 | 0 | 0 | 0 | 0 | 0 | 35096.04 | 35096
16 | 504030000 | CONTROL PANELS FOR FANS (OPERATED THROUGH VFD) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Design, manufacture, supply of the following cubicle type, dead front, sheet steel, wall mounted control panels, including anchoring into the wall, incoming cable wiring terminating into MCCB and copper earthing of suitable strip/dia in each panel shall be provided by the HVAC contractor. Only incoming cable upto the panel shall be in the scope of the Electrical contractor. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | All outgoing shall be provided with Stop /Manual Auto selector switch to facilitate operation through BAS. All starters shall be provided with potential free Contact for Connections to Building Automation System. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | All internal wiring, power cabling and copper earthing of motors from the panel to VFD & to the motor shall be included. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | The panel shall include the following co mponents & accessories. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
a. | 504030000 | MCCB/MPCB as per the ratings given below, suitable for motor duty and able to withstand fault level of 25 KA. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
b. | 504030000 | Terminal block for power distribution as required. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
c. | 504030000 | Phase indicating lights and indicating light for ON status. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
d. | 504030000 | 144 mm x 144 mm voltmeter and digital ammeter | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
e. | 504030000 | Wiring for microswitch for stopping the fan when fire damper closes (in case of Fan only). | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
f. | 504030000 | For on/off/remote and local operation, 3 pole single throw switch hall be provided in each panel to facilitate override of the automatic operation. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
g. | 504030000 | 3 Nos of Single Pole MCBs Shall be provided at the incoming section of the starter panel for DDC Panel , fire damper actuator & as a spare. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
h. | 504030000 | All starters shall be provided with suitable potential free contract f or connections to the Building Automation System. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 504030000 | 220 / 24 V Transformer | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
j. | 504030000 | VFD : space provision for mounting of VFD only. The quantity, unit rate and amount for VFD is appearing separately in BOQ. Hence not to be included in the cost of these control panel. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
k. | 504030000 | MCCB/MPCB shall be Type 2 Co-ordinated with the Mo tor starter. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
l. | 504030000 | Degree of Protection for the Outdoor start er panel shall be IP 55. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | The number of control panels shall be as follows. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16.1 | 504030000 | 80 amps MCCB, 40 HP VFD for cooling tower IP 55 required. | [8 empty] | Nos. | 3 | 40027 | 0 | 40027 | 5603.78 | 0 | 0 | 0 | 0 | 0 | 45630.78 | 136892
17 | 504030000 | CONTROL PANELS FOR FANS | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Design, manufacture, supply of the following cubicle type, dead front, sheet steel, wall mounted control panels, including anchoring into the wall, incoming cable wiring terminating into MCCB and copper earthing, in each panel shall be provided by the HVAC contractor. Only incoming cable upto the panel shall be in the scope of the Electrical contractor. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | All outgoing shall be provided with Stop /Manual /Auto selector switch to facilitate operation through BAS. All starters shall be provided with potential free Contact for Connections to Building Automation System. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | All wiring and copper earthing of motors from the panel shall be included. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | The panel shall include the following c omponents & accessories. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
a. | 504030000 | MCCB/MPCB as per the ratings given below, suitable for mot or duty and able to withstand fault level of 25 KA. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
b. | 504030000 | DOL / SD starter as per HP gratings g iven. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
c. | 504030000 | Terminal block for power distribut ion as required. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
d. | 504030000 | Contactor, over load relay with built in sing le phasing protection. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
e. | 504030000 | Phase indicating lights and ind icating light for ON status. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
f. | 504030000 | 144 mm x 144 mm voltmet er and digital ammeter. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
g. | 504030000 | Time delay relay for delayed automatic res tart of motor. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
h. | 504030000 | Wiring for microswitch for stopping the fan when fire damper closes (in case of Fire operation only). | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 504030000 | For on/off/remote and local operat ion, 3 pole single throw switch shall be provided in each panel to facilitate override of the automatic operation. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
j. | 504030000 | All starters shall be provided with suitable pote ntial free contract for connections to the Building Automation System. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
k. | 504030000 | MCCB/MPCB shall be Type 2 Co-ordinated w ith the Motor starter. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
l. | 504030000 | Degree of Protection for the Outdoor starter panel shall be IP 55. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | The number of control pan els shall be as follows. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17.1 | 504030000 | MPCB suitable for 2.25 KW/ 3HP motor with DOL Starter | [8 empty] | Nos. | 8 | 21711 | 0 | 21711 | 3039.54 | 0 | 0 | 0 | 0 | 0 | 24750.54 | 198004
17.2 | 504030000 | MPCB suitable for 3.75 KW/ 5 HP motor with DOL Starter | [8 empty] | Nos. | 4 | 21711 | 0 | 21711 | 3039.54 | 0 | 0 | 0 | 0 | 0 | 24750.54 | 99002
17.3 | 504030000 | MPCB suitable for 5.6 KW/ 7.5 HP motor with DOL Starter | [8 empty] | Nos. | 6 | 25407 | 0 | 25407 | 3556.98 | 0 | 0 | 0 | 0 | 0 | 28963.98 | 173784
17.4 | 504030000 | MPCB suitable for 7.5 KW/ 10 HP motor with DOL Starter | [8 empty] | Nos. | 9 | 25407 | 0 | 25407 | 3556.98 | 0 | 0 | 0 | 0 | 0 | 28963.98 | 260676
17.5 | 504030000 | MPCB suitable for 9.3 KW/ 12.5 HP motor with STAR DELTA Starter | [8 empty] | Nos. | 2 | 33580 | 0 | 33580 | 4701.2 | 0 | 0 | 0 | 0 | 0 | 38281.2 | 76562
17.6 | 504030000 | MCCB suitable for 15 KW/ 20 HP motor with STAR DELTA Starter | [8 empty] | No. | 1 | 53471 | 0 | 53471 | 7485.94 | 0 | 0 | 0 | 0 | 0 | 60956.94 | 60957
18 | 504030000 | CONTROL PANELS FOR HEAT RECOVERY UNIT | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Design, manufacture, supply of the following cubicle type, dead front, sheet steel, wall mounted control panels, including anchoring into the wall, incoming cable wiring terminating into MCCB and copper earthing, in each panel shall be provided by the HVAC contractor. Only incoming cable upto the panel shall be in the scope of the Electrical contractor. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | All outgoing shall be provid ed with Stop /Manual /Auto selector switch to facilitate operation through BAS. All starters shall be provided with potential free Contact for Connections to Building Automation System. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | All wiring and copper earthing of motors from the panel sh all be included. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | The panel shall include the follo wing components & accessories. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
a. | 504030000 | MCCB/MPCB as per the ratings given be low, suitable for motor duty and able to withstand fault level of 25 KA. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
b. | 504030000 | DOL / SD starter as p er HP gratings given. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
c. | 504030000 | Terminal block for power distribution as re quired. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
d. | 504030000 | Contactor, over load relay with built in sing le ph asing protection. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
e. | 504030000 | Phase indicating lights and indicating lig ht for ON status. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
f. | 504030000 | 144 mm x 144 mm voltmeter nd digital ammeter. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
g. | 504030000 | Time delay relay for del ayed automatic res tart of motor. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
h. | 504030000 | Wiring for microswitch for stopp ing the fan when fire damper closes (in case of Fire operation only). | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 504030000 | For on/off/remote and local opera tion, 3 pole single throw switch shall be provided in each panel to facilitate override of the automatic operation. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
j. | 504030000 | All starters shall be provid ed with suitable potential free contract for connections to the Building Automation System. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
k. | 504030000 | IP 55 required | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
l. | 504030000 | MCCB/MPCB shall be Type 2 Co-ordin ated with the Motor starter. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | The number of control pane ls shall be as follows. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18.1 | 504030000 | Incoming | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 63 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Bus Bars | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 63 amps (25 KA) TPNcopper bus bars with heat shrinkable insulation sleeve. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Outgoing | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | a) MPCB suitable for 9.3 KW motor with STAR DELTA Starter (For supply fan motor) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | b) MPCB suitable for 3.75 KW motor with DOL Starter (For Exhaust fan motor) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | c) MPCB suitable for 0.75 KW motor with DOL Starter (For HRW motor) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | MCC control panel described as above | [8 empty] | Nos. | 2 | 105450 | 0 | 105450 | 14763 | 0 | 0 | 0 | 0 | 0 | 120213 | 240426
19 | 504030000 | CONTROL PANELS FOR DUAL OPERATION CAR PARK FRESH AIR & EXHAUST AIR FANS | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Design, manufacture, supply of the following cubicle type, dead front, sheet steel, wall mounted control panels, including anchoring into the wall, incoming cable wiring terminating into MCCB and copper earthing, in each panel shall be provided by the HVAC contractor. Only incoming cable upto the panel shall be in the scope of the Electrical contractor. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | All outgoing shall be provided with Stop /Manual /Auto selector switch to facilitate operation through BAS. All starters shall be provided with potential free Contact for Connections to Building Automation System. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | All wiring and copper earthing of motors from the panel shall be included. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | The panel shall include the following components & accessories. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
a. | 504030000 | MCCB/MPCB as per the ratings given below, suitable for motor duty and able to withstand fault level of 25 KA. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
b. | 504030000 | DOL / SD starter as per HP gratings given. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
c. | 504030000 | Terminal block for power distribution as required. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
d. | 504030000 | Contactor, over load relay with built in single phasing protection. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
e. | 504030000 | Phase indicating lights and indicating light for ON status. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
f. | 504030000 | 144 mm x 144 mm voltmeter and digital ammeter. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
g. | 504030000 | Time delay relay for delayed automatic restart of motor. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
h. | 504030000 | Wiring for microswitch for stopping the fan when fire damper closes (in case of Fire operation only). | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 504030000 | For on/off/remote and local operation, 3 pole single throw switch shall be provided in each panel to facilitate override of the automatic operation. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
j. | 504030000 | All starters shall be provided with suitable potential free contract for connections to the Building Automation System. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
k. | 504030000 | MCCB/MPCB shall be Type 2 Co-ordinated with the Motor starter. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | The number of control panels shall be as follows. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19.1 | 504030000 | Starter Panel for Dual speed operated 30 HP Motor in Normal & Fire mode as per the requirement under section B 8 and with above requirements. | [8 empty] | Nos. | 1 | 71500 | 0 | 71500 | 10010 | 0 | 0 | 0 | 0 | 0 | 81510 | 81510
19.2 | 504030000 | Starter Panel for Dual speed operated 60 HP Motor in Normal & Fire mode as per the requirement under section B 8, B11 and with above requirements. | [8 empty] | Nos. | 4 | 91127 | 0 | 91127 | 12757.78 | 0 | 0 | 0 | 0 | 0 | 103884.78 | 415539
20 | 504030000 | Supply of 315 Amps Manual changeover switch with 315 A TPN Isolator MCCB (25 KA) breaking capacity with operating handle in 1.6 mm thick CRCA sheet steel enclosure of approved make design and painted with approved paint shade including supply & laying of suitable rating Aluminium Armoured cable from MCC HVAC panel. | [8 empty] | No. | 1 | 81500 | 0 | 81500 | 11410 | 0 | 0 | 0 | 0 | 0 | 92910 | 92910
C. | 504030000 | PIPING-CHILLED, HOT WATER AND CONDENSER WATER | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 504030000 | Providing the following MS C Class pipes with specified wall thickness (6 mm) cut to required lengths and installed with all welded / grooved joints, providing and fixing in position necessary fittings like bends, elbows, tees, reducers, mating flanges & sockets for BAS, fabricated to size and shape in workshop or brought out ready made where available of acceptable quality. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.1 | 504030000 | 300 mm dia MS pipes. | [8 empty] | RM | 2 | 2497 | 0 | 2497 | 124.85 | 0 | 0 | 0 | 0 | 0 | 2621.85 | 5244
1.2 | 504030000 | 250 mm dia MS pipes. | [8 empty] | RM | 120 | 2129 | 0 | 2129 | 106.45 | 0 | 0 | 0 | 0 | 0 | 2235.45 | 268254
2 | 504030000 | Providing the following MS class ‘C’ pipes (Wall Thickness as per IS code) cut to required lengths and installed with all welded joints, providing and fixing in position the necessary fittings like elbows, tees and reducers, mating flanges & sockets for BAS: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.1 | 504030000 | 200 mm dia MS pipes | [8 empty] | RM | 145 | 1700 | 0 | 1700 | 85 | 0 | 0 | 0 | 0 | 0 | 1785 | 258825
2.2 | 504030000 | 150 mm dia MS pipes | [8 empty] | RM | 225 | 1130 | 0 | 1130 | 56.5 | 0 | 0 | 0 | 0 | 0 | 1186.5 | 266963
2.3 | 504030000 | 125 mm dia MS pipes | [8 empty] | RM | 75 | 951 | 0 | 951 | 47.55 | 0 | 0 | 0 | 0 | 0 | 998.55 | 74891
2.4 | 504030000 | 100 mm dia MS pipes | [8 empty] | RM | 100 | 772 | 0 | 772 | 38.6 | 0 | 0 | 0 | 0 | 0 | 810.6 | 81060
2.5 | 504030000 | 80 mm dia MS pipes | [8 empty] | RM | 185 | 524 | 0 | 524 | 26.2 | 0 | 0 | 0 | 0 | 0 | 550.2 | 101787
2.6 | 504030000 | 65 mm dia MS pipes | [8 empty] | RM | 325 | 433 | 0 | 433 | 21.65 | 0 | 0 | 0 | 0 | 0 | 454.65 | 147761
2.7 | 504030000 | 50 mm dia MS pipes | [8 empty] | RM | 775 | 330 | 0 | 330 | 16.5 | 0 | 0 | 0 | 0 | 0 | 346.5 | 268538
2.8 | 504030000 | 40 mm dia MS pipes | [8 empty] | RM | 365 | 233 | 0 | 233 | 11.65 | 0 | 0 | 0 | 0 | 0 | 244.65 | 89297
2.9 | 504030000 | 32 mm dia MS pipes | [8 empty] | RM | 600 | 201 | 0 | 201 | 10.05 | 0 | 0 | 0 | 0 | 0 | 211.05 | 126630
2.1 | 504030000 | 25 mm dia MS pipes | [8 empty] | RM | 2500 | 156 | 0 | 156 | 7.8 | 0 | 0 | 0 | 0 | 0 | 163.8 | 409500
3 | 504030000 | Providing the following butterfly valves (PN16) with counter flanges, nuts & bolts and gasket to suit pressure rating. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.1 | 504030000 | 300 mm dia Valves. | [8 empty] | Nos. | 1 | 19714 | 0 | 19714 | 985.7 | 0 | 0 | 0 | 0 | 0 | 20699.7 | 20700
3.2 | 504030000 | 250 mm dia Vbalves. | [8 empty] | Nos. | 9 | 16584 | 0 | 16584 | 829.2 | 0 | 0 | 0 | 0 | 0 | 17413.2 | 156719
3.3 | 504030000 | 200 mm dia Valv es. | [8 empty] | Nos. | 6 | 10443 | 0 | 10443 | 522.15 | 0 | 0 | 0 | 0 | 0 | 10965.15 | 65791
3.4 | 504030000 | 150 mm dia Valv es. | [8 empty] | Nos. | 12 | 4787 | 0 | 4787 | 239.35 | 0 | 0 | 0 | 0 | 0 | 5026.35 | 60316
3.5 | 504030000 | 125 mm dia Valves. | [8 empty] | Nos. | 12 | 3733 | 0 | 3733 | 186.65 | 0 | 0 | 0 | 0 | 0 | 3919.65 | 47036
3.6 | 504030000 | 100 mm dia Valves. | [8 empty] | Nos. | 4 | 3398 | 0 | 3398 | 169.9 | 0 | 0 | 0 | 0 | 0 | 3567.9 | 14272
3.7 | 504030000 | 80 mm dia Valves. | [8 empty] | Nos. | 3 | 2564 | 0 | 2564 | 128.2 | 0 | 0 | 0 | 0 | 0 | 2692.2 | 8077
3.8 | 504030000 | 65 mm dia Valves. | [8 empty] | Nos. | 8 | 2364 | 0 | 2364 | 118.2 | 0 | 0 | 0 | 0 | 0 | 2482.2 | 19858
3.9 | 504030000 | 50 mm dia Valves. | [8 empty] | Nos. | 16 | 2190 | 0 | 2190 | 109.5 | 0 | 0 | 0 | 0 | 0 | 2299.5 | 36792
4 | 504030000 | Providing the following 3-Way valves with counter flanges, nuts & bolts and gasket to suit pressure rating. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4.1 | 504030000 | 200 mm dia Valves. | [8 empty] | Nos. | 2 | 177171 | 0 | 177171 | 24803.94 | 0 | 0 | 0 | 0 | 0 | 201974.94 | 403950
4.2 | 504030000 | 25 mm dia Valves. | [8 empty] | Nos. | 8 | 19584 | 0 | 19584 | 2741.76 | 0 | 0 | 0 | 0 | 0 | 22325.76 | 178606
5 | 504030000 | Supplying the following double regulating manual BALANCING VALVES. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.1 | 504030000 | 25 mm dia. | [8 empty] | Nos. | 8 | 3139 | 0 | 3139 | 156.95 | 0 | 0 | 0 | 0 | 0 | 3295.95 | 26368
6 | 504030000 | Supply of motorised butterfly valve (PN 16) of following sizes with counter flanges and accessories | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6.1 | 504030000 | 200 mm dia Valves. | [8 empty] | Nos. | 4 | 32733 | 0 | 32733 | 4582.62 | 0 | 0 | 0 | 0 | 0 | 37315.62 | 149262
6.2 | 504030000 | 150 mm dia Valves. | [8 empty] | Nos. | 2 | 30336 | 0 | 30336 | 4247.04 | 0 | 0 | 0 | 0 | 0 | 34583.04 | 69166
7 | 504030000 | Providing following ball valves without Y strainer. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7.1 | 504030000 | 50 mm dia valves | [8 empty] | Nos. | 24 | 2907 | 0 | 2907 | 145.35 | 0 | 0 | 0 | 0 | 0 | 3052.35 | 73256
7.2 | 504030000 | 40 mm dia valves | [8 empty] | Nos. | 6 | 2392 | 0 | 2392 | 119.6 | 0 | 0 | 0 | 0 | 0 | 2511.6 | 15070
7.3 | 504030000 | 32 mm dia valves | [8 empty] | Nos. | 6 | 2211 | 0 | 2211 | 110.55 | 0 | 0 | 0 | 0 | 0 | 2321.55 | 13929
7.4 | 504030000 | 25 m m dia valves | [8 empty] | Nos. | 8 | 1705 | 0 | 1705 | 85.25 | 0 | 0 | 0 | 0 | 0 | 1790.25 | 14322
8 | 504030000 | Providing the following ball valves with Y strainer | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8.1 | 504030000 | 40 mm dia Val ves | [8 empty] | Nos. | 6 | 3684 | 0 | 3684 | 184.2 | 0 | 0 | 0 | 0 | 0 | 3868.2 | 23209
8.2 | 504030000 | 32 mm dia Val ves | [8 empty] | Nos. | 6 | 3352 | 0 | 3352 | 167.6 | 0 | 0 | 0 | 0 | 0 | 3519.6 | 21118
8.3 | 504030000 | 25 mm dia Valves | [8 empty] | Nos. | 8 | 2679 | 0 | 2679 | 133.95 | 0 | 0 | 0 | 0 | 0 | 2812.95 | 22504
9 | 504030000 | Providing the following check valves : | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.1 | 504030000 | 200 mm dia valves | [8 empty] | Nos. | 3 | 11670 | 0 | 11670 | 583.5 | 0 | 0 | 0 | 0 | 0 | 12253.5 | 36761
9.2 | 504030000 | 150 mm dia valves | [8 empty] | Nos. | 3 | 6467 | 0 | 6467 | 323.35 | 0 | 0 | 0 | 0 | 0 | 6790.35 | 20371
9.3 | 504030000 | 125 mm dia valves | [8 empty] | Nos. | 6 | 5266 | 0 | 5266 | 263.3 | 0 | 0 | 0 | 0 | 0 | 5529.3 | 33176
9.4 | 504030000 | 100 mm dia valves | [8 empty] | Nos. | 1 | 4059 | 0 | 4059 | 202.95 | 0 | 0 | 0 | 0 | 0 | 4261.95 | 4262
10 | 504030000 | Providing the following ‘Y’ Strainers : | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10.1 | 504030000 | 250 mm dia strainers | [8 empty] | Nos. | 1 | 25876 | 0 | 25876 | 1293.8 | 0 | 0 | 0 | 0 | 0 | 27169.8 | 27170
10.2 | 504030000 | 200 mm dia strainers | [8 empty] | Nos. | 6 | 16719 | 0 | 16719 | 835.95 | 0 | 0 | 0 | 0 | 0 | 17554.95 | 105330
10.3 | 504030000 | 150 mm dia strainers | [8 empty] | Nos. | 12 | 10281 | 0 | 10281 | 514.05 | 0 | 0 | 0 | 0 | 0 | 10795.05 | 129541
10.4 | 504030000 | 125 mm dia strainers | [8 empty] | Nos. | 18 | 7555 | 0 | 7555 | 377.75 | 0 | 0 | 0 | 0 | 0 | 7932.75 | 142790
10.5 | 504030000 | 100 mm dia strainers | [8 empty] | Nos. | 2 | 6277 | 0 | 6277 | 313.85 | 0 | 0 | 0 | 0 | 0 | 6590.85 | 13182
10.6 | 504030000 | 80 mm dia strainers | [8 empty] | Nos. | 1 | 5018 | 0 | 5018 | 250.9 | 0 | 0 | 0 | 0 | 0 | 5268.9 | 5269
10.7 | 504030000 | 65 mm dia strainers | [8 empty] | Nos. | 4 | 4469 | 0 | 4469 | 223.45 | 0 | 0 | 0 | 0 | 0 | 4692.45 | 18770
10.8 | 504030000 | 50 mm dia strainers | [8 empty] | Nos. | 5 | 4043 | 0 | 4043 | 202.15 | 0 | 0 | 0 | 0 | 0 | 4245.15 | 21226
10.9 | 504030000 | 40 mm dia strainers | [8 empty] | Nos. | 1 | 3113 | 0 | 3113 | 155.65 | 0 | 0 | 0 | 0 | 0 | 3268.65 | 3269
11 | 504030000 | Providing the following pot strainers | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11.1 | 504030000 | 250 mm dia pip es | [8 empty] | Nos. | 2 | 106334 | 0 | 106334 | 5316.7 | 0 | 0 | 0 | 0 | 0 | 111650.7 | 223301
12 | 504030000 | Supply of flexible connections of suitable pressure rating to be installed at pump suction, discharge and at pipes crossing building expansion joints. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12.1 | 504030000 | 250 mm dia pipes | [8 empty] | No. | 1 | 11943 | 0 | 11943 | 597.15 | 0 | 0 | 0 | 0 | 0 | 12540.15 | 12540
12.2 | 504030000 | 200 mm dia pipes | [8 empty] | No. | 6 | 7091 | 0 | 7091 | 354.55 | 0 | 0 | 0 | 0 | 0 | 7445.55 | 44673
12.3 | 504030000 | 150 mm dia pipes | [8 empty] | No. | 12 | 5264 | 0 | 5264 | 263.2 | 0 | 0 | 0 | 0 | 0 | 5527.2 | 66326
12.4 | 504030000 | 125 mm dia pipes | [8 empty] | No. | 18 | 4657 | 0 | 4657 | 232.85 | 0 | 0 | 0 | 0 | 0 | 4889.85 | 88017
12.5 | 504030000 | 100 mm dia pipes | [8 empty] | No. | 1 | 4149 | 0 | 4149 | 207.45 | 0 | 0 | 0 | 0 | 0 | 4356.45 | 4356
13 | 504030000 | Supplying of Auto air vents. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13.1 | 504030000 | 25 mm dia pipes | [8 empty] | Nos. | 11 | 1651 | 0 | 1651 | 82.55 | 0 | 0 | 0 | 0 | 0 | 1733.55 | 19069
14 | 504030000 | Providing 80mm dia probe type flow meter to measure the flow in CHW & CDW pipe lines. The flow meter shall be provided with necessary fittings & electronic digital read out. | [8 empty] | Nos. | 2 | 89650 | 0 | 89650 | 12551 | 0 | 0 | 0 | 0 | 0 | 102201 | 204402
15 | 504030000 | Providing SS 304 the industrial dial type pressure gauges with gun metal valves. | [8 empty] | Nos. | 36 | 701 | 0 | 701 | 35.05 | 0 | 0 | 0 | 0 | 0 | 736.05 | 26498
16 | 504030000 | Providing SS 304 the mercury-in- glass industrial dial type thermometers. | [8 empty] | Nos. | 24 | 1443 | 0 | 1443 | 72.15 | 0 | 0 | 0 | 0 | 0 | 1515.15 | 36364
17 | 504030000 | Providing the following U-PVC pipes cut to required lengths and installed with all screwed joints, and providing and fixing in position the necessary elbows, tees and reducers as per specifications for AHU / FCU drain. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17.1 | 504030000 | 50 mm dia | [8 empty] | Rmt | 100 | 54 | 0 | 54 | 2.7 | 0 | 0 | 0 | 0 | 0 | 56.7 | 5670
17.2 | 504030000 | 40 mm dia | [8 empty] | Rmt | 110 | 36 | 0 | 36 | 1.8 | 0 | 0 | 0 | 0 | 0 | 37.8 | 4158
17.3 | 504030000 | 25 mm dia | [8 empty] | Rmt | 1500 | 20 | 0 | 20 | 1 | 0 | 0 | 0 | 0 | 0 | 21 | 31500
D. | 504030000 | AIR DISTRIBUTION | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | (FOR FACTORY FABRICATED DUCTS AS PER “SMACNA” STANDARDS & SPECIFICTIONS) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 504030000 | Supply of sheet metal ducts in accordance with the approved shop drawings and as required by the specifications. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | For Ducts with External SP upto 250 Pa (ESP upto 25mmWG) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Maximum Gauge Joint Type Bracing | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Duct Size Spacing | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1 -500 mm 26 C&S Connector Nil | [8 empty] | sq.m | 3500 | 407 | 0 | 407 | 20.35 | 0 | 0 | 0 | 0 | 0 | 427.35 | 1495725
| 504030000 | 501 -750 mm 26 C&S Connector Nil | [8 empty] | sq.m | 0 | 407 | 0 | 407 | 20.35 | 0 | 0 | 0 | 0 | 0 | 427.35 | 0
| 504030000 | 751 - 900 mm 26 TDF Flange Nil | [8 empty] | sq.m | 4000 | 447 | 0 | 447 | 22.35 | 0 | 0 | 0 | 0 | 0 | 469.35 | 1877400
| 504030000 | 901 - 1200 mm 24 TDF Flange Nil | [8 empty] | sq.m | 1900 | 521 | 0 | 521 | 26.05 | 0 | 0 | 0 | 0 | 0 | 547.05 | 1039395
| 504030000 | 1201 - 1500 mm 22 TDF Flange Nil | [8 empty] | sq.m | 0 | 614 | 0 | 614 | 30.7 | 0 | 0 | 0 | 0 | 0 | 644.7 | 0
| 504030000 | 1501 - 1800 mm 22 TDF Flange JTR or ZEE BAR | [8 empty] | sq.m | 1000 | 614 | 0 | 614 | 30.7 | 0 | 0 | 0 | 0 | 0 | 644.7 | 644700
| 504030000 | 1801 - 2100 mm 20 TDF Flange JTR or ZEE BAR | [8 empty] | sq.m | 750 | 741 | 0 | 741 | 37.05 | 0 | 0 | 0 | 0 | 0 | 778.05 | 583538
| 504030000 | 2101 - above 18 TDF Flange JTR or ZEE BAR | [8 empty] | sq.m | 1800 | 861 | 0 | 861 | 43.05 | 0 | 0 | 0 | 0 | 0 | 904.05 | 1627290
2 | 504030000 | Kitchen ducting 1.2mm CRCA with Fire paint (Flame bar BW11)(heat resistent painting) and all accessories as per specifications. (with clean outs as per NFPA at base of vertical riser and change in direction and maximum at every 6.0 M in horizontal & every third floor of vertical riser and at sprinkler heads) with weather proof painting for outdoor application | [8 empty] | sq.m | 1750 | 1931 | 0 | 1931 | 96.55 | 0 | 0 | 0 | 0 | 0 | 2027.55 | 3548213
4 | 504030000 | Supply the flexible connections constructed of fire resistance flexible double canvas sleeve with sandwitched 25 mm thick fibreglass insulation as per the approved shop drawings. | [8 empty] | sq.m | 4 | 6124 | 0 | 6124 | 857.36 | 0 | 0 | 0 | 0 | 0 | 6981.36 | 27925
5 | 504030000 | Supply of motorised combined smoke & fire damper (CPRI Approved) complete with control panel, inter connecting wiring at locations shown in approved shop drawings and as per specifications. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.1 | 504030000 | Smoke & Fire Dampers. (Sizes Given Below) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1800 x 1000 = 2 Sq.m. | [8 empty] | Nos. | 5 | 28286 | 0 | 28286 | 3960.04 | 0 | 0 | 0 | 0 | 0 | 32246.04 | 161230
| 504030000 | 1800 x 600 = 1 Sq.m. | [8 empty] | Nos. | 2 | 15368 | 0 | 15368 | 2151.52 | 0 | 0 | 0 | 0 | 0 | 17519.52 | 35039
| 504030000 | 1700 x 400 = 1 Sq.m. | [8 empty] | Nos. | 2 | 12647 | 0 | 12647 | 1770.58 | 0 | 0 | 0 | 0 | 0 | 14417.58 | 28835
| 504030000 | 1600 x 450 = 1 Sq.m. | [8 empty] | Nos. | 2 | 12918 | 0 | 12918 | 1808.52 | 0 | 0 | 0 | 0 | 0 | 14726.52 | 29453
| 504030000 | 1400 x 500 = 1 Sq.m. | [8 empty] | Nos. | 2 | 12782 | 0 | 12782 | 1789.48 | 0 | 0 | 0 | 0 | 0 | 14571.48 | 29143
| 504030000 | 1400 x 450 = 1 Sq.m. | [8 empty] | Nos. | 6 | 12306 | 0 | 12306 | 1722.84 | 0 | 0 | 0 | 0 | 0 | 14028.84 | 84173
| 504030000 | 1300 x 450 = 1 Sq.m. | [8 empty] | Nos. | 2 | 12000 | 0 | 12000 | 1680 | 0 | 0 | 0 | 0 | 0 | 13680 | 27360
| 504030000 | 1250 x 600 = 1 Sq.m. | [8 empty] | Nos. | 2 | 13123 | 0 | 13123 | 1837.22 | 0 | 0 | 0 | 0 | 0 | 14960.22 | 29920
| 504030000 | 1250 x 400 = 1 Sq.m. | [8 empty] | Nos. | 2 | 11422 | 0 | 11422 | 1599.08 | 0 | 0 | 0 | 0 | 0 | 13021.08 | 26042
| 504030000 | 1200 x 400 = 0.5 Sq.m. | [8 empty] | Nos. | 4 | 11285 | 0 | 11285 | 1579.9 | 0 | 0 | 0 | 0 | 0 | 12864.9 | 51460
| 504030000 | 1150 x 500 = 1 Sq.m. | [8 empty] | Nos. | 4 | 11932 | 0 | 11932 | 1670.48 | 0 | 0 | 0 | 0 | 0 | 13602.48 | 54410
| 504030000 | 1100 x 450 = 0.5 Sq.m. | [8 empty] | Nos. | 6 | 11388 | 0 | 11388 | 1594.32 | 0 | 0 | 0 | 0 | 0 | 12982.32 | 77894
| 504030000 | 1000 x 350 = 0.5 Sq.m. | [8 empty] | Nos. | 2 | 9550 | 0 | 9550 | 1337 | 0 | 0 | 0 | 0 | 0 | 10887 | 21774
| 504030000 | 1000 x 400 = 0.5 Sq.m. | [8 empty] | Nos. | 6 | 10741 | 0 | 10741 | 1503.74 | 0 | 0 | 0 | 0 | 0 | 12244.74 | 73468
| 504030000 | 1000 x 500 = 1 Sq.m. | [8 empty] | Nos. | 3 | 11422 | 0 | 11422 | 1599.08 | 0 | 0 | 0 | 0 | 0 | 13021.08 | 39063
| 504030000 | 950 x 1350 = 1 Sq.m. | [8 empty] | Nos. | 1 | 24765 | 0 | 24765 | 3467.1 | 0 | 0 | 0 | 0 | 0 | 28232.1 | 28232
| 504030000 | 950 x 400 = 0.5 Sq.m. | [8 empty] | Nos. | 5 | 10605 | 0 | 10605 | 1484.7 | 0 | 0 | 0 | 0 | 0 | 12089.7 | 60449
| 504030000 | 950 x 350 = 0.5 Sq.m. | [8 empty] | Nos. | 1 | 9430 | 0 | 9430 | 1320.2 | 0 | 0 | 0 | 0 | 0 | 10750.2 | 10750
| 504030000 | 900 x 900 = 1 Sq.m. | [8 empty] | Nos. | 4 | 13532 | 0 | 13532 | 1894.48 | 0 | 0 | 0 | 0 | 0 | 15426.48 | 61706
| 504030000 | 900 x 450 = 0.5 Sq.m. | [8 empty] | Nos. | 1 | 10775 | 0 | 10775 | 1508.5 | 0 | 0 | 0 | 0 | 0 | 12283.5 | 12284
| 504030000 | 900 x 350 = 0.5 Sq.m. | [8 empty] | Nos. | 2 | 9311 | 0 | 9311 | 1303.54 | 0 | 0 | 0 | 0 | 0 | 10614.54 | 21229
| 504030000 | 850 x 850 = 1 Sq.m. | [8 empty] | Nos. | 1 | 12936 | 0 | 12936 | 1811.04 | 0 | 0 | 0 | 0 | 0 | 14747.04 | 14747
| 504030000 | 850 x 650 = 1 Sq.m. | [8 empty] | Nos. | 2 | 11779 | 0 | 11779 | 1649.06 | 0 | 0 | 0 | 0 | 0 | 13428.06 | 26856
| 504030000 | 850 x 400 = 0.5 Sq.m. | [8 empty] | Nos. | 2 | 9481 | 0 | 9481 | 1327.34 | 0 | 0 | 0 | 0 | 0 | 10808.34 | 21617
| 504030000 | 850 x 300 = 0.5 Sq.m. | [8 empty] | Nos. | 1 | 9073 | 0 | 9073 | 1270.22 | 0 | 0 | 0 | 0 | 0 | 10343.22 | 10343
| 504030000 | 850 x 250 = 0.5 Sq.m. | [8 empty] | Nos. | 1 | 8614 | 0 | 8614 | 1205.96 | 0 | 0 | 0 | 0 | 0 | 9819.96 | 9820
| 504030000 | 800 x 400 = 0.5 Sq.m. | [8 empty] | Nos. | 6 | 9345 | 0 | 9345 | 1308.3 | 0 | 0 | 0 | 0 | 0 | 10653.3 | 63920
| 504030000 | 800 x 350 = 0.5 Sq.m. | [8 empty] | Nos. | 2 | 9073 | 0 | 9073 | 1270.22 | 0 | 0 | 0 | 0 | 0 | 10343.22 | 20686
| 504030000 | 750 x 700 = 1 Sq.m. | [8 empty] | Nos. | 2 | 11591 | 0 | 11591 | 1622.74 | 0 | 0 | 0 | 0 | 0 | 13213.74 | 26427
| 504030000 | 750 x 500 = 0.5 Sq.m. | [8 empty] | Nos. | 1 | 10571 | 0 | 10571 | 1479.94 | 0 | 0 | 0 | 0 | 0 | 12050.94 | 12051
| 504030000 | 750 x 300 = 0.5 Sq.m. | [8 empty] | Nos. | 2 | 8698 | 0 | 8698 | 1217.72 | 0 | 0 | 0 | 0 | 0 | 9915.72 | 19831
| 504030000 | 700 x 500 = 0.5 Sq.m. | [8 empty] | Nos. | 2 | 9550 | 0 | 9550 | 1337 | 0 | 0 | 0 | 0 | 0 | 10887 | 21774
| 504030000 | 700 x 450 = 0.5 Sq.m. | [8 empty] | Nos. | 2 | 9311 | 0 | 9311 | 1303.54 | 0 | 0 | 0 | 0 | 0 | 10614.54 | 21229
| 504030000 | 700 x 400 = 0.5 Sq.m. | [8 empty] | Nos. | 2 | 9073 | 0 | 9073 | 1270.22 | 0 | 0 | 0 | 0 | 0 | 10343.22 | 20686
| 504030000 | 650 x 300 = 0.5 Sq.m. | [8 empty] | Nos. | 2 | 8494 | 0 | 8494 | 1189.16 | 0 | 0 | 0 | 0 | 0 | 9683.16 | 19366
| 504030000 | 600 x 650 = 0.5 Sq.m. | [8 empty] | Nos. | 2 | 10673 | 0 | 10673 | 1494.22 | 0 | 0 | 0 | 0 | 0 | 12167.22 | 24334
| 504030000 | 600 x 400 = 0.5 Sq.m. | [8 empty] | Nos. | 2 | 8801 | 0 | 8801 | 1232.14 | 0 | 0 | 0 | 0 | 0 | 10033.14 | 20066
| 504030000 | 600 x 350 = 0.5 Sq.m. | [8 empty] | Nos. | 13 | 8597 | 0 | 8597 | 1203.58 | 0 | 0 | 0 | 0 | 0 | 9800.58 | 127408
| 504030000 | 550 x 400 = 0.5 Sq.m. | [8 empty] | Nos. | 1 | 8665 | 0 | 8665 | 1213.1 | 0 | 0 | 0 | 0 | 0 | 9878.1 | 9878
| 504030000 | 500 x 750 = 0.5 Sq.m. | [8 empty] | Nos. | 5 | 10571 | 0 | 10571 | 1479.94 | 0 | 0 | 0 | 0 | 0 | 12050.94 | 60255
| 504030000 | 500 x 400 = 0.5 Sq.m. | [8 empty] | Nos. | 3 | 8529 | 0 | 8529 | 1194.06 | 0 | 0 | 0 | 0 | 0 | 9723.06 | 29169
| 504030000 | 500 x 300 = 0.5 Sq.m. | [8 empty] | Nos. | 35 | 8188 | 0 | 8188 | 1146.32 | 0 | 0 | 0 | 0 | 0 | 9334.32 | 326701
| 504030000 | 450 x 450 = 0.5 Sq.m. | [8 empty] | Nos. | 2 | 8545 | 0 | 8545 | 1196.3 | 0 | 0 | 0 | 0 | 0 | 9741.3 | 19483
| 504030000 | 450 x 400 = 0.5 Sq.m. | [8 empty] | Nos. | 2 | 8392 | 0 | 8392 | 1174.88 | 0 | 0 | 0 | 0 | 0 | 9566.88 | 19134
| 504030000 | 450 x 200 = 0.5 Sq.m. | [8 empty] | Nos. | 2 | 7848 | 0 | 7848 | 1098.72 | 0 | 0 | 0 | 0 | 0 | 8946.72 | 17893
| 504030000 | 400 x 300 = 0.5 Sq.m. | [8 empty] | Nos. | 28 | 7985 | 0 | 7985 | 1117.9 | 0 | 0 | 0 | 0 | 0 | 9102.9 | 254881
| 504030000 | 400 x 250 = 0.5 Sq.m. | [8 empty] | Nos. | 5 | 7848 | 0 | 7848 | 1098.72 | 0 | 0 | 0 | 0 | 0 | 8946.72 | 44734
| 504030000 | 400 x 200 = 0.5 Sq.m. | [8 empty] | Nos. | 2 | 7848 | 0 | 7848 | 1098.72 | 0 | 0 | 0 | 0 | 0 | 8946.72 | 17893
| 504030000 | 350 x 900 = 0.5 Sq.m. | [8 empty] | Nos. | 6 | 10163 | 0 | 10163 | 1422.82 | 0 | 0 | 0 | 0 | 0 | 11585.82 | 69515
| 504030000 | 350 x 200 = 0.5 Sq.m. | [8 empty] | Nos. | 1 | 7848 | 0 | 7848 | 1098.72 | 0 | 0 | 0 | 0 | 0 | 8946.72 | 8947
| 504030000 | 300 x 300 = 0.5 Sq.m. | [8 empty] | Nos. | 4 | 7848 | 0 | 7848 | 1098.72 | 0 | 0 | 0 | 0 | 0 | 8946.72 | 35787
| 504030000 | 250 x 250 = 0.5 Sq.m. | [8 empty] | Nos. | 2 | 7848 | 0 | 7848 | 1098.72 | 0 | 0 | 0 | 0 | 0 | 8946.72 | 17893
| 504030000 | 250 x 200 = 0.5 Sq.m. | [8 empty] | Nos. | 2 | 7848 | 0 | 7848 | 1098.72 | 0 | 0 | 0 | 0 | 0 | 8946.72 | 17893
| 504030000 | 200 x 150 = 0.5 Sq.m. | [8 empty] | Nos. | 20 | 7848 | 0 | 7848 | 1098.72 | 0 | 0 | 0 | 0 | 0 | 8946.72 | 178934
| 504030000 | 200 x 100 = 0.5 Sq.m. | [8 empty] | Nos. | 47 | 7848 | 0 | 7848 | 1098.72 | 0 | 0 | 0 | 0 | 0 | 8946.72 | 420496
| 504030000 | 100 x 100 = 0.5 Sq.m. | [8 empty] | Nos. | 15 | 7848 | 0 | 7848 | 1098.72 | 0 | 0 | 0 | 0 | 0 | 8946.72 | 134201
| 504030000 | Total Qty. | [8 empty] | Sq.M. | 37 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.2 | 504030000 | Actuators (above 1600mm size to be provided with 2 actuators) | [8 empty] | Nos. | 21 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.3 | 504030000 | Control Panel & Wiring (cost for all 6.1 to 6.2) | [8 empty] | Nos. | 21 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.4 | 504030000 | Fire damper with fusible links to be provided in duct collars. | [8 empty] | sq.m | 2 | 7375 | 0 | 7375 | 1032.5 | 0 | 0 | 0 | 0 | 0 | 8407.5 | 16815
6 | 504030000 | Supply of powder coated Extruded Aluminium exhaust air Grilles with volume control dampers in accordance with the approved shop drawings and specifications. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6.1 | 504030000 | With adjustable double louvers. | [8 empty] | sq.m | 1 | 7379 | 0 | 7379 | 1033.06 | 0 | 0 | 0 | 0 | 0 | 8412.06 | 8412
6.2 | 504030000 | With horizontal fixed bars (For Toilet Exhaust) | [8 empty] | sq.m | 20 | 5969 | 0 | 5969 | 835.66 | 0 | 0 | 0 | 0 | 0 | 6804.66 | 136093
7 | 504030000 | Supply of Air Grilles without volume control dampers. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7.1 | 504030000 | With adjustable double louvers powder coated extruded aluminium. | [8 empty] | sq.m | 100 | 4652 | 0 | 4652 | 651.28 | 0 | 0 | 0 | 0 | 0 | 5303.28 | 530328
7.2 | 504030000 | With horizontal fixed bars for Guest Room FCU powder coated extruded aluminium (subject to final interior design). | [8 empty] | sq.m | 100 | 3242 | 0 | 3242 | 453.88 | 0 | 0 | 0 | 0 | 0 | 3695.88 | 369588
8 | 504030000 | Supply of square shape ceiling diffusers with removable core & anti smudge ring & volume control dampers as per approved drawings and specifications. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8.1 | 504030000 | Powder coated extruded aluminium construction. | [8 empty] | sq.m | 40 | 8312 | 0 | 8312 | 1163.68 | 0 | 0 | 0 | 0 | 0 | 9475.68 | 379027
8.2 | 504030000 | Powder coated MS construction.l | [8 empty] | sq.m | 1 | 8312 | 0 | 8312 | 1163.68 | 0 | 0 | 0 | 0 | 0 | 9475.68 | 9476
9 | 504030000 | Supply of square shape return air diffusers with removable core, antismudge ring & without volume control damper as per specifications. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.1 | 504030000 | Powder coated extruded aluminiumm construction | [8 empty] | sq.m | 25 | 5584 | 0 | 5584 | 781.76 | 0 | 0 | 0 | 0 | 0 | 6365.76 | 159144
9.2 | 504030000 | Powder coated MS construction | [8 empty] | sq.m | 1 | 5584 | 0 | 5584 | 781.76 | 0 | 0 | 0 | 0 | 0 | 6365.76 | 6366
10 | 504030000 | Supply of supply air and return air grilles in accordance with the approved shop drawings and specifications for Parking, Mechanical and Back of the house areas. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10.1 | 504030000 | Powder coated MS Grilles with volume control dampers and adjustable louvers. | [8 empty] | sq.m | 45 | 7379 | 0 | 7379 | 1033.06 | 0 | 0 | 0 | 0 | 0 | 8412.06 | 378543
11 | 504030000 | Supply of supply air and return air, square / round shaped diffusers volume damper as per specifications for back of the house areas. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11.1 | 504030000 | Powder coated MS Diffusers with volume control damper for supply air. | [8 empty] | sq.m | 3 | 8312 | 0 | 8312 | 1163.68 | 0 | 0 | 0 | 0 | 0 | 9475.68 | 28427
11.2 | 504030000 | Powder coated MS Diffusers without volume control damper for return air. | [8 empty] | sq.m | 5 | 5584 | 0 | 5584 | 781.76 | 0 | 0 | 0 | 0 | 0 | 6365.76 | 31829
12 | 504030000 | Supply of constant volume damper as per specifications for guest rooms with the air flow capacity mentioned below. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12.1 | 504030000 | 50 cfm | [8 empty] | Nos. | 225 | 1943 | 0 | 1943 | 272.02 | 0 | 0 | 0 | 0 | 0 | 2215.02 | 498380
12.2 | 504030000 | 60 cfm | [8 empty] | Nos. | 225 | 1943 | 0 | 1943 | 272.02 | 0 | 0 | 0 | 0 | 0 | 2215.02 | 498380
13 | 504030000 | Supply of Linear Grilles with removable core and volume control damper as per approved drawings and specifications (subject to final interior design). | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13.1 | 504030000 | Powder coated extruded aluminium construction..n | [8 empty] | sq.m | 5 | 5969 | 0 | 5969 | 835.66 | 0 | 0 | 0 | 0 | 0 | 6804.66 | 34023
13.2 | 504030000 | Powder coated MS constructions | [8 empty] | sq.m | 1 | 5969 | 0 | 5969 | 835.66 | 0 | 0 | 0 | 0 | 0 | 6804.66 | 6805
14 | 504030000 | Supply of Powder Coated Extruded Aluminium Linear supply Air Multi Slot Diffuser complete with air pattern controllers & Hit & Miss volume control damper with acoustically line 22 G G.I plenum as per specifications and approved drawings. | [8 empty] | sq.m | 90 | 7456 | 0 | 7456 | 1043.84 | 0 | 0 | 0 | 0 | 0 | 8499.84 | 764986
15 | 504030000 | Supply of Powder Coated Extruded Aluminium Multi Slot return Air Diffuser with air pattern controller as per specification and approved drawings. | [8 empty] | sq.m | 135 | 6410 | 0 | 6410 | 897.4 | 0 | 0 | 0 | 0 | 0 | 7307.4 | 986499
16 | 504030000 | Supplying of opposed blade volume control dampers in supply air duct collars as per approved drawings and specifications. Damper shall be with 18G GSS body and blades shall be with aluminium airfoil construction. | [8 empty] | sq.m | 80 | 7700 | 0 | 7700 | 1078 | 0 | 0 | 0 | 0 | 0 | 8778 | 702240
17 | 504030000 | Supply of inlet air louvers with bird screen and volume damper for fresh air as per specifications and approved shop drawings. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17.1 | 504030000 | Powder coated/Anodised extruded aluminium construction. | [8 empty] | sq.m | 140 | 6628 | 0 | 6628 | 927.92 | 0 | 0 | 0 | 0 | 0 | 7555.92 | 1057829
17.2 | 504030000 | Powder coated MS constructionm | [8 empty] | sq.m | 1 | 6628 | 0 | 6628 | 927.92 | 0 | 0 | 0 | 0 | 0 | 7555.92 | 7556
18 | 504030000 | Supply of louvers with bird screen for exhaust air as per specifications and approved drawings. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18.1 | 504030000 | Powder coated/Anodised extruded aluminium constructionn. | [8 empty] | sq.m | 30 | 3900 | 0 | 3900 | 546 | 0 | 0 | 0 | 0 | 0 | 4446 | 133380
18.2 | 504030000 | Powder coated MS constructionn | [8 empty] | sq.m | 1 | 3900 | 0 | 3900 | 546 | 0 | 0 | 0 | 0 | 0 | 4446 | 4446
19 | 504030000 | Motorised fresh air dampers with controllers. Damper actuator shall work on 230 V supply (derived from AHU starter panel). Controller shall receive 4-20 mA / 0-10 V control signal from remote BMS system & accordingly modulate fresh air quantity to the AHU. Control shall give feed back signal to remote BMS System. Fresh air dampers shall be modulated based on signal recieved from CO2 sensors. (CO2 sensors shall be by others). | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19.1 | 504030000 | Fresh Air Damper | [8 empty] | sq.m | 5 | 7700 | 0 | 7700 | 1078 | 0 | 0 | 0 | 0 | 0 | 8778 | 43890
19.2 | 504030000 | Control Panel & Wiringee | [8 empty] | Nos. | 17 | 1803 | 0 | 1803 | 252.42 | 0 | 0 | 0 | 0 | 0 | 2055.42 | 34942
19.3 | 504030000 | Actuatorr | [8 empty] | Nos. | 17 | 6541 | 0 | 6541 | 915.74 | 0 | 0 | 0 | 0 | 0 | 7456.74 | 126765
20 | 504030000 | Motorised dampers with controllers for smoke Management in basements. Damper actuator shall work on 230 V supply (derived from fan starter panel). Controller shall receive 4-20 mA / 0-10 V control signal from remote Fire alarm system & accordingly open the dampers for required operation. Control shall give feed back signal to remote BMS System. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20.1 | 504030000 | Dampers | [8 empty] | sq.m | 12 | 7700 | 0 | 7700 | 1078 | 0 | 0 | 0 | 0 | 0 | 8778 | 105336
20.2 | 504030000 | Control Panel & Wiring | [8 empty] | Nos. | 10 | 1803 | 0 | 1803 | 252.42 | 0 | 0 | 0 | 0 | 0 | 2055.42 | 20554
20.3 | 504030000 | Actuator | [8 empty] | Nos. | 10 | 6541 | 0 | 6541 | 915.74 | 0 | 0 | 0 | 0 | 0 | 7456.74 | 74567
E - 1 | 504030000 | THERMAL INSULATION | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 504030000 | Supplying of 19 mm thick Closed cell nitrile rubber Class O with factory laminated black treated woven glass cloth on chilled water and condensate drain piping and fitting like valves, flanges union, etc. as per the approved shop drawings and specifications. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.1 | 504030000 | 50 mm dia pipes | [8 empty] | RM | 100 | 305 | 0 | 305 | 42.7 | 0 | 0 | 0 | 0 | 0 | 347.7 | 34770
1.2 | 504030000 | 40 mm dia pipese | [8 empty] | RM | 110 | 271 | 0 | 271 | 37.94 | 0 | 0 | 0 | 0 | 0 | 308.94 | 33983
1.3 | 504030000 | 25 mm dia pipes | [8 empty] | RM | 1100 | 233 | 0 | 233 | 32.62 | 0 | 0 | 0 | 0 | 0 | 265.62 | 292182
2 | 504030000 | Supply of External Thermal insulation with protective coating on ducts as per the specifications. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.1 | 504030000 | Insulation with 50mm thick 32 kg/cu.mtr density fiber glass winsulation with factory laminated Alu glass external surface. | [8 empty] | sq.mtr | 11000 | 331 | 0 | 331 | 16.55 | 0 | 0 | 0 | 0 | 0 | 347.55 | 3823050
2.2 | 504030000 | Insulation with 50mm thick 32 kg/cu.mtr density fiber glass insulation with factory laminated Alu glass external surface. | [8 empty] | Sq.mtr | 750 | 331 | 0 | 331 | 16.55 | 0 | 0 | 0 | 0 | 0 | 347.55 | 260663
2.3 | 504030000 | Supply of Fibreglass insulation, 24 kg / m3 density, and Alu Glass lamination face as per specifications for kitchen exhaust ducting. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.3.1 | 504030000 | 50 mm thick | [8 empty] | sq.m | 1750 | 274 | 0 | 274 | 13.7 | 0 | 0 | 0 | 0 | 0 | 287.7 | 503475
3 | 504030000 | Supply of acoustic insulation. Material shall be Class 1 open cell nitrile rubber and all accessories as per specification. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.1 | 504030000 | 15mm thick | [8 empty] | sq.m | 1200 | 1062 | 0 | 1062 | 53.1 | 0 | 0 | 0 | 0 | 0 | 1115.1 | 1338120
| 504030000 | All walls and ceiling of the room shall be provided with acoustic lining of resin bonded fiberglass/ mineral wool with minimum density @ 48 Kg / M3 as per Schedule of Quantities. The surface shall be cleaned and frame work of 22 gage GI fabricated Channels 50 mm x 75 mm screwed back to back at 60 cm centres shall be provided vertically and horizontally so that 60 x 60 cm squares are formed. The gaps between frames shall be filled with 75 mm thick about 60 cm x 60 cm cut panels of resin bonded fiberglass /mineral wool slabs. The entire surface shall then be covered with fibreglass tissue and 22 gauge perforated aluminium sheet, 60 cm or 120 cm wide having atleast 15 percent perforations, fixed with sheet metal screws.(Rivets with powder coating) Over-lapping of sheets shall be covered with Aluminium beading. Acoustic lining of walls shall be terminated approximately 15 cm above the finished floor to prevent damage to insulation due to accidental water-logging. A minimum airgap of 25mm shall be provided between the wall and wall insulation material. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 504030000 | 50mm thick | [8 empty] | sq.m | 356 | 712 | 0 | 712 | 35.6 | 0 | 0 | 0 | 0 | 0 | 747.6 | 266146
| 504030000 | [9 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4.1 | 504030000 | 100mm thick | [8 empty] | sq.m | 95 | 1039 | 0 | 1039 | 51.95 | 0 | 0 | 0 | 0 | 0 | 1090.95 | 103640
5 | 504030000 | Supply of 25 mm thick Closed cell nitrile rubber Class O with factory laminated black treated woven glass cloth on chilled water pipes and fittings like valves, flanges and unions, etc. as per approved shop drawings and specifications. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.1 | 504030000 | 100 mm dia pipesg | [8 empty] | RM | 100 | 778 | 0 | 778 | 108.92 | 0 | 0 | 0 | 0 | 0 | 886.92 | 88692
5.2 | 504030000 | 80 mm dia pipes | [8 empty] | RM | 160 | 555 | 0 | 555 | 77.7 | 0 | 0 | 0 | 0 | 0 | 632.7 | 101232
5.3 | 504030000 | 65 mm dia pipes | [8 empty] | RM | 290 | 496 | 0 | 496 | 69.44 | 0 | 0 | 0 | 0 | 0 | 565.44 | 163978
5.4 | 504030000 | 50 mm dia pipes | [8 empty] | RM | 695 | 448 | 0 | 448 | 62.72 | 0 | 0 | 0 | 0 | 0 | 510.72 | 354950
5.5 | 504030000 | 40 mm dia pipes | [8 empty] | RM | 325 | 371 | 0 | 371 | 51.94 | 0 | 0 | 0 | 0 | 0 | 422.94 | 137456
5.6 | 504030000 | 32 mm dia pipes | [8 empty] | RM | 550 | 343 | 0 | 343 | 48.02 | 0 | 0 | 0 | 0 | 0 | 391.02 | 215061
5.7 | 504030000 | 25 mm dia pipes;d | [8 empty] | RM | 2500 | 328 | 0 | 328 | 45.92 | 0 | 0 | 0 | 0 | 0 | 373.92 | 934800
6 | 504030000 | Supply of 32 mm thick Closed cell nitrile rubber Class O with factory laminated black treated woven glass cloth on chilled water pipes and fittings like valves, flanges and unions, etc. as per approved shop drawings and specifications. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6.1 | 504030000 | 250 mm dia pipes | [8 empty] | RM | 1 | 1057 | 0 | 1057 | 52.85 | 0 | 0 | 0 | 0 | 0 | 1109.85 | 1110
6.2 | 504030000 | 200 mm dia pipesl | [8 empty] | RM | 145 | 895 | 0 | 895 | 44.75 | 0 | 0 | 0 | 0 | 0 | 939.75 | 136264
6.3 | 504030000 | 150 mm dia pipese | [8 empty] | RM | 225 | 733 | 0 | 733 | 36.65 | 0 | 0 | 0 | 0 | 0 | 769.65 | 173171
6.4 | 504030000 | 125 mm dia pipes | [8 empty] | RM | 70 | 652 | 0 | 652 | 32.6 | 0 | 0 | 0 | 0 | 0 | 684.6 | 47922

## Certification
Scenario 2
Local Supply |  |  | COP-R001 | [22 empty] | 7701827.85 | 0 | 7701827.85 | 782471.817 | 0 | 0 | 0 | 0 | 0 | 8484299.667
|  | UNIQUE IDENTIFIERS | [8 empty] | UOM | QTY | RATE (can be entered directly or summed up for totals)
Sr. No. | Item Range Code | Description | Area | Make | Model No./ Product Code | Tag/ Item No. | ITC HS Code | Country of Origin | Port of Loading | User defined column |  |  | Local supply rate | [10 empty] | COP Cerification
[13 empty] | Basic Rate | Excise | Subtotal = Basic + Excise | VAT/CST on Subtotal | Octroi / LBT | Insurance | Freight | Packing & Forwarding | Other | Supply Rate Total | AMOUNT | COP Percentage | COP Quantity | COP Basic | COP Excise | COP SUB Total=COP Basic+COP Excise | COP VAT/CST on Subtotal | COP Octroi / LBT | COP Insurance | COP Freight | COP Packing & Forwarding | COP Other | Final COP Amount
A. | 504010000 | EQUIPMENT (IMPORTED) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 504010000 | Testing and commissioning of multiple compressor SCREW WATER CHILLING UNITS each complete with 250 TR capacity (total) screw compressors with Constant speed Drive, motor, starter panel machine mounted with adaptor box consisting of tinned copper busbar suitable for termination of 2 nos 185 sqmm Al. Armoured cable , water cooled condenser, insulated chiller, flow switch at chiller and condenser, vibration isolators, integral refrigerant piping and wiring, BMS interface unit (Tracer / Microgateway / Datalink) grooved couplings for condenser and cooler water in/out connections, complete charge of refrigerant and oil, accessories as required and called for, automatic and safety controls mounted in central micro-processor based console panel and all mounted on a steel frame complete as per specifications. Motor shall be suitable for 415±10% 50 cycles. 3 phase AC supply and motor cable terminal box shall be suitable to connect Aluminium Cabling. Refrigerant used shall be Ozone friendly HFC-134a as detailed in specifications. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Chiller | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Chiller Water IN 53°F | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Chilled Water OUT 43°F | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Fouling factor 0.0005 FPS | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Condenser | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Condenser Water IN 88.4°F(Amb. Wet bulb+5.40F) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Condenser Water OUT 98.4°F(∆T of 10oF) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Fouling factor 0.001 FPS | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Maximum Power Consumed at design conditions : Not greater than 0.6 IkW/TR @100% Load | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Test Standard : 550/590-1998 | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.1 | 504010000 | Supply imported portion of above chillers CIF (Delhi). | [8 empty] | Nos. | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.2 | 504010000 | Indicate for all chillers port charges, port handling charges, other local duties, loading, transportation/insurance upto site, octroi charges and all other taxes and incidentals complete till delivered at site.l | [8 empty] | Nos. | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.3 | 504010000 | Customs duty and countervailing duty for the above imported equipment.i | [8 empty] | Nos | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.4 | 504010000 | Receiving at site above imported equipment, unloading, storing, handling hoisting, installing in position, effecting connections, anchoring, grouting testing and commissioning above equipment including supplying & installing all necessary indigenous accessories as required to complete the installation. | [8 empty] | Nos. | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 504010000 | Supplying of CENTRIFUGAL PUMPS, factory mounted on a common base with electric motor for recirculation of water for the central air conditioning system as per specifications. All pumps shall be aligned properly as required. The pump motor shall be suitable for 415 ± 10% volts, 50 cycles, 3 phase power supply. The motor selected shall be energy efficient having efficiency (EFF I) at full load ranging between 91.5% to 94% in accordance with motor rating as per specification. Minimum pump efficiency shall be 75%. The quoted price shall include cost of thermal insulation and cladding for item 2.1. Pumps with performance characteristics as given below : | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Primary Chilled water pumps | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Water flow rate = 600 USGPM | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Head = 45 Ft. of water | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Motor KW = 7.5 (10 HP). | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Quantity indicated includes one standby…. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.1 | 504010000 | Supply imported portion of above pumps CIF (Delhi) | [8 empty] | Nos | 3 | 79768 | 0 | 79768 | 3988.4 | 0 | 0 | 0 | 0 | 0 | 83756.4 | 251269 | 15 | 3 | 35895.6 | 0 | 35895.6 | 1794.78 | 0 | 0 | 0 | 0 | 0 | 37690.38
2.2 | 504010000 | Indicate for all chillers port charges, port handling charges, other local duties, loading, transportation/insurance upto site, octroi charges and all other taxes and incidentals complete till delivered at site… | [8 empty] | Nos | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.3 | 504010000 | Customs duty and countervailing duty for the above imported equipment…n | [8 empty] | Nos. | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.4 | 504010000 | Receiving at site above imported equipment, unloading, storing, handling hoisting, installing in position, effecting connections, anchoring, grouting testing and commissioning above equipment including supplying & installing all necessary indigenous accessories as required to complete the installation. | [8 empty] | Nos | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 504010000 | Supplying of CENTRIFUGAL PUMPS, factory mounted on a common base with electric motor for recirculation of cooling water for the central air conditioning system. All pumps shall be aligned properly as required as per specifications.Minimum efficiency of the pump shall be 75%. The pump motor shall be suitable for 415 ± 10% volts, 50 cycles, 3 phase power supply. The motor selected shall be energy efficient having efficiency (EFF 1) at full load ranging between 91.5% to 94% in accordance with motor rating as per specification. The performance shall be as given below : | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.1 | 504010000 | Condensing water pumps | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Water flow rate = 750 USGPM | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Head = 113 Ft. of water | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Motor KW = 30 (40 HP) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Quantity indicated includes one standby… | [8 empty] | Nos. | 3 | 154909 | 0 | 154909 | 7745.45 | 0 | 0 | 0 | 0 | 0 | 162654.45 | 487963 | 15 | 3 | 69709.05 | 0 | 69709.05 | 3485.4525 | 0 | 0 | 0 | 0 | 0 | 73194.5025
| 504010000 | Condensing water pumps - For Cold Storages in BOH | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Water flow rate = 300 USGPM | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Head = 80 Ft. of water | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Motor KW = 7.5 (10 HP) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Quantity indicated includes one standby.. | [8 empty] | Nos. | 2 | 92946 | 0 | 92946 | 4647.3 | 0 | 0 | 0 | 0 | 0 | 97593.3 | 195187 | 15 | 2 | 27883.8 | 0 | 27883.8 | 1394.19 | 0 | 0 | 0 | 0 | 0 | 29277.99
3.1.1 | 504010000 | Supply imported portion of above chillers CIF (Delhi) | [8 empty] | Nos | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.1.2 | 504010000 | Indicate for all chillers port charges, port handling charges, other local duties, loading, transportation/insurance upto site, octroi charges and all other taxes and incidentals complete till delivered at site. | [8 empty] | Nos | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.1.3 | 504010000 | Customs duty and countervailing duty for the above imported equipment… | [8 empty] | Nos. | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.1.4 | 504010000 | Receiving at site above imported equipment, unloading, storing, handling hoisting, installing in position, effecting connections, anchoring, grouting testing and commissioning above equipment including supplying & installing all necessary indigenous accessories as required to complete the installation. | [8 empty] | Nos | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 504010000 | Supplying of CENTRIFUGAL CASING PUMPS, factory mounted on a common base with electric motor for recirculation of water for the central air conditioning system as per specifications. Minimum pump hydraulic efficiency shall be 75%. All pumps shall be aligned properly as required. The pump motor shall be suitable for 415 + 10% volts, 50 cycles, 3 phase power supply. The motors of secondary chilled water pumps shall be suitable for operation on adjustable frequency drive. The motor selected shall be energy efficient having efficiency (Class I) at full load ranging between 91.5% to 94% in accordance with motor rating as per specification. The quoted price shall include cost of thermal insulation and cladding for item 12.1.1, 12.1.2 & 12.1.3. Pumps with performance characteristics as given below : | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4.1 | 504010000 | Supply imported portion of following pumps CIF Delhi | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4.1.1 | 504010000 | Secondary Chilled Water pumps | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Zone A | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Water flow rate = 400 USGPM | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Head = 70 Ft. of water | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Motor kW = 8.5 (12.5 HP) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Quantity indicated includes one standby.m | [8 empty] | Nos. | 3 | 94692 | 0 | 94692 | 4734.6 | 0 | 0 | 0 | 0 | 0 | 99426.6 | 298280 | 15 | 3 | 42611.4 | 0 | 42611.4 | 2130.57 | 0 | 0 | 0 | 0 | 0 | 44741.97
4.1.2 | 504010000 | Zone B | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Water flow rate = 600 USGPM | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Head = 75 Ft. of water | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Motor HP = 10 (15 HP) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Quantity indicated includes one standby. | [8 empty] | Nos. | 3 | 125291 | 0 | 125291 | 6264.55 | 0 | 0 | 0 | 0 | 0 | 131555.55 | 394667 | 15 | 3 | 56380.95 | 0 | 56380.95 | 2819.0475 | 0 | 0 | 0 | 0 | 0 | 59199.9975
4.2 | 504010000 | Indicate for all pumps port charges, port handling charges, other local duties, loading, transportation /insurance upto site, octroi charges and all other taxes and incidentals complete till delivered at site. | [8 empty] | Nos. | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4.3 | 504010000 | Customs duty and countervailing duty for the above imported equipment.o | [8 empty] | Nos. | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4.4 | 504010000 | Receiving at site above imported equipment, unloading, storing, handling hoisting, installing in position, effecting connections, anchoring, grouting testing and commissioning above equipment including supplying and installing all necessary indigenous accessories as required to complete the installation. | [8 empty] | Nos. | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 504010000 | Supplying of VARIABLE SPEED PUMPING SYSTEM consisting of adjustable frequency drive (AFD) for each pump, one dedicated microprocessor based pump controller per zone housed within the enclosure of one of the AFD with parallel pumping software duly down loaded and multiple differential pressure sensor / transmitters along with complete control cabling from transmitter to AFD Panel as per the site requirement. The entire system along with primary / secondary pumps as described under item 3 must be sourced from single manufacturer only, to ensure unit responsibility. Necessary factory test certificates for entire system shall be submitted along with the equipment. Sensor / Transmitters as described in specification. System shall be BMS compatible with open protocol communication port, so that complete data can be transported to remote IBMS console. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | The system shall be complete in all respects and suitable for following motor ratings : | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.1 | 504010000 | Supply Imported portion of AFD, Pump Controller & Sensor Transmitters CIF (Delhi) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.1.1 | 504010000 | 8.5 KW | [8 empty] | Nos. | 3 | 87968 | 0 | 87968 | 12315.52 | 0 | 0 | 0 | 0 | 0 | 100283.52 | 300851 | 15 | 3 | 39585.6 | 0 | 39585.6 | 5541.984 | 0 | 0 | 0 | 0 | 0 | 45127.584
5.1.2 | 504010000 | 10 KW | [8 empty] | Nos. | 3 | 98265 | 0 | 98265 | 13757.1 | 0 | 0 | 0 | 0 | 0 | 112022.1 | 336066 | 15 | 3 | 44219.25 | 0 | 44219.25 | 6190.695 | 0 | 0 | 0 | 0 | 0 | 50409.945
5.2 | 504010000 | Indicate for all equipment port charges, port handling charges, other local duties, loading, transportation/insurance upto site, octroi charges and all other taxes and incidentals complete till delivered at site. | [8 empty] | Nos. | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.3 | 504010000 | Customs duty and countervailing duty for the above imyported equipment. | [8 empty] | Nos. | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.4 | 504010000 | Receiving at site above imported equipment, unloading, storing, handling hoisting, installing in position, effecting connections, anchoring, grouting testing and commissioning above equipment including supplying & installing all necessary indigenous accessories as required to complete the installation. | [8 empty] | Nos. | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 504020000 | Installing, testing and commissioning of horizontal FAN COIL UNITS (2 PIPE SYSTEMS), blow thru type, each complete with 3 rows deep Chilled Water Coil, one or more centrifugal fans, cleanable fabric filters, main condensate extended SS drain pans, RA insulated plenum, as described in specifications, casing, coil piping connections, through copper pipes, condensate drain connections, wiring, control wiring in conduit upto thermostat boxes. Installation shall be considered with supply and installation of valve package comprising of pressure independent balancing cum control valve with integrated 2 way motorized actuator in a single body for modulating operation suitable for static pressure of 1600 kPa and actuator shall be capable of withstanding 400 kPa shut off pressure, 24 V AC incoming power supply, ball valve with Y-strainer at inlet & Ball valve at outlet and necessary copper coil piping connections. The actuator of modulating valve shall be provided with interface cards to receive 0-10V or 4-20 mA signal from Digital Thermostat. (Temporary bypass arrangement in chilled water line with related accesories to be considered to facililate flushing during precommissioning and commissioning of the system). cost shall include 4Cx10sqmm YRY cable from FCU to Thermostat (10 mtrs) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504020000 | The actuator of the valve shall have necessary torque to overcome pressure differential of 4 bars rating. All fan coil units shall be suitable for 220±6% volts, 50 cycles, single phase power supply. Fan coil units shall be of following refrigeration capacities as listed. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6.1 | 504020000 | Supply imported portion of above Fan Coil Units CIF (Delhi) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504020000 | Horizontal unit with cabinet (Ceiling Hung) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6.1.1 | 504020000 | 1.5 TR nominal capacity - 650 CFM | [8 empty] | Nos. | 246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6.1.2 | 504020000 | 2 TR nominal capacity - 850 CFM | [8 empty] | Nos. | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6.1.3 | 504020000 | 2.5 TR nominal capacity - 1050 CFM | [8 empty] | Nos. | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6.1.4 | 504020000 | 1.5 TR High Static - 650 CFM | [8 empty] | Nos. | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6.1.5 | 504020000 | 2 TR High Static - 850 CFM | [8 empty] | Nos. | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6.1.6 | 504020000 | 2.5 TR High Static - 1050 CFM | [8 empty] | Nos. | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6.2 | 504020000 | Installing in position, effecting connections, anchoring, grouting testing and commissioning above equipment including supplying & installing all necessary indigenous accessories as required to complete the installation. | [8 empty] | Nos. | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 504030000 | Supply of Electronic Self Balancing Valve pressure independent with independent type dynamic balancing valve for AHUs with integrated 2 way modulating control valves in a single body. The actuator shall be capable of accepting 2-10 VDC / 4-20 mA electric signal and shall provide similar transduced feedback output signal to control system for flow measurement. Contractor shall show actual flow measurement v/s flow indicated by valve for atleast 5% of the valves. Necessary instruments for manual flow measurement shall be included. The minimum close off pressure actuator must be 1.5 times shut off head of pump OR 5 bars whichever is maximum. The valves shall be suitable for following pipe sizes: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7.1 | 504030000 | Supply imported portion of the Electronic Self Balancing valve CIF (Delhi): | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7.1.1 | 504030000 | 100 mm dia pipes. | [8 empty] | Nos. | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7.1.2 | 504030000 | 80 mm dia pipes. | [8 empty] | Nos. | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7.1.3 | 504030000 | 65 mm dia pipes. | [8 empty] | Nos. | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7.1.4 | 504030000 | 50 mm dia pipes. | [8 empty] | Nos. | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7.1.5 | 504030000 | 40 mm dia pipes. | [8 empty] | Nos. | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7.1.6 | 504030000 | 32 mm dia pipes. | [8 empty] | Nos. | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7.2 | 504030000 | Indicate for all valves port charges, port handling charges, other local duties, loading, transportation /insurance upto site, octroi charges and all other taxes and incidentals complete till delivered at site. | [8 empty] | Nos. | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7.4 | 504030000 | Receiving at site above imported equipment, unloading, storing, handling hoisting, installing in position, effecting connections, anchoring, grouting testing and commissioning above equipment including supplying and installing all necessary indigenous accessories as required to complete the installation. | [8 empty] | Nos. | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8.1 | 504020000 | Supply imported portion of above Thermostats CIF (Delhi) for working in heating and cooling mode | [8 empty] | Nos. | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8.3 | 504020000 | Indicate for all thermostat port charges, port handling charges, other local duties, loading, transportation /insurance upto site, octroi charges and all other taxes and incidentals complete till delivered at site. | [8 empty] | Nos. | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8.5 | 504020000 | Receiving at site above imported equipment, unloading, storing, handling hoisting, installing in position, effecting connections, anchoring, grouting testing and commissioning above equipment including supplying and installing all necessary indigenous accessories as required to complete the installation. | [8 empty] | Nos. | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 504020000 | Supplying of the following PRESSURE INDEPENDENT AUTO BALANCING VALVES. For condenser and chiller | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.1 | 504020000 | Supply imported portion following automatic balancing valves CIF Delhi. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
a | 504020000 | 300 mm dia. | [8 empty] | Nos. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
b | 504020000 | 250 mm dia. | [8 empty] | Nos. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
c | 504020000 | 200 mm dia. | [8 empty] | Nos. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
d | 504020000 | 150 mm dia. | [8 empty] | Nos. | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
e | 504020000 | 125 mm dia. | [8 empty] | Nos. | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.2 | 504020000 | Indicate for all balancing valves port charges, port handling charges, other local duties, loading, transportation /insurance upto site, octroi charges and all other taxes and incidentals complete till delivered at site. | [8 empty] | Nos. | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.3 | 504020000 | Customs duty and countervailing duty for the abkove imported equipment. | [8 empty] | Nos. | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.4 | 504020000 | Receiving at site above imported equipment, unloading, storing, handling hoisting, installing in position, effecting connections, anchoring, grouting testing and commissioning above equipment including supplying & installing all necessary indigenous accessories as required to complete the installation. | [8 empty] | Nos. | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 504010000 | Supply of INDUCED DRAFT COOLING TOWERS. Fan and motor shall be suitable for VFD. Each tower shall be complete with basin, casing, distribution system, filling, louvers, ladder, fan and motor. Motor shall be suitable for 415±10% volts, 50 cycles, 3 phase power supply, Isolator panel with MCCB at cooling tower and earthing, shall also be included. Tower for airconditioning system shall be selected on the basis of ambient wet bulb 79 oF : Maximum approach accepted is 3 deg.c | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504010000 | Cooling tower shall be of CTI certifed for assured thermal performace. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10.1 | 504010000 | Cooling tower (315 TR) for Water Cooled Screw chillers inlet temperature of 90°F and outlet temperature of 100 °F. | [8 empty] | Nos. | 3 | 499606 | 0 | 499606 | 69944.84 | 0 | 0 | 0 | 0 | 0 | 569550.84 | 1708653 | 15 | 3 | 224822.7 | 0 | 224822.7 | 31475.178 | 0 | 0 | 0 | 0 | 0 | 256297.878
10.2 | 504010000 | Supply imported portion of above Cooling Towers CIF (Delhi): | [8 empty] | Nos. | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10.3 | 504010000 | Indicate for all controls port charges, port handling charges, other local duties, loading, transportation /insurance upto site, octroi charges and all other taxes and incidentals complete till delivered at site. | [8 empty] | Nos. | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10.4 | 504010000 | Customs duty and countervailing duty f/or the above imported equipment. | [8 empty] | Nos. | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10.5 | 504010000 | Receiving at site above imported equipment, unloading, storing, handling hoisting, installing in position, effecting connections, anchoring, grouting testing and commissioning above equipment including supplying & installing all necessary indigenous accessories as required to complete the installation. | [8 empty] | Nos. | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 504030000 | Supply of HVAC dedicated VFDs with minimum IP 20 enclosures & disconnect, complying with the tender specifications and having: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Built-in dual 5% impedance DC link reactor (harmonic filters) on the positive and negative rails of the DC bus of the VFD. THdi shall be maintained < 5%. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Built-in EMC Filters (electromagnetic compatibility filters) for restriction of conducted emissions to comply with IEC61800: 3 (unrestricted distribution):2004 Category C 1 for 50 meters of cable length between motor & VFD, | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Automatic Energy Optimization / Load dependent flux optimization functionality for maximum energy savings. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | MODBUS RTU as the communication protocol between BMS & VFDs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11.1 | 504030000 | The system shall be complete in all respects and suitable for following motor rating: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | SPACE EQUIPMENT NO. MOTOR HP QTY | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Basement-2 Corridor B3-AH-01 5 1 | [8 empty] | Nos. | 1 | 28926 | 0 | 28926 | 4049.64 | 0 | 0 | 0 | 0 | 0 | 32975.64 | 32976 | 15 | 1 | 4338.9 | 0 | 4338.9 | 607.446 | 0 | 0 | 0 | 0 | 0 | 4946.346
| 504030000 | Pre-Function MF-AH-02 7.5 1 | [8 empty] | Nos. | 1 | 33094 | 0 | 33094 | 4633.16 | 0 | 0 | 0 | 0 | 0 | 37727.16 | 37727 | 15 | 1 | 4964.1 | 0 | 4964.1 | 694.974 | 0 | 0 | 0 | 0 | 0 | 5659.074
| 504030000 | Ballroom MF-AH-01 10 1 | [8 empty] | Nos. | 1 | 38117 | 0 | 38117 | 5336.38 | 0 | 0 | 0 | 0 | 0 | 43453.38 | 43453 | 15 | 1 | 5717.55 | 0 | 5717.55 | 800.457 | 0 | 0 | 0 | 0 | 0 | 6518.007
| 504030000 | Lift Lobby / Break-out TF-AH-05 5 1 | [8 empty] | Nos. | 1 | 28926 | 0 | 28926 | 4049.64 | 0 | 0 | 0 | 0 | 0 | 32975.64 | 32976 | 15 | 1 | 4338.9 | 0 | 4338.9 | 607.446 | 0 | 0 | 0 | 0 | 0 | 4946.346
| 504030000 | Lift Lobby / Reception TF-AH-06 5 1 | [8 empty] | Nos. | 1 | 28926 | 0 | 28926 | 4049.64 | 0 | 0 | 0 | 0 | 0 | 32975.64 | 32976 | 15 | 1 | 4338.9 | 0 | 4338.9 | 607.446 | 0 | 0 | 0 | 0 | 0 | 4946.346
| 504030000 | Italian Restaurant TF-AH-07 7.5 1 | [8 empty] | Nos. | 1 | 33094 | 0 | 33094 | 4633.16 | 0 | 0 | 0 | 0 | 0 | 37727.16 | 37727 | 15 | 1 | 4964.1 | 0 | 4964.1 | 694.974 | 0 | 0 | 0 | 0 | 0 | 5659.074
| 504030000 | Chiness Restaurant TF-AH-01 7.5 1 | [8 empty] | Nos. | 1 | 33094 | 0 | 33094 | 4633.16 | 0 | 0 | 0 | 0 | 0 | 37727.16 | 37727 | 15 | 1 | 4964.1 | 0 | 4964.1 | 694.974 | 0 | 0 | 0 | 0 | 0 | 5659.074
| 504030000 | Lounge / Bar TF-AH-03 7.5 1 | [8 empty] | Nos. | 1 | 33094 | 0 | 33094 | 4633.16 | 0 | 0 | 0 | 0 | 0 | 37727.16 | 37727 | 15 | 1 | 4964.1 | 0 | 4964.1 | 694.974 | 0 | 0 | 0 | 0 | 0 | 5659.074
| 504030000 | Regency Club PTF-AH-01 5 1 | [8 empty] | Nos. | 1 | 28926 | 0 | 28926 | 4049.64 | 0 | 0 | 0 | 0 | 0 | 32975.64 | 32976 | 15 | 1 | 4338.9 | 0 | 4338.9 | 607.446 | 0 | 0 | 0 | 0 | 0 | 4946.346
| 504030000 | Cooling Tower 12.5 | [8 empty] | Nos. | 4 | 45277 | 0 | 45277 | 6338.78 | 0 | 0 | 0 | 0 | 0 | 51615.78 | 206463 | 15 | 4 | 27166.2 | 0 | 27166.2 | 3803.268 | 0 | 0 | 0 | 0 | 0 | 30969.468
11.2 | 504030000 | Indicate for all VFD system port charges , port handling charges, other local duties, loading, transportation / insurance upto site, octroi charges and all other taxes and incidentals complete till delivered at site | [8 empty] | Nos. | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11.3 | 504030000 | Customs duty and countervailing duty for the above imported equipment. | [8 empty] | Nos. | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11.4 | 504030000 | Receiving at site above imported equipment, unloading, storing, handling hoisting, installing in position, effecting connections, anchoring, grouting testing and commissioning above equipment including supplying & installing all necessary indigenous accessories as required to complete the installation. | [8 empty] | Nos. | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
B. | 504030000 | EQUIPMENT , | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 504030000 | Supplying of Open type chilled WATER EXPANSION TANK with outdoor weather protected insulation suitable for total volume of water in chilled water circuits along with necessary accessories such as centrifugal air separator, pumps etc. in order to keep chilled water system under (+) pressure and to prevent entrapment of pressure and to prevent entrapment of air in the system. The tank shall be precharged steel expansion tank with replaceable heavy duty butyl rubber bladder. The tank shall have 50 MM system connection and 20 mm drain and charging valve connection to facilitate the on site charging of the tank to meet system requirement. The tank shall be fitted with lifting rings and a floor mounting skirt for vertical installation. The tank and air separator must be constructed in accordance with section VIII of the ASME Boiler and pressure vessel (Unfired)code and stamped 175 PSI working pressure. The complete system shall be sourced from single manufacturer and supplied and installed with all accessories and safety fixtures and safety fixtures required for proper functioning of the complete hydronic system. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Capacity - 2.0 cu.mtr and static head of approximately 75 mtrs | [8 empty] | Nos. | 1 | 44354 | 0 | 44354 | 2217.7 | 0 | 0 | 0 | 0 | 0 | 46571.7 | 46572 | 15 | 1 | 6653.1 | 0 | 6653.1 | 332.655 | 0 | 0 | 0 | 0 | 0 | 6985.755
2 | 504030000 | Supplying of AHU WITH INTEGRAL HEAT RECOVERY PIPE SECTION double skin construction with Thermal Break Profile as per specification. The unit shall comprise of DIDW airfoil backward curve fan with motor and drive package exhaust air, heat pipe section, internal bypass damper for non-fresh air component of return air, and exhaust air VCD for exhaust air and chilled water as per required parameters as listed below. The fan for exhaust air shall be sized for total return air quantity and shall be installed on the exhaust air side of the Heat pipes. The heat pipes shall be installed in vertical position. The exhaust air fan will draw return air from the air-conditioned area and blow it through the heat pipes where transfer of sensible and latent cooling to incoming fresh air shall take place. A bypass damper will allow the non-fresh air component of return air to re-enter the main AHU up stream of the prefilter, while the remaining quantity shall be exhausted. A second volume control damper shall be provided at the exit of heat recovery section to help control the air quantities. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | All VCDs shall be of non leak type. Heat pipes shall be complete with required charge and intercoil connecting piping. AIR HANDLING UNIT Section as per AHU specification, each complete with pre-filter section (90% down to 10 microns), min 6 Row Deep water coil of copper tube & aluminium fins construction,squirrel cage induction motor, airfoil centrifugal fan belt drive and vibration isolators, coil size shall be selected for a maximum face velocity of 500 feet/minute and static pressure shall be as indicated. The motor selected shall be energy efficient having efficiency (EFF 1) at full load ranging between 82.5% to 92% in accordance with motor rating as per specification. Motor shall be suitable for 415±10% volts, 50 cycles, 3 phase AC supply. Fan motor assembly (as whole) shall be statically and dynamically balanced to grade G 6.3 as per ISO-1940/AMCA 204-3. All units shall be complete with opposed blade volume control dampers at oulet, return and fresh air connections. Duct flexible connector (fire proof) shall be provided at outlets and return connection of AHU. For AHUs with VFD, complete equipment shall be designed to limit THDi to less than 5%. Heat pipe medium of heat trasfer shall be water only. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Design conditions shall be as follows | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Fresh Air | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1. DB - 109 deg F (Summer) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 2. WB - 79 deg F(Summer) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1. DB - 94 deg F (Monsoon) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 2. WB - 83 deg F(Monsoon) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Exhaus/Return Air Temp. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1. DB - 75 deg F | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 2. WB - 60 deg F | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Inside design Conditions | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1. DB - 72 deg F | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 2. WB - 60.1deg F | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.1 | 504030000 | AHU Tag: MF-AH-02 (PRE-FUNCTION) (With Mixing box, Thermal break profile & 25mm Panel thickness) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Dehumidified Air Quantity: 9200 CFM | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Cooling Capacity: 41 TR | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Fresh Air Qty: 4100 cfm | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | External Static Pressure: 50 mm | [8 empty] | No. | 1 | 343802 | 0 | 343802 | 48132.28 | 0 |  |  |  |  | 391934.28 | 391934 | 15 | 1 | 51570.3 | 0 | 51570.3 | 7219.842 | 0 | 0 | 0 | 0 | 0 | 58790.142
| 504030000 | Motor HP: 7.5 HP | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Floor Mounted 6 Row Deep Coil | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.1a | 504030000 | Water based heat pipe section for the item 2.1 | [8 empty] | No. | 1 |  | 0 | 0 |  | 0 |  |  |  |  | 0 | 0 | 15 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.1b | 504030000 | Indicate for all (Pre-Function MF- AH-02 Heat Pipe) port charges, port handling charges, other local duties, loading, transportation /insurance upto site, octroi charges and all other taxes and incidentals complete till delivered at site. | [8 empty] | No. | 1 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.1c | 504030000 | Customs duty and countervailing duty for the above imported equipment.- (Pre Fuction AH-02 Heat Pipe) | [8 empty] | Nos. | 1 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.2 | 504030000 | AHU Tag: MF-AH-01 (BALLROOM) (Without Mixing box and Thermal break profile & with 25mm Panel thickness) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Dehumidified Air Quantity: 14800 CFM | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Cooling Capacity: 51.0 TR | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Fresh Air Qty: 3200 cfm | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | External Static Pressure: 50mm/ | [8 empty] | No. | 1 | 509534 | 0 | 509534 | 71334.76 | 0 | 0 | 0 | 0 | 0 | 580868.76 | 580869 | 15 | 1 | 76430.1 | 0 | 76430.1 | 10700.214 | 0 | 0 | 0 | 0 | 0 | 87130.314
| 504030000 | Motor HP: 10 HP | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Floor Mounted 6 Row Deep Coil | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.2a | 504030000 | Water based heat pipe section for the item 2.2 | [8 empty] | No. | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.2b | 504030000 | Indicate for all (Ball Room MF-AH-01 Heat Pipe) port charges, port handling charges, other local duties, loading, transportation /insurance upto site, octroi charges and all other taxes and incidentals complete till delivered at site. | [8 empty] | No. | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.2c | 504030000 | Customs duty and countervailing duty for the above imported equipment.- (Ball Room AH-01 Heat Pipe) | [8 empty] | Nos. | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.3 | 504030000 | AHU Tag: TF-AH-01 (CHINESE RESTAURANT) (With Mixing box, Thermal break profile & 25mm Panel thickness) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Dehumidified Air Quantity: 8550 CFM | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Cooling Capacity: 21.0 TR | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Fresh Air Qty: 1015 cfm | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | External Static Pressure: 50mm | [8 empty] | No. | 1 | 302782 | 0 | 302782 | 42389.48 | 0 | 0 | 0 | 0 | 0 | 345171.48 | 345171 | 15 | 1 | 45417.3 | 0 | 45417.3 | 6358.422 | 0 | 0 | 0 | 0 | 0 | 51775.722
| 504030000 | Motor HP: 7.5 HP | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Floor Mounted 6 Row Deep Coil | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.3a | 504030000 | Water based heat pipe section for the item 2.3 | [8 empty] | No. | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.3b | 504030000 | Indicate for all (Chinese Restaurant TF-AH-01 Heat Pipe) port charges, port handling charges, other local duties, loading, transportation /insurance upto site, octroi charges and all other taxes and incidentals complete till delivered at site. | [8 empty] | No. | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.3c | 504030000 | Customs duty and countervailing duty for the above imported equipment.- (Chinese Restaurant AH-01 Heat Pipe) | [8 empty] | Nos. | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.4 | 504030000 | AHU Tag: TF-AH-03 (LOBBY LOUNGE & BAR) (With Mixing box, Thermal break profile & 25mm Panel thickness) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Dehumidified Air Quantity: 7600 CFM | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Cooling Capacity: 18.0 TR | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Fresh Air Qty: 800 cfm | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | External Static Pressure: 50mmm | [8 empty] | No. | 1 | 288480 | 0 | 288480 | 40387.2 | 0 | 0 | 0 | 0 | 0 | 328867.2 | 328867 | 15 | 1 | 43272 | 0 | 43272 | 6058.08 | 0 | 0 | 0 | 0 | 0 | 49330.08
| 504030000 | Motor HP: 7.5 HP | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Floor Mounted 6 Row Deep Coil | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.4a | 504030000 | Water based heat pipe section for the item 2.4 | [8 empty] | No. | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.4b | 504030000 | Indicate for all (Lobby Lounge & Bar TF-AH-03 Heat Pipe) port charges, port handling charges, other local duties, loading, transportation /insurance upto site, octroi charges and all other taxes and incidentals complete till delivered at site. | [8 empty] | No. | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.4c | 504030000 | Customs duty and countervailing duty for the above imported equipment.- (Lobby Lounge & Bar AH-03 Heat Pipe) | [8 empty] | Nos. | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.5 | 504030000 | AHU Tag: TF-AH-07 (ITALIAN RESTAURANT) (With Mixing box, Thermal break profile & 25mm Panel thickness) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Dehumidified Air Quantity: 9700 CFM | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Cooling Capacity: 28.0 TR | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Fresh Air Qty: 1800 cfm | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | External Static Pressure: 50mm2 | [8 empty] | No. | 1 | 355118 | 0 | 355118 | 49716.52 | 0 | 0 | 0 | 0 | 0 | 404834.52 | 404835 | 15 | 1 | 53267.7 | 0 | 53267.7 | 7457.478 | 0 | 0 | 0 | 0 | 0 | 60725.178
| 504030000 | Motor HP: 7.5 HP | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Floor Mounted 6 Row Deep Coil | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.5b | 504030000 | Indicate for all (Italian Restaurant & Bar TF-AH-07 Heat Pipe) port charges, port handling charges, other local duties, loading, transportation /insurance upto site, octroi charges and all other taxes and incidentals complete till delivered at site. | [8 empty] | No. | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.5c | 504030000 | Customs duty and countervailing duty for the above imported equipment.- (Italian Restaurant AH-07 Heat Pipe) | [8 empty] | Nos. | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 504030000 | Supplying of double skin construction draw thru type AIR HANDLING UNITS with Thermal Break Profile as per specification, each complete with pre-filter section (90% down to 10 microns), 6 Row Deep water coil of copper tube & aluminium fins construction , squirrel cage induction motor, airfoil centrifugal fan belt drive and vibration isolators, coil size shall be selected for a maximum face velocity of 500 feet/minute and static pressure shall be as indicated. The motor selected shall be energy efficient having efficiency (EFF I) at full load ranging between 82.5% to 92% in accordance with motor rating as per specification. Motor shall be suitable for 415±10% volts, 50 cycles, 3 phase AC supply. Fan motor assembly (as whole) shall be statically and dynamically balanced to grade G 6.3 as per ISO-1940/AMCA 204-3.All units shall be complete with opposed blade volume control dampers at oulet, return and fresh air connections. Duct flexible connector (fire proof) shall be provided at outlets and return connection of AHU. For AHUs with VFD, complete equipment shall be designed to limit THDi to less than 5%. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1EMPLOYEES CAFÉB2-AH-0130002150800403Floor Mounted 6 RD Coil, 25mm Panel thickness, No Mixing box & No Thermal break profile | [8 empty] | Nos. | 1 | 75991 | 0 | 75991 | 10638.74 | 0 | 0 | 0 | 0 | 0 | 86629.74 | 86630 | 15 | 1 | 11398.65 | 0 | 11398.65 | 1595.811 | 0 | 0 | 0 | 0 | 0 | 12994.461
| 504030000 | 2F&B OfficesB2-AH-0222003006402Floor Mounted 6 RD Coil, 25mm Panel thickness, No Mixing box & No Thermal break profile | [8 empty] | Nos. | 1 | 67504 | 0 | 67504 | 9450.56 | 0 | 0 | 0 | 0 | 0 | 76954.56 | 76955 | 15 | 1 | 10125.6 | 0 | 10125.6 | 1417.584 | 0 | 0 | 0 | 0 | 0 | 11543.184
| 504030000 | 3HR OfficesB2-AH-0325003506.5403Floor Mounted 6 RD Coil, 25mm Panel thickness, No Mixing box & No Thermal break profile | [8 empty] | Nos. | 1 | 69940 | 0 | 69940 | 9791.6 | 0 | 0 | 0 | 0 | 0 | 79731.6 | 79732 | 15 | 1 | 10491 | 0 | 10491 | 1468.74 | 0 | 0 | 0 | 0 | 0 | 11959.74
| 504030000 | 4CoridorB3-AH-015400240013405Floor Mounted 6 RD Coil, 25mm Panel thickness, No Mixing box & No Thermal break profile | [8 empty] | Nos. | 1 | 112689 | 0 | 112689 | 15776.46 | 0 | 0 | 0 | 0 | 0 | 128465.46 | 128465 | 15 | 1 | 16903.35 | 0 | 16903.35 | 2366.469 | 0 | 0 | 0 | 0 | 0 | 19269.819
| 504030000 | BASEMENT-1 | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1Commissary KitchenB1-AH-016400113017403Floor Mounted 6 RD Coil, 25mm Panel thickness, Thermal break profile & Mixing Box | [8 empty] | Nos. | 1 | 144594 | 0 | 144594 | 20243.16 | 0 | 0 | 0 | 0 | 0 | 164837.16 | 164837 | 15 | 1 | 21689.1 | 0 | 21689.1 | 3036.474 | 0 | 0 | 0 | 0 | 0 | 24725.574
| 504030000 | GROUND FLOOR | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1LoungeGF-AH-0129004007403Floor Mounted 6 RD Coil, 25mm Panel thickness, Thermal break profile & Mixing Box | [8 empty] | Nos. | 1 | 88249 | 0 | 88249 | 12354.86 | 0 | 0 | 0 | 0 | 0 | 100603.86 | 100604 | 15 | 1 | 13237.35 | 0 | 13237.35 | 1853.229 | 0 | 0 | 0 | 0 | 0 | 15090.579
| 504030000 | 2Banquet KitchenGF-TFA-013600180016403Floor Mounted 6 RD Coil, 25mm Panel thickness, Thermal break profile & Mixing Box | [8 empty] | Nos. | 1 | 99173 | 0 | 99173 | 13884.22 | 0 | 0 | 0 | 0 | 0 | 113057.22 | 113057 | 15 | 1 | 14875.95 | 0 | 14875.95 | 2082.633 | 0 | 0 | 0 | 0 | 0 | 16958.583
| 504030000 | MEZZANINE FLOOR | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1Lift LobbyTF-AH-05470095012405Floor Mounted 6 RD Coil, 25mm Panel thickness, Thermal break profile & Mixing Box | [8 empty] | Nos. | 1 | 119368 | 0 | 119368 | 16711.52 | 0 | 0 | 0 | 0 | 0 | 136079.52 | 136080 | 15 | 1 | 17905.2 | 0 | 17905.2 | 2506.728 | 0 | 0 | 0 | 0 | 0 | 20411.928
| 504030000 | 2Meeting Room 3MF-AH-03350075012505Floor Mounted 6 RD Coil, 25mm Panel thickness, Thermal break profile & Mixing Box | [8 empty] | Nos. | 1 | 98387 | 0 | 98387 | 13774.18 | 0 | 0 | 0 | 0 | 0 | 112161.18 | 112161 | 15 | 1 | 14758.05 | 0 | 14758.05 | 2066.127 | 0 | 0 | 0 | 0 | 0 | 16824.177
| 504030000 | FIRST FLOOR | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1ReceptionTF-AH-06430060010405Floor Mounted 6 RD Coil, 25mm Panel thickness, Thermal break profile & Mixing Box | [8 empty] | Nos. | 1 | 109310 | 0 | 109310 | 15303.4 | 0 | 0 | 0 | 0 | 0 | 124613.4 | 124613 | 15 | 1 | 16396.5 | 0 | 16396.5 | 2295.51 | 0 | 0 | 0 | 0 | 0 | 18692.01
| 504030000 | 2Display KitchenTF-TFA-01400090011405Floor Mounted 6 RD Coil, 25mm Panel thickness, Thermal break profile & Mixing Box | [8 empty] | Nos. | 1 | 102473 | 0 | 102473 | 14346.22 | 0 | 0 | 0 | 0 | 0 | 116819.22 | 116819 | 15 | 1 | 15370.95 | 0 | 15370.95 | 2151.933 | 0 | 0 | 0 | 0 | 0 | 17522.883
| 504030000 | 3Restaurant KitchenTF-TFA-02400090011405Floor Mounted 6 RD Coil, 25mm Panel thickness, Thermal break profile & Mixing Box | [8 empty] | Nos. | 1 | 102473 | 0 | 102473 | 14346.22 | 0 | 0 | 0 | 0 | 0 | 116819.22 | 116819 | 15 | 1 | 15370.95 | 0 | 15370.95 | 2151.933 | 0 | 0 | 0 | 0 | 0 | 17522.883
| 504030000 | SECOND FLOOR | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1Office CorridorTF-AH-04250012009303Floor Mounted 6 RD Coil, 25mm Panel thickness, Thermal break profile & Mixing Box | [8 empty] | Nos. | 1 | 81884 | 0 | 81884 | 11463.76 | 0 | 0 | 0 | 0 | 0 | 93347.76 | 93348 | 15 | 1 | 12282.6 | 0 | 12282.6 | 1719.564 | 0 | 0 | 0 | 0 | 0 | 14002.164
| 504030000 | 2SpaTF-AH-02755040013403Floor Mounted 6 RD Coil, 25mm Panel thickness, Thermal break profile & Mixing Box | [8 empty] | Nos. | 1 | 173827 | 0 | 173827 | 24335.78 | 0 | 0 | 0 | 0 | 0 | 198162.78 | 198163 | 15 | 1 | 26074.05 | 0 | 26074.05 | 3650.367 | 0 | 0 | 0 | 0 | 0 | 29724.417
| 504030000 | 3Gym / AerobicTF-AH-0837005009403Floor Mounted 6 RD Coil, 25mm Panel thickness, Thermal break profile & Mixing Box | [8 empty] | Nos. | 1 | 100037 | 0 | 100037 | 14005.18 | 0 | 0 | 0 | 0 | 0 | 114042.18 | 114042 | 15 | 1 | 15005.55 | 0 | 15005.55 | 2100.777 | 0 | 0 | 0 | 0 | 0 | 17106.327
| 504030000 | PENTHOUSE FLOOR | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1Regency ClubPTF-AH-01505095015405Floor Mounted 6 RD Coil, 50mm Panel thickness, Thermal break profile & Mixing Box | [8 empty] | Nos. | 1 | 123612 | 0 | 123612 | 17305.68 | 0 | 0 | 0 | 0 | 0 | 140917.68 | 140918 | 15 | 1 | 18541.8 | 0 | 18541.8 | 2595.852 | 0 | 0 | 0 | 0 | 0 | 21137.652
4 | 504030000 | Supplying of HEAT RECOVERY UNIT (HRU) 50mm thick double skin construction with Thermal Break Profile as per specification, each complete with pre-filter section (90% down to 10 microns), min 8 Row Deep water coil of copper tube & aluminium fins construction. The coil shall be sized for the actual capacity considering with out heat recovery unit. The unit shall comprise of filter section, heat recovery unit, fresh air inlet / exhaust air outlet, fan section with DIDW fan with motor and drive package. The unit shall be installed above main AHU and interconnected in a manner so as to receive part return air thru public area which shall be passed through HRW and transfer sensible and latent cooling to incoming fresh air. The precooled fresh air shall be let into the mixing box of the main AHU and return air is exhausted outdoors. The exhaust section of the unit shall be provided with motor actuated GSS damper duly interlocked with the fan. Minimum sensible and latent heat transfer efficiency of heat recovery unit shall be 80%. For units with VFD, complete equipment shall be designed to limit THDi to less than 5% | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Design conditions shall be as follows | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Fresh Air | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1. DB - 109 deg F | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 2. WB - 79 deg F | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Return Air Temp. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1. DB - 77.0 deg F | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 2. WB - 65.7 deg F | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Air moving capacity shall be as follows : | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | SR.SPACETAG. NO.FRESH AIRMOTOR EXHAUST MOTOR ACTUAL AIR | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | NO.CFMHP CFM HP TR | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1FOR GUEST FLOORPTF-TFA-HRW-011700012.5 5475 5 106 | [8 empty] | Nos. | 1 | 604149 | 0 | 604149 | 84580.86 | 0 | 0 | 0 | 0 | 0 | 688729.86 | 688730 | 15 | 1 | 90622.35 | 0 | 90622.35 | 12687.129 | 0 | 0 | 0 | 0 | 0 | 103309.479
| 504030000 | 2FOR GUEST FLOORPTF-TFA-HRW-021700012.5 5475 5 106 | [8 empty] | Nos. | 1 | 604149 | 0 | 604149 | 84580.86 | 0 | 0 | 0 | 0 | 0 | 688729.86 | 688730 | 15 | 1 | 90622.35 | 0 | 90622.35 | 12687.129 | 0 | 0 | 0 | 0 | 0 | 103309.479
5 | 504030000 | Supply of micro-processor controlled precision air-conditioning unit with scroll compressor(s) on HFC-134a / HFC-410a, air cooled condenser with installation stand, insulated refrigerant piping with supports, cooling coil, electrical heating coil, steam humidifier, necessary measuring and control devices, evaporator fan with motor, pre and micro-vee filters and inbuilt starter. Power will be provided by other agency near the indoor unit inbuilt starter. Power and control cabling from indoor to outdoor unit along with supports / cable trays shall be included. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.1 | 504030000 | 5 TR | [8 empty] | Nos. | 1 | 391897 | 0 | 391897 | 54865.58 | 0 | 0 | 0 | 0 | 0 | 446762.58 | 446763 | 15 | 1 | 58784.55 | 0 | 58784.55 | 8229.837 | 0 | 0 | 0 | 0 | 0 | 67014.387
| 504030000 | [9 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.2 | 504030000 | 10 TR | [8 empty] | Nos. | 1 | 516321 | 0 | 516321 | 72284.94 | 0 | 0 | 0 | 0 | 0 | 588605.94 | 588606 | 15 | 1 | 77448.15 | 0 | 77448.15 | 10842.741 | 0 | 0 | 0 | 0 | 0 | 88290.891
6 | 504030000 | Supply of wall mounted air cooled split air conditioning units as described in specifications. The unit shall be complete with decorative type fan coil unit and external condensing unit, complete in all respects, inclusive of copper refrigerant piping of 10mtr length, GI condensate drain piping, valves and insulation quoted price shall include cost of cooling thermostat, power wiring, control wiring and earthing. The unit capacities shall be as follows: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Note : Fins and copper tubes of Air Cooled Condenser alongwith copper tubing / piping with all joints and U-Bends exposed to coastal areas corrosive atmosphere / aggressive ambient, shall be painted with special corrosion prevention coating either in factory or at site. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6.1 | 504030000 | 1.5TR split air conditioning system | [8 empty] | Nos. | 1 | 38100 | 0 | 38100 | 5334 | 0 | 0 | 0 | 0 | 0 | 43434 | 43434 | 15 | 1 | 5715 | 0 | 5715 | 800.1 | 0 | 0 | 0 | 0 | 0 | 6515.1
6.2 | 504030000 | 2TR split air conditioning system | [8 empty] | Nos. | 1 | 42100 | 0 | 42100 | 5894 | 0 | 0 | 0 | 0 | 0 | 47994 | 47994 | 15 | 1 | 6315 | 0 | 6315 | 884.1 | 0 | 0 | 0 | 0 | 0 | 7199.1
6.3 | 504030000 | 2.5TR split air conditioning system | [8 empty] | Nos. | 1 | 68100 | 0 | 68100 | 9534 | 0 | 0 | 0 | 0 | 0 | 77634 | 77634 | 15 | 1 | 10215 | 0 | 10215 | 1430.1 | 0 | 0 | 0 | 0 | 0 | 11645.1
7 | 504030000 | Supplying of AIR HANDLING UNITS ( FAN SECTIONS ONLY)with 25mm thick double skin construction as per specificatopns, each complete with squirrel cage induction motor (mounted internally), airfoil centrifugal fan belt drive and vibrations isolators.Motors shall be suitable for 415 +- 10% volts, 50 cycles , 3 phase AC supply an static pressure shall be as indicated . Fan-motor assembly (as whole) shall be statically & dynamically balanced to grade G6.3 as per ISO-1940/AMCA 204-3. All AHUS (Fan sections) shall be suitable for outdoor duty and complete with duct flexible connections and volume control damper . In additional all supply fans (SF) shall be provided with prefilter | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Note EF- Exhaust Fan , SF - Supply Fan | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | SR. NO.SPACEFanCFMSPMotorType | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | TagmmHP | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | BASEMENT-3 | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1STPB3-EF-018400655Outdoor type mounted at terrace level | [8 empty] | Nos. | 1 | 89743 | 0 | 89743 | 12564.02 | 0 | 0 | 0 | 0 | 0 | 102307.02 | 102307 | 15 | 1 | 13461.45 | 0 | 13461.45 | 1884.603 | 0 | 0 | 0 | 0 | 0 | 15346.053
| 504030000 | 2STPB3-FF-017200405Loft Mounted | [8 empty] | Nos. | 1 | 79291 | 0 | 79291 | 11100.74 | 0 | 0 | 0 | 0 | 0 | 90391.74 | 90392 | 15 | 1 | 11893.65 | 0 | 11893.65 | 1665.111 | 0 | 0 | 0 | 0 | 0 | 13558.761
| 504030000 | 3HVAC PlantroomB3-EF-02137004010Loft Mounted | [8 empty] | Nos. | 1 | 151430 | 0 | 151430 | 21200.2 | 0 | 0 | 0 | 0 | 0 | 172630.2 | 172630 | 15 | 1 | 22714.5 | 0 | 22714.5 | 3180.03 | 0 | 0 | 0 | 0 | 0 | 25894.53
| 504030000 | 4HVAC PlantroomB3-FF-0211000407.5Loft Mounted | [8 empty] | Nos. | 1 | 112610 | 0 | 112610 | 15765.4 | 0 | 0 | 0 | 0 | 0 | 128375.4 | 128375 | 15 | 1 | 16891.5 | 0 | 16891.5 | 2364.81 | 0 | 0 | 0 | 0 | 0 | 19256.31
| 504030000 | 5Plumbing PlantroomB3-EF-0310000407.5Loft Mounted | [8 empty] | Nos. | 1 | 97915 | 0 | 97915 | 13708.1 | 0 | 0 | 0 | 0 | 0 | 111623.1 | 111623 | 15 | 1 | 14687.25 | 0 | 14687.25 | 2056.215 | 0 | 0 | 0 | 0 | 0 | 16743.465
| 504030000 | 6Plumbing PlantroomB3-FF-038700405Loft Mounted | [8 empty] | Nos. | 1 | 86678 | 0 | 86678 | 12134.92 | 0 | 0 | 0 | 0 | 0 | 98812.92 | 98813 | 15 | 1 | 13001.7 | 0 | 13001.7 | 1820.238 | 0 | 0 | 0 | 0 | 0 | 14821.938
| 504030000 | 7Hot Water Plant roomB3-FF-049800405Loft Mounted | [8 empty] | RO | 0 | 100980 | 0 | 100980 |  | 0 | 0 | 0 | 0 | 0 | 100980 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | BASEMENT-2 | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1LaundryB2-FF-047000405Loft Mounted | [8 empty] | RO | 0 | 79291 | 0 | 79291 | 11100.74 | 0 | 0 | 0 | 0 | 0 | 90391.74 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 2Employees Cafe KitchenB2-FF-035000403Loft Mounted | [8 empty] | RO | 0 | 58388 | 0 | 58388 | 8174.32 | 0 | 0 | 0 | 0 | 0 | 66562.32 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | BASEMENT-1 | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1Commissary KitchenB1-FF-019000605Loft Mounted | [8 empty] | RO | 0 | 107109 | 0 | 107109 | 14995.26 | 0 | 0 | 0 | 0 | 0 | 122104.26 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 2Boiler RoomB1-FF-023700403Ceiling Suspended | [8 empty] | RO | 0 | 42200 | 0 | 42200 | 5908 | 0 | 0 | 0 | 0 | 0 | 48108 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | GROUND FLOOR | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1Banquet KitchenGF-FF-01160005010Loft Mounted | [8 empty] | RO | 0 | 160075 | 0 | 160075 | 22410.5 | 0 | 0 | 0 | 0 | 0 | 182485.5 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | FIRST FLOOR | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1Italian KitchenTF-TFA-012400405Floor Mounted | [8 empty] | RO | 0 | 43929 | 0 | 43929 | 6150.06 | 0 | 0 | 0 | 0 | 0 | 50079.06 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 2All Day Dining Kitchen / TF-FF-0112000507.5Floor Mounted | [8 empty] | RO | 0 | 123062 | 0 | 123062 | 17228.68 | 0 | 0 | 0 | 0 | 0 | 140290.68 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Chineese Kitchen | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Transfer Floor | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1Transfer FloorTF-EF-09200003012.5Floor Mounted | [8 empty] | Nos. | 1 | 205417 | 0 | 205417 | 28758.38 | 0 | 0 | 0 | 0 | 0 | 234175.38 | 234175 | 15 | 1 | 30812.55 | 0 | 30812.55 | 4313.757 | 0 | 0 | 0 | 0 | 0 | 35126.307
| 504030000 | 2Transfer FloorTF-FF-0210000307.5Floor Mounted | [8 empty] | Nos. | 1 | 100980 | 0 | 100980 | 14137.2 | 0 | 0 | 0 | 0 | 0 | 115117.2 | 115117 | 15 | 1 | 15147 | 0 | 15147 | 2120.58 | 0 | 0 | 0 | 0 | 0 | 17267.58
| 504030000 | 3Transfer FloorTF-FF-0310000307.5Floor Mounted | [8 empty] | Nos. | 1 | 100980 | 0 | 100980 | 14137.2 | 0 | 0 | 0 | 0 | 0 | 115117.2 | 115117 | 15 | 1 | 15147 | 0 | 15147 | 2120.58 | 0 | 0 | 0 | 0 | 0 | 17267.58
8 | 504030000 | Supplying of Smoke spill fans as per specifications.Fan shall be direct driven.Fan and casing shall be suitable for smoke exhaust application.Motor and belt drive shall be mounted outside ,so that it is not exposed to smoke stream & thermally rated for 2500C for 2 hours as per [BS EN 12101-3:2002] Class-B. Motors shall be suitable for 415+10% volts, 50 cycles , 3 phase AC supply an static pressure shall be as indicated . Fans shall be activated from fire signal from fire alarm system .Fan shall be with flexible fire proof flexibel connection at inlet and outlet | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | [9 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | SR. NO.SPACEFanCFMSPMotorType | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | TagmmHP | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | BASEMENT-3 | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1Car Parking Exhaust FanB3-EF-05340004025Tube axial flow fan | [8 empty] | Nos. | 2 | 127474 | 0 | 127474 | 17846.36 | 0 | 0 | 0 | 0 | 0 | 145320.36 | 290641 | 15 | 2 | 38242.2 | 0 | 38242.2 | 5353.908 | 0 | 0 | 0 | 0 | 0 | 43596.108
| 504030000 | 2Hot Water PlantroomB3-EF-0411400407.5Loft Mounted centrifugal cabinet fan | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | BASEMENT-2 | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1Car Parking Exhaust FanB2-EF-01340004025Tube axial flow fan | [8 empty] | Nos. | 2 | 127474 | 0 | 127474 | 17846.36 | 0 | 0 | 0 | 0 | 0 | 145320.36 | 290641 | 15 | 2 | 38242.2 | 0 | 38242.2 | 5353.908 | 0 | 0 | 0 | 0 | 0 | 43596.108
| 504030000 | 2LaundryPTF-EF-018000605Loft Mounted centrifugal cabinet fan | [8 empty] | Nos. | 1 | 117600 | 0 | 117600 | 16464 | 0 | 0 | 0 | 0 | 0 | 134064 | 134064 | 15 | 1 | 17640 | 0 | 17640 | 2469.6 | 0 | 0 | 0 | 0 | 0 | 20109.6
| 504030000 | 3Employees Cafe KitchenB1-EF-056650907.5SISW Outdoor type at terrace level | [8 empty] | Nos. | 1 | 85559 | 0 | 85559 | 11978.26 | 0 | 0 | 0 | 0 | 0 | 97537.26 | 97537 | 15 | 1 | 12833.85 | 0 | 12833.85 | 1796.739 | 0 | 0 | 0 | 0 | 0 | 14630.589
| 504030000 | BASEMENT-1 | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1Car Parking Exhaust FanB1-EF-03200004015Tube axial flow fan | [8 empty] | Nos. | 2 | 77544 | 0 | 77544 | 10856.16 | 0 | 0 | 0 | 0 | 0 | 88400.16 | 176800 | 15 | 2 | 23263.2 | 0 | 23263.2 | 3256.848 | 0 | 0 | 0 | 0 | 0 | 26520.048
| 504030000 | 2Commissary KitchenB1-EF-0110000907.5SISW Outdoor type at terrace level | [8 empty] | Nos. | 1 | 110178 | 0 | 110178 | 15424.92 | 0 | 0 | 0 | 0 | 0 | 125602.92 | 125603 | 15 | 1 | 16526.7 | 0 | 16526.7 | 2313.738 | 0 | 0 | 0 | 0 | 0 | 18840.438
| 504030000 | 3Boiler RoomB1-EF-024400603Ceiling Suspended Centrifugal cabinet fan | [8 empty] | Nos. | 1 | 79429 | 0 | 79429 | 11120.06 | 0 | 0 | 0 | 0 | 0 | 90549.06 | 90549 | 15 | 1 | 11914.35 | 0 | 11914.35 | 1668.009 | 0 | 0 | 0 | 0 | 0 | 13582.359
| 504030000 | 1Chineese Display KitchenTF-FF-0310250905SISW Floor Mounted | [8 empty] | Nos. | 1 | 135566 | 0 | 135566 | 18979.24 | 0 | 0 | 0 | 0 | 0 | 154545.24 | 154545 | 15 | 1 | 20334.9 | 0 | 20334.9 | 2846.886 | 0 | 0 | 0 | 0 | 0 | 23181.786
| 504030000 | 2Italian Restaurant KitchenTF-FF-043000905SISW Floor Mounted | [8 empty] | Nos. | 1 | 51137 | 0 | 51137 | 7159.18 | 0 | 0 | 0 | 0 | 0 | 58296.18 | 58296 | 15 | 1 | 7670.55 | 0 | 7670.55 | 1073.877 | 0 | 0 | 0 | 0 | 0 | 8744.427
| 504030000 | 3All Day Dining KitchenTF-FF-0513000907.5SISW Floor Mounted | [8 empty] | Nos. | 1 | 164093 | 0 | 164093 | 22973.02 | 0 | 0 | 0 | 0 | 0 | 187066.02 | 187066 | 15 | 1 | 24613.95 | 0 | 24613.95 | 3445.953 | 0 | 0 | 0 | 0 | 0 | 28059.903
| 504030000 | 4Banquet KitchenTF-EF-02200009015SISW Outdoor type at terrace level | [8 empty] | Nos. | 1 | 197504 | 0 | 197504 | 27650.56 | 0 | 0 | 0 | 0 | 0 | 225154.56 | 225155 | 15 | 1 | 29625.6 | 0 | 29625.6 | 4147.584 | 0 | 0 | 0 | 0 | 0 | 33773.184
| 504030000 | PENTHOUSE TERRACE FLOORn | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1Smoke EvacuationPTF-EF-026800405SISW Floor Mounted | [8 empty] | Nos. | 1 | 82579 | 0 | 82579 | 11561.06 | 0 | 0 | 0 | 0 | 0 | 94140.06 | 94140 | 15 | 1 | 12386.85 | 0 | 12386.85 | 1734.159 | 0 | 0 | 0 | 0 | 0 | 14121.009
9 | 504030000 | Supplying of INLINE FANS suitable for installing in any position in vertical or horizontal ducts. The casing shall be double skin, internally acoustically lined and constructed of galvanised steel. The fan shall be DIDW with forward curve impeller fitted with maintenance free external rotor motor. The motor shall be suitable for 220±10% volt single phase 50 cycles AC supply. All units shall be complete with duct flexible connector and volume control damper. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | The fan shall have low sound level exceeding not more than 40 DBA at three metre distance. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | SR. NO.SPACEFanCFMSPMotorType | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | TagmmHP | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | BASEMENT-2 | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1Dishwash AreaB2-EF-03600301.5Ceiling Suspended | [8 empty] | Nos. | 1 | 48903 | 0 | 48903 | 6846.42 | 0 | 0 | 0 | 0 | 0 | 55749.42 | 55749 | 15 | 1 | 7335.45 | 0 | 7335.45 | 1026.963 | 0 | 0 | 0 | 0 | 0 | 8362.413
| 504030000 | 2Toilet exhaustB1-EF-06850301.5Ceiling Suspended | [8 empty] | Nos. | 1 | 49486 | 0 | 49486 | 6928.04 | 0 | 0 | 0 | 0 | 0 | 56414.04 | 56414 | 15 | 1 | 7422.9 | 0 | 7422.9 | 1039.206 | 0 | 0 | 0 | 0 | 0 | 8462.106
| 504030000 | GROUND FLOOR | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1Toilet exhaustGF-EF-02800301.5Ceiling Suspended | [8 empty] | Nos. | 1 | 48903 | 0 | 48903 | 6846.42 | 0 | 0 | 0 | 0 | 0 | 55749.42 | 55749 | 15 | 1 | 7335.45 | 0 | 7335.45 | 1026.963 | 0 | 0 | 0 | 0 | 0 | 8362.413
| 504030000 | MEZZANINE FLOOR | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1Fresh Air for UnitsMF-FF-011400301.5Ceiling Suspended | [8 empty] | Nos. | 1 | 54798 | 0 | 54798 | 7671.72 | 0 | 0 | 0 | 0 | 0 | 62469.72 | 62470 | 15 | 1 | 8219.7 | 0 | 8219.7 | 1150.758 | 0 | 0 | 0 | 0 | 0 | 9370.458
| 504030000 | 2Toilet exhaustTF-EF-011000301.5Ceiling Suspended | [8 empty] | Nos. | 1 | 48903 | 0 | 48903 | 6846.42 | 0 | 0 | 0 | 0 | 0 | 55749.42 | 55749 | 15 | 1 | 7335.45 | 0 | 7335.45 | 1026.963 | 0 | 0 | 0 | 0 | 0 | 8362.413
| 504030000 | FIRST FLOOR | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1Toilet exhaustTF-EF-06900301.5Ceiling Suspended | [8 empty] | Nos. | 1 | 48903 | 0 | 48903 | 6846.42 | 0 | 0 | 0 | 0 | 0 | 55749.42 | 55749 | 15 | 1 | 7335.45 | 0 | 7335.45 | 1026.963 | 0 | 0 | 0 | 0 | 0 | 8362.413
| 504030000 | SECOND FLOOR | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1SPA (Male) Toilet ExhaustTF-EF-07250301.5Ceiling Suspended | [8 empty] | Nos. | 1 | 25255 | 0 | 25255 | 3535.7 | 0 | 0 | 0 | 0 | 0 | 28790.7 | 28791 | 15 | 1 | 3788.25 | 0 | 3788.25 | 530.355 | 0 | 0 | 0 | 0 | 0 | 4318.605
| 504030000 | 2SPA (Female) Toilet ExhaustTF-EF-08150301.5Ceiling Suspended | [8 empty] | Nos. | 1 | 25255 | 0 | 25255 | 3535.7 | 0 | 0 | 0 | 0 | 0 | 28790.7 | 28791 | 15 | 1 | 3788.25 | 0 | 3788.25 | 530.355 | 0 | 0 | 0 | 0 | 0 | 4318.605
10 | 504030000 | Supplying of direct driven PROPELLER FANS for exhaust air as shown in drawings. Each fan shall be complete with permanent split capacitor or shaded pole motor, mounting plate, accessories like wire guard, bird screen and fixed louvers for weather protection as required. Fan selection arrangement and Electrical characteristics shall be as follows : | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10.1 | 504030000 | 350 mm dia 900 RPM fan suitable for 220±6% volts 50 cycles, 1 phase AC supply. | [8 empty] | Nos. | 4 | 4357 | 0 | 4357 | 609.98 | 0 | 0 | 0 | 0 | 0 | 4966.98 | 19868 | 15 | 4 | 2614.2 | 0 | 2614.2 | 365.988 | 0 | 0 | 0 | 0 | 0 | 2980.188
10.2 | 504030000 | 300 mm dia 900 RPM fan suitable for 220±6% volts 50 cycles, 1 phase AC supply. | [8 empty] | Nos. | 1 | 4069 | 0 | 4069 | 569.66 | 0 | 0 | 0 | 0 | 0 | 4638.66 | 4639 | 15 | 1 | 610.35 | 0 | 610.35 | 85.449 | 0 | 0 | 0 | 0 | 0 | 695.799
11 | 504030000 | Supply of FANS for return air & exhaust air suitable for installing in any position in Horizontal or vertical. The motor shall be suitable for 415 V + 10% volts three phase 50cycle, AC supply.The fan shall be equipped with mounting bracket & outlet core required at discharge. The fan shall be low RPM (less than 1000 RPM) and capacities based on minimum 1.5 inch (4cm WC) static pressure or to suit the system, shall be as follows: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | The fan shall have low sound power level not exceeding 65dBA at three meter distance at both ends. To achieve these DB levels, sound attenuators of suitable length, at inlet & outlet of the fans must be included in the cost. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | SR. NO.SPACEFanCFMSPMotorType | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | TagmmHP | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | BASEMENT-3 | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1Car Parking Fresh Air FanB3-FF-05340003020Tube axial flow fan | [8 empty] | Nos. | 2 | 277152 | 0 | 277152 | 38801.28 | 0 | 0 | 0 | 0 | 0 | 315953.28 | 631907 | 15 | 2 | 83145.6 | 0 | 83145.6 | 11640.384 | 0 | 0 | 0 | 0 | 0 | 94785.984
| 504030000 | BASEMENT-2 | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1Car Parking Fresh Air FanB2-FF-01340003020Tube axial flow fan | [8 empty] | Nos. | 2 | 277152 | 0 | 277152 | 38801.28 | 0 | 0 | 0 | 0 | 0 | 315953.28 | 631907 | 15 | 2 | 83145.6 | 0 | 83145.6 | 11640.384 | 0 | 0 | 0 | 0 | 0 | 94785.984
| 504030000 | BASEMENT-1 | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1Staircase-4 PressurizationB1-FF-033000303SISW Floor Mounted | [8 empty] | Nos. | 1 | 97419 | 0 | 97419 | 13638.66 | 0 | 0 | 0 | 0 | 0 | 111057.66 | 111058 | 15 | 1 | 14612.85 | 0 | 14612.85 | 2045.799 | 0 | 0 | 0 | 0 | 0 | 16658.649
| 504030000 | PENTHOUSE FLOOR | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1Fresh Air for Smoke EvacuationPF-FF-013400303Floor Mounted | [8 empty] | Nos. | 1 | 98054 | 0 | 98054 | 13727.56 | 0 | 0 | 0 | 0 | 0 | 111781.56 | 111782 | 15 | 1 | 14708.1 | 0 | 14708.1 | 2059.134 | 0 | 0 | 0 | 0 | 0 | 16767.234
| 504030000 | PENTHOUSE TERRACE FLOOR | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1Fresh Air for Smoke EvacuationPTF-FF-013400303Floor Mounted | [8 empty] | Nos. | 1 | 98054 | 0 | 98054 | 13727.56 | 0 | 0 | 0 | 0 | 0 | 111781.56 | 111782 | 15 | 1 | 14708.1 | 0 | 14708.1 | 2059.134 | 0 | 0 | 0 | 0 | 0 | 16767.234
| 504030000 | 2Lift PressurizationPTF-FF-02140003010Floor Mounted | [8 empty] | Nos. | 1 | 133745 | 0 | 133745 | 18724.3 | 0 | 0 | 0 | 0 | 0 | 152469.3 | 152469 | 15 | 1 | 20061.75 | 0 | 20061.75 | 2808.645 | 0 | 0 | 0 | 0 | 0 | 22870.395
| 504030000 | 3Lift PressurizationPTF-FF-03140003010Floor Mounted | [8 empty] | Nos. | 1 | 133745 | 0 | 133745 | 18724.3 | 0 | 0 | 0 | 0 | 0 | 152469.3 | 152469 | 15 | 1 | 20061.75 | 0 | 20061.75 | 2808.645 | 0 | 0 | 0 | 0 | 0 | 22870.395
| 504030000 | 4Lift PressurizationPTF-FF-04140003010Floor Mounted | [8 empty] | Nos. | 1 | 133745 | 0 | 133745 | 18724.3 | 0 | 0 | 0 | 0 | 0 | 152469.3 | 152469 | 15 | 1 | 20061.75 | 0 | 20061.75 | 2808.645 | 0 | 0 | 0 | 0 | 0 | 22870.395
| 504030000 | 5Lift PressurizationPTF-FF-05140003010Floor Mounted | [8 empty] | Nos. | 1 | 133745 | 0 | 133745 | 18724.3 | 0 | 0 | 0 | 0 | 0 | 152469.3 | 152469 | 15 | 1 | 20061.75 | 0 | 20061.75 | 2808.645 | 0 | 0 | 0 | 0 | 0 | 22870.395
| 504030000 | 6Staircase-2 PressurizationPTF-FF-06170003010Floor Mounted | [8 empty] | Nos. | 1 | 158221 | 0 | 158221 | 22150.94 | 0 | 0 | 0 | 0 | 0 | 180371.94 | 180372 | 15 | 1 | 23733.15 | 0 | 23733.15 | 3322.641 | 0 | 0 | 0 | 0 | 0 | 27055.791
| 504030000 | ROOF FLOOR | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1Staircase-1 PressurizationRF-FF-01170003010Floor Mounted | [8 empty] | Nos. | 1 | 158221 | 0 | 158221 | 22150.94 | 0 | 0 | 0 | 0 | 0 | 180371.94 | 180372 | 15 | 1 | 23733.15 | 0 | 23733.15 | 3322.641 | 0 | 0 | 0 | 0 | 0 | 27055.791
| 504030000 | 2Staircase-3 PressurizationRF-FF-02170003010Floor Mounted | [8 empty] | Nos. | 1 | 158221 | 0 | 158221 | 22150.94 | 0 | 0 | 0 | 0 | 0 | 180371.94 | 180372 | 15 | 1 | 23733.15 | 0 | 23733.15 | 3322.641 | 0 | 0 | 0 | 0 | 0 | 27055.791
12 | 504030000 | Supply of Scrubber each comprising of electrostatic precipitation technology, dry type air cleaner to remove oil, smoke and fumes from exhaust air, as per the Specifications. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Electrostatic section shall be made of 16 gauge galvanised sheet, high bake epoxy powder coated, washable type aluminium mesh filters, stainless steel spiked ionizers to create high voltage DC field, aluminum collector plates which should be alternatively charged positive and negative with large collecting area with 14" deep cell, to work as magnet for charged smoke and oil particles. Average efficiency of 90-95% in single pass as per ASHRAE test method. Electrostatic Precipitator should be able to charge particles from 0.01 micron to 10 microns through solid state power supply. Collector cell should be of permanent type and incorporate slide out facility for easy removal for cleaning. Power supplies shall be 100% solid state UL Listed, Module of capacity above 3000 CFM shall be equipped with Pulse width modulating (PWM)The system should be fitted with interlock switch for safety . The system should allow connection to a fan section to achieve 500 FPM velocity across the air cleaner. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Operating Voltage : 220V, 50 Hz | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Ionizing Voltage : 12.5 to 13 KVDC | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Collector Cell Voltage : 6 to 6.5 KVDC | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Power Consumption : Not more than 50W per cell. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Air Moving Capacities shall be as follows: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | SpaceCFMQTY | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Italina Restaurant Kitchen30001 | [8 empty] | Nos. | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | All Day Dining Kitchen130001 | [8 empty] | Nos. | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Chineese Restaurant kitchen102501 | [8 empty] | Nos. | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | The unit shall be integrated & connected with exhaust fan sections for kitchen including all necessary accessories to complete the installation. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12.1 | 504030000 | Indicate for all Dry Scrubber port charges, port handling charges, other local duties, loading, transportation /insurance upto site, octroi charges and all other taxes and incidentals complete till delivered at site. | [8 empty] | Nos. | 3 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12.2 | 504030000 | Customs duty and countervailing duty for the above imported equipment.- Dry Scrubber | [8 empty] | Nos. | 3 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
B. | 504030000 | EQUIPMENT | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 504030000 | MOTOR CONTROL CENTRES FOR AIR CONDITIONING (PLANT ROOM) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Design, manufacture, supply of the following cubicle type 2 mm thick sheet steel enclosed separate compartment for each feeder, front operated, rear connections indoor type LT motor control panel, dust and vermin proof, drawout/hinged and lockable doors, complete with internal wiring, colour coding with ferrules, cable glands, bonding to earth and painting. Quoted price for each panel & motor control centre shall include all cabling & earthing over cable trays into various equipment, all associated control wiring and interlocking circuitary. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Each MCC shall include cost of wiring, control wiring & inter locking between chillers, primary CHW pumps, condenser water pumps, motorized valves at chillers and condensers, flow meter & flow switch installed in de-coupler by-pass line, in order to execute the required sequence of operation. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | All outgoing shall be provided with Stop/Manual/ Auto/selector switch to facilitate operation through BAS. All starters shall be provided with potential free Contact for Connections to Building Automation System. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | A separate set of CTs to be provided for BAS and wiring from CT’s and voltage transducers to be brought on to separate set of terminals. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13.1 | 504030000 | Motor Control Centre 415V Bus Section-1 consisting of | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
a. | 504030000 | Incomingg | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | One No. 800 amps 4P Microprocessor based incoming MCCB with LSI protection complete with the following accessories :: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 504030000 | 0 - 500 volts 96 x 96 sq mm digital voltmeter with selector switch - 1 Set | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 504030000 | 0 - 800 amps 96 x 96 sq mm digital ammeter with 800/5 amps CT’s and selector switch - 1 Set | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 504030000 | Over voltage tripping mechanism for persistent voltage exceeding 110% of the rated voltage for more than 5 minutes - 1 Set; | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iv. | 504030000 | Phase indicating lamps, with toggle switches - 3 Sets; | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
b. | 504030000 | TPN bus bars shall be of Copper and shall be sleeved. Phase bus bars shall be rated at 800 amps (25 KA) and neutral bus bar shall be of 50% capacityl | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Maximum density of copper bus bars for current carrying capacity shall be 1.4 amp per square mm.e | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Outgoingq | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
c. | 504030000 | 2 Nos. 315 amps TPN MCCB, and outgoing feeders to. 2 nos 200 TR (140 KW) chilling unit starter panel and outgoing feeders to chilling unit compressor motors. The MCCB compartment shall contain :; | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 504030000 | 0 - 500 volts 96 x 96 sq mm digital voltmeter with selector switcha | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 504030000 | 0 - 315 amps 96 x 96 sq mm digital ammeter with 315/5 amps CT’s and selector switchq | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 504030000 | Over voltage tripping mechanism for persistent voltage exceeding 110% of the rated voltage for more than 5 minutes.z | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iv. | 504030000 | Phase indicating light shall be protected by 2 amps MCB’s. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
d. | 504030000 | 2 Nos 25 amps TPN MCCB, 10 HP DOL starters, over load relay with built in single phasing protection and outgoing feeders to primary chilled water pump motors. compartment shall contain CT operated digital ammeter of 0-25 amps range with selector switch, and an indicating lamp with MCB and toggle switch for ‘ON’ status of pump motors. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
g. | 504030000 | 3 Nos. 40 amps TPN MCCB and outgoing feeders to Variable Frequency Drive (VFD) panel and outgoing feeders to secondary chilled water pump motors. The compartments shall contain CT operated digital ammeter 0 - 40 amps range with selector switch and an indicating lamp with MCB and toggle switch for ‘ON’ status of pump motors. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
h. | 504030000 | 1 Nos. 80 amps TPN MCCB 40 HP star delta starter, over load relay with built in single phasing protection and outgoing feeders to condenser water pump motors (Working). The compartment shall contain CT operated digital ammeter of 0-80 amps range with selector switch and an indicating lamp with MCB and toggle switch for ‘ON’ status of pump motors. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 504030000 | 2 Nos. 25 amps TPN MCCB 10 HP DOL starter, over load relay with built in single phasing protection and outgoing feeders to condenser water pump motors for cold storage (1 working + 1standby). The compartment shall contain CT operated digital ammeter of suitable amps range with selector switch and an indicating lamp with MCB and toggle switch for ‘ON’ status of pump motors. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
j | 504030000 | 1 Nos. 80 amps TPN MCCBs, outgoing feed to 1 No. VFD panel at terrace floor and outgoing feeder to cooling tower fan motor (Working). The compartment shall contain an indicating lamp with MCB and toggle switch for ‘ON’ status of fan motor. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
k | 504030000 | 1 Nos. suitable amps TPN MPCB with 10 HP DOL starter, over load relay with built in single phasing protection and outgoing feeders to Supply Fan motors . Each of these compartment shall contain CT operated digital ammeter of suitable amps range with selector switch and an indicating lamp with MCB and toggle switch for ‘ON’ status of pump motors. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
l. | 504030000 | 2 Nos. suitable amps TPN MPCB with 1 HP DOL starter, over load relay with built in single phasing protection and outgoing feeders to Hot water recirculation pump (1working + 1 standby) . Each of these compartment shall contain direct operated digital ammeter of suitable amps range with selector switch and an indicating lamp with MCB and toggle switch for ‘ON’ status of pump motors. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
m. | 504030000 | 2 Nos 63 amp MCCB with space provision for star/delta (SPARE)x | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
n. | 504030000 | Necessary cable alleys, space for spare switches, internal wiring, control wiring/cabling and copper earthing of all equipment shall also be included. All switches and other components shall be motor duty ratingc | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Bus Coupler : | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 800 amps 4 pole MCCB with operating handle and with ON / OFF/Trip indicating lamps with control MCB’s, shunt trip etc. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13.2 | 504030000 | Motor Control Centre section No. 2 (415 V) consisting of : | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
a. | 504030000 | Incomingz | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | One No. 800 amps 4P Microprocessor based incoming MCCB with LSI protection complete with the following accessories : | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 504030000 | 0 - 500 volts 96 x 96 sq mm digital voltmeter with selector switch - 1 Set | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 504030000 | 0 - 800 amps 96 x 96 sq mm digital ammeter with 800/5 amps CT’s and selector switch - 1 Set | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 504030000 | Over voltage tripping mechanism for persistent voltage exceeding 110% of the rated voltage for more than 5 minutes - 1 Set | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iv. | 504030000 | Phase indicating lamps, with toggle switches - 3 Sets | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
b. | 504030000 | TPN bus bars shall be of Copper and shall be sleeved. Phase bus bars shall be rated at 800 amps (25 KA) and neutral bus bar shall be of 50% capacity. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Maximum density of copper bus bars for current carrying capacity shall be 1.4 amp per square mm. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Outgoingz | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
c. | 504030000 | 2 Nos. 315 amps TPN MCCB, and outgoing feeders to. 2 nos 200 TR (140 KW) chilling unit starter panel and outgoing feeders to chilling unit compressor motors. The MCCB compartment shall contain : | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 504030000 | 0 - 500 volts 96 x 96 sq mm digital voltmeter with selector switch. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 504030000 | 0 - 315 amps 96 x 96 sq mm digital ammeter with 315/5 amps CT’s and selector switch | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 504030000 | Over voltage tripping mechanism for persistent voltage exceeding 110% of the rated voltage for more than 5 minutes. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iv. | 504030000 | Phase indicating lightshall be protected by 2 amps MCB’s. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
d. | 504030000 | 1 Nos 25 amps TPN MCCB, 10 HP DOL starters, over load relay with built in single phasing protection and outgoing feeders to primary chilled water pump motors (Working). The compartment shall contain CT operated digital ammeter of 0-25 amps range with selector switch, and an indicating lamp with MCB and toggle switch for ‘ON’ status of pump motors. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
e. | 504030000 | 3 Nos. 40 amps TPN MCCB and outgoing feeders to Variable Frequency Drive (VFD) panel and outgoing feeders to secondary chilled water pump motors ( 2 working + 1 standby). The compartments shall contain CT operated digital ammeter 0 - 40 amps range with selector switch and an indicating lamp with MCB and toggle switch for ‘ON’ status of pump motors. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
f. | 504030000 | 2 Nos. 80 amps TPN MCCB 40 HP star delta starter, over load relay with built in single phasing protection and outgoing feeders to 2 nos condenser water pump motors (1 Working + 1standby). Each compartment shall contain CT operated digital ammeter of 0-80 amps range with selector switch and an indicating lamp with MCB and toggle switch for ‘ON’ status of pump motors. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
g. | 504030000 | 2 Nos. 80 amps TPN MCCBs, outgoing feed to 2 No. VFD panel at terrace floor and outgoing feeder to cooling tower fan motor (Both Working). The compartment shall contain an indicating lamp with MCB and toggle switch for ‘ON’ status of fan motor. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
h. | 504030000 | 1 Nos. suitable amps TPN MPCB with 10 HP DOL starter, over load relay with built in single phasing protection and outgoing feeders to Exhaust Fan motors . Each of these compartment shall contain CT operated digital ammeter of suitable amps range with selector switch and an indicating lamp with MCB and toggle switch for ‘ON’ status of pump motors. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 504030000 | 2 Nos. suitable amps TPN MPCB with 1 HP DOL starter, over load relay with built in single phasing protection and outgoing feeders to Hot water recirculation pump (1working + 1 standby) . Each of these compartment shall contain direct operated digital ammeter of suitable amps range with selector switch and an indicating lamp with MCB and toggle switch for ‘ON’ status of pump motors. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
j. | 504030000 | 2 Nos 63 amp MCCB with space provision for star/delta (SPARE) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Necessary cable alleys, space for spare switches, internal wiring, control wiring/cabling and copper earthing of all equipment shall also be included. All switches and other components shall be motor duty rating. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Motor Control Centre as described above. | [8 empty] | No. | 1 | 1499393 | 0 | 1499393 | 209915.02 | 0 | 0 | 0 | 0 | 0 | 1709308.02 | 1709308 | 15 | 1 | 224908.95 | 0 | 224908.95 | 31487.253 | 0 | 0 | 0 | 0 | 0 | 256396.203
Note | 504030000 | MCCB’s shall be motor duty type 2 co-ordinated and suitable for 25 KA (ICS) fault current. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 504030000 | CONTROL PANEL FOR AHU (WITH DOL / SD STARTER) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14.1 | 504030000 | Design, manufacture, supply of the following cubicle type, dead front, sheet steel, wall mounted control panels including anchoring into the wall, wiring, incoming cable wiring terminating into MCCB, copper earthing of suitable strip/dia & terminating into MCCB/MPCB in each panel shall be provided by the HVAC contractor. Only incoming cable upto the panel shall be in the scope of the Electrical contractor. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | All internal wiring power cabling and copper earthing of air handling unit motors from the panel shall be included. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | All outgoing shall be provided with Stop Manual /Auto selector switch to facilitate operation through BAS. All starters shall be provided with potential free Contact for Connections to Building Automation System. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | The panel shall include the following components and accessories | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
a. | 504030000 | MCCB/MPCB as per the ratings given below, suitable for motor duty and able to withstand fault level of 25 KA | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
b. | 504030000 | DOL / SD starter as per HP ratings | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
c. | 504030000 | Terminal block for power distribution | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
d. | 504030000 | Contactor, over load relay with built in single phasing protection | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
e. | 504030000 | Phase indicating lights and indicating light for ON status | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
f. | 504030000 | Digital volttmeter and digital ammeter with selector switches. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
g. | 504030000 | Time delay relay for delayed automatic restart of air handling unit motor. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
h. | 504030000 | Wiring for microswitch for rstopping the fan when fire damper closes. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 504030000 | For on/off/remote and local operation, 3 pole single throw switch shall be provided in each AHU panel to facilitate override of the automatic operation. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
j. | 504030000 | All starters shall be provided with suitable potential free contact for connections to the Building Automation System. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
k. | 504030000 | 3 Nos of Single Pole MCBs Shall be provided at the incoming section of the starter panel for DDC Panel , fire damper actuator & as a spare. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
l. | 504030000 | 220 / 24 V Transformer for Power supply to valves / damper actuators. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
m. | 504030000 | MCCB/MPCB shall be Type 2 Co-ordinated with the Motor starter. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
n. | 504030000 | Degree of Protection for the Outdoor starter panel shall be IP 55. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | The number of AHU control panels shall be as follows. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14.1.1 | 504030000 | MPCB suitable for 1.1 KW motor with DOL Starter | [8 empty] | No. | 1 | 22613 | 0 | 22613 | 3165.82 | 0 | 0 | 0 | 0 | 0 | 25778.82 | 25779 | 15 | 1 | 3391.95 | 0 | 3391.95 | 474.873 | 0 | 0 | 0 | 0 | 0 | 3866.823
14.1.2 | 504030000 | MPCB suitable for 1.5 KW motor with DOL Starter | [8 empty] | No. | 1 | 23079 | 0 | 23079 | 3231.06 | 0 | 0 | 0 | 0 | 0 | 26310.06 | 26310 | 15 | 1 | 3461.85 | 0 | 3461.85 | 484.659 | 0 | 0 | 0 | 0 | 0 | 3946.509
14.1.3 | 504030000 | MPCB suitable for 2.25 KW motor with DOL Starter | [8 empty] | No. | 3 | 23544 | 0 | 23544 | 3296.16 | 0 | 0 | 0 | 0 | 0 | 26840.16 | 80520 | 15 | 3 | 10594.8 | 0 | 10594.8 | 1483.272 | 0 | 0 | 0 | 0 | 0 | 12078.072
14.1.4 | 504030000 | MPCB suitable for 3.75 KW motor with DOL Starter | [8 empty] | No. | 1 | 23544 | 0 | 23544 | 3296.16 | 0 | 0 | 0 | 0 | 0 | 26840.16 | 26840 | 15 | 1 | 3531.6 | 0 | 3531.6 | 494.424 | 0 | 0 | 0 | 0 | 0 | 4026.024
15 | 504030000 | CONTROL PANEL FOR AHU (OPERATED THROUGH VFD) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15.1 | 504030000 | Design, manufacture, supply of the following cubicle type, dead front, sheet steel, wall mounted control panels including anchoring into the wall, wiring, incoming cable wiring terminating into MCCB, copper earthing of suitable strip/dia & terminating into MCCB/MPCB in each panel shall be provided by the HVAC contractor. Only incoming cable upto the panel shall be in the scope of the Electrical contractor. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | All internal wiring power cabling and copper earthing of air handling unit motors from the panel to VFD & to the motor shall be included. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | All outgoing shall be provided with Stop / Manual /Auto selector switch to facilitate operation through BAS. All starters shall be provided with potential free Contact for Connections to Building Automation System. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | The panel shall include the following components and accessories. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
a. | 504030000 | MCCB/MPCB as per the ratings given below, suitable for motor duty and able to withstand fault level of 25 KA. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
b. | 504030000 | VFD starter as per HP ratings (Supply of VFD under item No. 11 of Imported section) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
c. | 504030000 | Terminal block for power distribution. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
d. | 504030000 | Phase indicating lights and indicating light for ON status. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
e. | 504030000 | Digital voltmeter and digital ammeter with selector switches. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
f. | 504030000 | Wiring for microswitch for stopping the fan when fire damper closes. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
g. | 504030000 | For on/off/remote and local operation, 3 pole single throw switch shall be provided in each AHU panel to facilitate override of the automatic operation. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
h. | 504030000 | All starters shall be provided with suitable potential free contact for connections to the Building Automation System. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 504030000 | 3 Nos of Single Pole MCBs Shall be provided at the incoming section of the starter panel for DDC Panel , fire damper actuator & as a spare. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
j. | 504030000 | 220 / 24 V Transformer | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
k. | 504030000 | VFD : space provision for mounting of VFD only. The quantity, unit rate and amount for VFD is appearing separately in BOQ. Hence not to be included in the cost of these control panel. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
l. | 504030000 | MCCB/MPCB shall be Type 2 Co- ordinated with the Motor starter. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
m. | 504030000 | Degree of Protection for the Outdoor starters panel shall be IP 55. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | The number of AHU control panels shall be as follows. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15.1.1 | 504030000 | 25 amps MCCB, 2 HP VFD . | [8 empty] | No. | 1 | 28458 | 0 | 28458 | 3984.12 | 0 | 0 | 0 | 0 | 0 | 32442.12 | 32442 | 15 | 1 | 4268.7 | 0 | 4268.7 | 597.618 | 0 | 0 | 0 | 0 | 0 | 4866.318
15.1.2 | 504030000 | 25 amps MCCB, 3 HP VFD . | [8 empty] | Nos. | 7 | 28458 | 0 | 28458 | 3984.12 | 0 | 0 | 0 | 0 | 0 | 32442.12 | 227095 | 15 | 7 | 29880.9 | 0 | 29880.9 | 4183.326 | 0 | 0 | 0 | 0 | 0 | 34064.226
15.1.3 | 504030000 | 25 amps MCCB, 5 HP VFD . | [8 empty] | Nos. | 6 | 29389 | 0 | 29389 | 4114.46 | 0 | 0 | 0 | 0 | 0 | 33503.46 | 201021 | 15 | 6 | 26450.1 | 0 | 26450.1 | 3703.014 | 0 | 0 | 0 | 0 | 0 | 30153.114
15.1.4 | 504030000 | 25 amps MCCB, 7.5 HP VFD . | [8 empty] | No. | 1 | 30786 | 0 | 30786 | 4310.04 | 0 | 0 | 0 | 0 | 0 | 35096.04 | 35096 | 15 | 1 | 4617.9 | 0 | 4617.9 | 646.506 | 0 | 0 | 0 | 0 | 0 | 5264.406
16 | 504030000 | CONTROL PANELS FOR FANS (OPERATED THROUGH VFD) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Design, manufacture, supply of the following cubicle type, dead front, sheet steel, wall mounted control panels, including anchoring into the wall, incoming cable wiring terminating into MCCB and copper earthing of suitable strip/dia in each panel shall be provided by the HVAC contractor. Only incoming cable upto the panel shall be in the scope of the Electrical contractor. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | All outgoing shall be provided with Stop /Manual Auto selector switch to facilitate operation through BAS. All starters shall be provided with potential free Contact for Connections to Building Automation System. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | All internal wiring, power cabling and copper earthing of motors from the panel to VFD & to the motor shall be included. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | The panel shall include the following co mponents & accessories. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
a. | 504030000 | MCCB/MPCB as per the ratings given below, suitable for motor duty and able to withstand fault level of 25 KA. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
b. | 504030000 | Terminal block for power distribution as required. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
c. | 504030000 | Phase indicating lights and indicating light for ON status. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
d. | 504030000 | 144 mm x 144 mm voltmeter and digital ammeter | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
e. | 504030000 | Wiring for microswitch for stopping the fan when fire damper closes (in case of Fan only). | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
f. | 504030000 | For on/off/remote and local operation, 3 pole single throw switch hall be provided in each panel to facilitate override of the automatic operation. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
g. | 504030000 | 3 Nos of Single Pole MCBs Shall be provided at the incoming section of the starter panel for DDC Panel , fire damper actuator & as a spare. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
h. | 504030000 | All starters shall be provided with suitable potential free contract f or connections to the Building Automation System. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 504030000 | 220 / 24 V Transformer | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
j. | 504030000 | VFD : space provision for mounting of VFD only. The quantity, unit rate and amount for VFD is appearing separately in BOQ. Hence not to be included in the cost of these control panel. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
k. | 504030000 | MCCB/MPCB shall be Type 2 Co-ordinated with the Mo tor starter. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
l. | 504030000 | Degree of Protection for the Outdoor start er panel shall be IP 55. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | The number of control panels shall be as follows. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16.1 | 504030000 | 80 amps MCCB, 40 HP VFD for cooling tower IP 55 required. | [8 empty] | Nos. | 3 | 40027 | 0 | 40027 | 5603.78 | 0 | 0 | 0 | 0 | 0 | 45630.78 | 136892 | 15 | 3 | 18012.15 | 0 | 18012.15 | 2521.701 | 0 | 0 | 0 | 0 | 0 | 20533.851
17 | 504030000 | CONTROL PANELS FOR FANS | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Design, manufacture, supply of the following cubicle type, dead front, sheet steel, wall mounted control panels, including anchoring into the wall, incoming cable wiring terminating into MCCB and copper earthing, in each panel shall be provided by the HVAC contractor. Only incoming cable upto the panel shall be in the scope of the Electrical contractor. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | All outgoing shall be provided with Stop /Manual /Auto selector switch to facilitate operation through BAS. All starters shall be provided with potential free Contact for Connections to Building Automation System. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | All wiring and copper earthing of motors from the panel shall be included. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | The panel shall include the following c omponents & accessories. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
a. | 504030000 | MCCB/MPCB as per the ratings given below, suitable for mot or duty and able to withstand fault level of 25 KA. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
b. | 504030000 | DOL / SD starter as per HP gratings g iven. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
c. | 504030000 | Terminal block for power distribut ion as required. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
d. | 504030000 | Contactor, over load relay with built in sing le phasing protection. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
e. | 504030000 | Phase indicating lights and ind icating light for ON status. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
f. | 504030000 | 144 mm x 144 mm voltmet er and digital ammeter. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
g. | 504030000 | Time delay relay for delayed automatic res tart of motor. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
h. | 504030000 | Wiring for microswitch for stopping the fan when fire damper closes (in case of Fire operation only). | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 504030000 | For on/off/remote and local operat ion, 3 pole single throw switch shall be provided in each panel to facilitate override of the automatic operation. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
j. | 504030000 | All starters shall be provided with suitable pote ntial free contract for connections to the Building Automation System. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
k. | 504030000 | MCCB/MPCB shall be Type 2 Co-ordinated w ith the Motor starter. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
l. | 504030000 | Degree of Protection for the Outdoor starter panel shall be IP 55. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | The number of control pan els shall be as follows. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17.1 | 504030000 | MPCB suitable for 2.25 KW/ 3HP motor with DOL Starter | [8 empty] | Nos. | 8 | 21711 | 0 | 21711 | 3039.54 | 0 | 0 | 0 | 0 | 0 | 24750.54 | 198004 | 15 | 8 | 26053.2 | 0 | 26053.2 | 3647.448 | 0 | 0 | 0 | 0 | 0 | 29700.648
17.2 | 504030000 | MPCB suitable for 3.75 KW/ 5 HP motor with DOL Starter | [8 empty] | Nos. | 4 | 21711 | 0 | 21711 | 3039.54 | 0 | 0 | 0 | 0 | 0 | 24750.54 | 99002 | 15 | 4 | 13026.6 | 0 | 13026.6 | 1823.724 | 0 | 0 | 0 | 0 | 0 | 14850.324
17.3 | 504030000 | MPCB suitable for 5.6 KW/ 7.5 HP motor with DOL Starter | [8 empty] | Nos. | 6 | 25407 | 0 | 25407 | 3556.98 | 0 | 0 | 0 | 0 | 0 | 28963.98 | 173784 | 15 | 6 | 22866.3 | 0 | 22866.3 | 3201.282 | 0 | 0 | 0 | 0 | 0 | 26067.582
17.4 | 504030000 | MPCB suitable for 7.5 KW/ 10 HP motor with DOL Starter | [8 empty] | Nos. | 9 | 25407 | 0 | 25407 | 3556.98 | 0 | 0 | 0 | 0 | 0 | 28963.98 | 260676 | 15 | 9 | 34299.45 | 0 | 34299.45 | 4801.923 | 0 | 0 | 0 | 0 | 0 | 39101.373
17.5 | 504030000 | MPCB suitable for 9.3 KW/ 12.5 HP motor with STAR DELTA Starter | [8 empty] | Nos. | 2 | 33580 | 0 | 33580 | 4701.2 | 0 | 0 | 0 | 0 | 0 | 38281.2 | 76562 | 15 | 2 | 10074 | 0 | 10074 | 1410.36 | 0 | 0 | 0 | 0 | 0 | 11484.36
17.6 | 504030000 | MCCB suitable for 15 KW/ 20 HP motor with STAR DELTA Starter | [8 empty] | No. | 1 | 53471 | 0 | 53471 | 7485.94 | 0 | 0 | 0 | 0 | 0 | 60956.94 | 60957 | 15 | 1 | 8020.65 | 0 | 8020.65 | 1122.891 | 0 | 0 | 0 | 0 | 0 | 9143.541
18 | 504030000 | CONTROL PANELS FOR HEAT RECOVERY UNIT | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Design, manufacture, supply of the following cubicle type, dead front, sheet steel, wall mounted control panels, including anchoring into the wall, incoming cable wiring terminating into MCCB and copper earthing, in each panel shall be provided by the HVAC contractor. Only incoming cable upto the panel shall be in the scope of the Electrical contractor. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | All outgoing shall be provid ed with Stop /Manual /Auto selector switch to facilitate operation through BAS. All starters shall be provided with potential free Contact for Connections to Building Automation System. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | All wiring and copper earthing of motors from the panel sh all be included. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | The panel shall include the follo wing components & accessories. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
a. | 504030000 | MCCB/MPCB as per the ratings given be low, suitable for motor duty and able to withstand fault level of 25 KA. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
b. | 504030000 | DOL / SD starter as p er HP gratings given. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
c. | 504030000 | Terminal block for power distribution as re quired. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
d. | 504030000 | Contactor, over load relay with built in sing le ph asing protection. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
e. | 504030000 | Phase indicating lights and indicating lig ht for ON status. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
f. | 504030000 | 144 mm x 144 mm voltmeter nd digital ammeter. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
g. | 504030000 | Time delay relay for del ayed automatic res tart of motor. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
h. | 504030000 | Wiring for microswitch for stopp ing the fan when fire damper closes (in case of Fire operation only). | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 504030000 | For on/off/remote and local opera tion, 3 pole single throw switch shall be provided in each panel to facilitate override of the automatic operation. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
j. | 504030000 | All starters shall be provid ed with suitable potential free contract for connections to the Building Automation System. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
k. | 504030000 | IP 55 required | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
l. | 504030000 | MCCB/MPCB shall be Type 2 Co-ordin ated with the Motor starter. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | The number of control pane ls shall be as follows. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18.1 | 504030000 | Incoming | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 63 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Bus Bars | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 63 amps (25 KA) TPNcopper bus bars with heat shrinkable insulation sleeve. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Outgoing | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | a) MPCB suitable for 9.3 KW motor with STAR DELTA Starter (For supply fan motor) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | b) MPCB suitable for 3.75 KW motor with DOL Starter (For Exhaust fan motor) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | c) MPCB suitable for 0.75 KW motor with DOL Starter (For HRW motor) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | MCC control panel described as above | [8 empty] | Nos. | 2 | 105450 | 0 | 105450 | 14763 | 0 | 0 | 0 | 0 | 0 | 120213 | 240426 | 15 | 2 | 31635 | 0 | 31635 | 4428.9 | 0 | 0 | 0 | 0 | 0 | 36063.9
19 | 504030000 | CONTROL PANELS FOR DUAL OPERATION CAR PARK FRESH AIR & EXHAUST AIR FANS | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Design, manufacture, supply of the following cubicle type, dead front, sheet steel, wall mounted control panels, including anchoring into the wall, incoming cable wiring terminating into MCCB and copper earthing, in each panel shall be provided by the HVAC contractor. Only incoming cable upto the panel shall be in the scope of the Electrical contractor. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | All outgoing shall be provided with Stop /Manual /Auto selector switch to facilitate operation through BAS. All starters shall be provided with potential free Contact for Connections to Building Automation System. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | All wiring and copper earthing of motors from the panel shall be included. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | The panel shall include the following components & accessories. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
a. | 504030000 | MCCB/MPCB as per the ratings given below, suitable for motor duty and able to withstand fault level of 25 KA. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
b. | 504030000 | DOL / SD starter as per HP gratings given. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
c. | 504030000 | Terminal block for power distribution as required. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
d. | 504030000 | Contactor, over load relay with built in single phasing protection. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
e. | 504030000 | Phase indicating lights and indicating light for ON status. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
f. | 504030000 | 144 mm x 144 mm voltmeter and digital ammeter. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
g. | 504030000 | Time delay relay for delayed automatic restart of motor. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
h. | 504030000 | Wiring for microswitch for stopping the fan when fire damper closes (in case of Fire operation only). | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 504030000 | For on/off/remote and local operation, 3 pole single throw switch shall be provided in each panel to facilitate override of the automatic operation. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
j. | 504030000 | All starters shall be provided with suitable potential free contract for connections to the Building Automation System. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
k. | 504030000 | MCCB/MPCB shall be Type 2 Co-ordinated with the Motor starter. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | The number of control panels shall be as follows. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19.1 | 504030000 | Starter Panel for Dual speed operated 30 HP Motor in Normal & Fire mode as per the requirement under section B 8 and with above requirements. | [8 empty] | Nos. | 1 | 71500 | 0 | 71500 | 10010 | 0 | 0 | 0 | 0 | 0 | 81510 | 81510 | 15 | 1 | 10725 | 0 | 10725 | 1501.5 | 0 | 0 | 0 | 0 | 0 | 12226.5
19.2 | 504030000 | Starter Panel for Dual speed operated 60 HP Motor in Normal & Fire mode as per the requirement under section B 8, B11 and with above requirements. | [8 empty] | Nos. | 4 | 91127 | 0 | 91127 | 12757.78 | 0 | 0 | 0 | 0 | 0 | 103884.78 | 415539 | 15 | 4 | 54676.2 | 0 | 54676.2 | 7654.668 | 0 | 0 | 0 | 0 | 0 | 62330.868
20 | 504030000 | Supply of 315 Amps Manual changeover switch with 315 A TPN Isolator MCCB (25 KA) breaking capacity with operating handle in 1.6 mm thick CRCA sheet steel enclosure of approved make design and painted with approved paint shade including supply & laying of suitable rating Aluminium Armoured cable from MCC HVAC panel. | [8 empty] | No. | 1 | 81500 | 0 | 81500 | 11410 | 0 | 0 | 0 | 0 | 0 | 92910 | 92910 | 15 | 1 | 12225 | 0 | 12225 | 1711.5 | 0 | 0 | 0 | 0 | 0 | 13936.5
C. | 504030000 | PIPING-CHILLED, HOT WATER AND CONDENSER WATER | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 504030000 | Providing the following MS C Class pipes with specified wall thickness (6 mm) cut to required lengths and installed with all welded / grooved joints, providing and fixing in position necessary fittings like bends, elbows, tees, reducers, mating flanges & sockets for BAS, fabricated to size and shape in workshop or brought out ready made where available of acceptable quality. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.1 | 504030000 | 300 mm dia MS pipes. | [8 empty] | RM | 2 | 2497 | 0 | 2497 | 124.85 | 0 | 0 | 0 | 0 | 0 | 2621.85 | 5244 | 15 | 2 | 749.1 | 0 | 749.1 | 37.455 | 0 | 0 | 0 | 0 | 0 | 786.555
1.2 | 504030000 | 250 mm dia MS pipes. | [8 empty] | RM | 120 | 2129 | 0 | 2129 | 106.45 | 0 | 0 | 0 | 0 | 0 | 2235.45 | 268254 | 15 | 120 | 38322 | 0 | 38322 | 1916.1 | 0 | 0 | 0 | 0 | 0 | 40238.1
2 | 504030000 | Providing the following MS class ‘C’ pipes (Wall Thickness as per IS code) cut to required lengths and installed with all welded joints, providing and fixing in position the necessary fittings like elbows, tees and reducers, mating flanges & sockets for BAS: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.1 | 504030000 | 200 mm dia MS pipes | [8 empty] | RM | 145 | 1700 | 0 | 1700 | 85 | 0 | 0 | 0 | 0 | 0 | 1785 | 258825 | 15 | 145 | 36975 | 0 | 36975 | 1848.75 | 0 | 0 | 0 | 0 | 0 | 38823.75
2.2 | 504030000 | 150 mm dia MS pipes | [8 empty] | RM | 225 | 1130 | 0 | 1130 | 56.5 | 0 | 0 | 0 | 0 | 0 | 1186.5 | 266963 | 15 | 225 | 38137.5 | 0 | 38137.5 | 1906.875 | 0 | 0 | 0 | 0 | 0 | 40044.375
2.3 | 504030000 | 125 mm dia MS pipes | [8 empty] | RM | 75 | 951 | 0 | 951 | 47.55 | 0 | 0 | 0 | 0 | 0 | 998.55 | 74891 | 15 | 75 | 10698.75 | 0 | 10698.75 | 534.9375 | 0 | 0 | 0 | 0 | 0 | 11233.6875
2.4 | 504030000 | 100 mm dia MS pipes | [8 empty] | RM | 100 | 772 | 0 | 772 | 38.6 | 0 | 0 | 0 | 0 | 0 | 810.6 | 81060 | 15 | 100 | 11580 | 0 | 11580 | 579 | 0 | 0 | 0 | 0 | 0 | 12159
2.5 | 504030000 | 80 mm dia MS pipes | [8 empty] | RM | 185 | 524 | 0 | 524 | 26.2 | 0 | 0 | 0 | 0 | 0 | 550.2 | 101787 | 15 | 185 | 14541 | 0 | 14541 | 727.05 | 0 | 0 | 0 | 0 | 0 | 15268.05
2.6 | 504030000 | 65 mm dia MS pipes | [8 empty] | RM | 325 | 433 | 0 | 433 | 21.65 | 0 | 0 | 0 | 0 | 0 | 454.65 | 147761 | 15 | 325 | 21108.75 | 0 | 21108.75 | 1055.4375 | 0 | 0 | 0 | 0 | 0 | 22164.1875
2.7 | 504030000 | 50 mm dia MS pipes | [8 empty] | RM | 775 | 330 | 0 | 330 | 16.5 | 0 | 0 | 0 | 0 | 0 | 346.5 | 268538 | 15 | 775 | 38362.5 | 0 | 38362.5 | 1918.125 | 0 | 0 | 0 | 0 | 0 | 40280.625
2.8 | 504030000 | 40 mm dia MS pipes | [8 empty] | RM | 365 | 233 | 0 | 233 | 11.65 | 0 | 0 | 0 | 0 | 0 | 244.65 | 89297 | 15 | 365 | 12756.75 | 0 | 12756.75 | 637.8375 | 0 | 0 | 0 | 0 | 0 | 13394.5875
2.9 | 504030000 | 32 mm dia MS pipes | [8 empty] | RM | 600 | 201 | 0 | 201 | 10.05 | 0 | 0 | 0 | 0 | 0 | 211.05 | 126630 | 15 | 600 | 18090 | 0 | 18090 | 904.5 | 0 | 0 | 0 | 0 | 0 | 18994.5
2.1 | 504030000 | 25 mm dia MS pipes | [8 empty] | RM | 2500 | 156 | 0 | 156 | 7.8 | 0 | 0 | 0 | 0 | 0 | 163.8 | 409500 | 15 | 2500 | 58500 | 0 | 58500 | 2925 | 0 | 0 | 0 | 0 | 0 | 61425
3 | 504030000 | Providing the following butterfly valves (PN16) with counter flanges, nuts & bolts and gasket to suit pressure rating. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.1 | 504030000 | 300 mm dia Valves. | [8 empty] | Nos. | 1 | 19714 | 0 | 19714 | 985.7 | 0 | 0 | 0 | 0 | 0 | 20699.7 | 20700 | 15 | 1 | 2957.1 | 0 | 2957.1 | 147.855 | 0 | 0 | 0 | 0 | 0 | 3104.955
3.2 | 504030000 | 250 mm dia Vbalves. | [8 empty] | Nos. | 9 | 16584 | 0 | 16584 | 829.2 | 0 | 0 | 0 | 0 | 0 | 17413.2 | 156719 | 15 | 9 | 22388.4 | 0 | 22388.4 | 1119.42 | 0 | 0 | 0 | 0 | 0 | 23507.82
3.3 | 504030000 | 200 mm dia Valv es. | [8 empty] | Nos. | 6 | 10443 | 0 | 10443 | 522.15 | 0 | 0 | 0 | 0 | 0 | 10965.15 | 65791 | 15 | 6 | 9398.7 | 0 | 9398.7 | 469.935 | 0 | 0 | 0 | 0 | 0 | 9868.635
3.4 | 504030000 | 150 mm dia Valv es. | [8 empty] | Nos. | 12 | 4787 | 0 | 4787 | 239.35 | 0 | 0 | 0 | 0 | 0 | 5026.35 | 60316 | 15 | 12 | 8616.6 | 0 | 8616.6 | 430.83 | 0 | 0 | 0 | 0 | 0 | 9047.43
3.5 | 504030000 | 125 mm dia Valves. | [8 empty] | Nos. | 12 | 3733 | 0 | 3733 | 186.65 | 0 | 0 | 0 | 0 | 0 | 3919.65 | 47036 | 15 | 12 | 6719.4 | 0 | 6719.4 | 335.97 | 0 | 0 | 0 | 0 | 0 | 7055.37
3.6 | 504030000 | 100 mm dia Valves. | [8 empty] | Nos. | 4 | 3398 | 0 | 3398 | 169.9 | 0 | 0 | 0 | 0 | 0 | 3567.9 | 14272 | 15 | 4 | 2038.8 | 0 | 2038.8 | 101.94 | 0 | 0 | 0 | 0 | 0 | 2140.74
3.7 | 504030000 | 80 mm dia Valves. | [8 empty] | Nos. | 3 | 2564 | 0 | 2564 | 128.2 | 0 | 0 | 0 | 0 | 0 | 2692.2 | 8077 | 15 | 3 | 1153.8 | 0 | 1153.8 | 57.69 | 0 | 0 | 0 | 0 | 0 | 1211.49
3.8 | 504030000 | 65 mm dia Valves. | [8 empty] | Nos. | 8 | 2364 | 0 | 2364 | 118.2 | 0 | 0 | 0 | 0 | 0 | 2482.2 | 19858 | 15 | 8 | 2836.8 | 0 | 2836.8 | 141.84 | 0 | 0 | 0 | 0 | 0 | 2978.64
3.9 | 504030000 | 50 mm dia Valves. | [8 empty] | Nos. | 16 | 2190 | 0 | 2190 | 109.5 | 0 | 0 | 0 | 0 | 0 | 2299.5 | 36792 | 15 | 16 | 5256 | 0 | 5256 | 262.8 | 0 | 0 | 0 | 0 | 0 | 5518.8
4 | 504030000 | Providing the following 3-Way valves with counter flanges, nuts & bolts and gasket to suit pressure rating. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4.1 | 504030000 | 200 mm dia Valves. | [8 empty] | Nos. | 2 | 177171 | 0 | 177171 | 24803.94 | 0 | 0 | 0 | 0 | 0 | 201974.94 | 403950 | 15 | 2 | 53151.3 | 0 | 53151.3 | 7441.182 | 0 | 0 | 0 | 0 | 0 | 60592.482
4.2 | 504030000 | 25 mm dia Valves. | [8 empty] | Nos. | 8 | 19584 | 0 | 19584 | 2741.76 | 0 | 0 | 0 | 0 | 0 | 22325.76 | 178606 | 15 | 8 | 23500.8 | 0 | 23500.8 | 3290.112 | 0 | 0 | 0 | 0 | 0 | 26790.912
5 | 504030000 | Supplying the following double regulating manual BALANCING VALVES. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.1 | 504030000 | 25 mm dia. | [8 empty] | Nos. | 8 | 3139 | 0 | 3139 | 156.95 | 0 | 0 | 0 | 0 | 0 | 3295.95 | 26368 | 15 | 8 | 3766.8 | 0 | 3766.8 | 188.34 | 0 | 0 | 0 | 0 | 0 | 3955.14
6 | 504030000 | Supply of motorised butterfly valve (PN 16) of following sizes with counter flanges and accessories | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6.1 | 504030000 | 200 mm dia Valves. | [8 empty] | Nos. | 4 | 32733 | 0 | 32733 | 4582.62 | 0 | 0 | 0 | 0 | 0 | 37315.62 | 149262 | 15 | 4 | 19639.8 | 0 | 19639.8 | 2749.572 | 0 | 0 | 0 | 0 | 0 | 22389.372
6.2 | 504030000 | 150 mm dia Valves. | [8 empty] | Nos. | 2 | 30336 | 0 | 30336 | 4247.04 | 0 | 0 | 0 | 0 | 0 | 34583.04 | 69166 | 15 | 2 | 9100.8 | 0 | 9100.8 | 1274.112 | 0 | 0 | 0 | 0 | 0 | 10374.912
7 | 504030000 | Providing following ball valves without Y strainer. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7.1 | 504030000 | 50 mm dia valves | [8 empty] | Nos. | 24 | 2907 | 0 | 2907 | 145.35 | 0 | 0 | 0 | 0 | 0 | 3052.35 | 73256 | 15 | 24 | 10465.2 | 0 | 10465.2 | 523.26 | 0 | 0 | 0 | 0 | 0 | 10988.46
7.2 | 504030000 | 40 mm dia valves | [8 empty] | Nos. | 6 | 2392 | 0 | 2392 | 119.6 | 0 | 0 | 0 | 0 | 0 | 2511.6 | 15070 | 15 | 6 | 2152.8 | 0 | 2152.8 | 107.64 | 0 | 0 | 0 | 0 | 0 | 2260.44
7.3 | 504030000 | 32 mm dia valves | [8 empty] | Nos. | 6 | 2211 | 0 | 2211 | 110.55 | 0 | 0 | 0 | 0 | 0 | 2321.55 | 13929 | 15 | 6 | 1989.9 | 0 | 1989.9 | 99.495 | 0 | 0 | 0 | 0 | 0 | 2089.395
7.4 | 504030000 | 25 m m dia valves | [8 empty] | Nos. | 8 | 1705 | 0 | 1705 | 85.25 | 0 | 0 | 0 | 0 | 0 | 1790.25 | 14322 | 15 | 8 | 2046 | 0 | 2046 | 102.3 | 0 | 0 | 0 | 0 | 0 | 2148.3
8 | 504030000 | Providing the following ball valves with Y strainer | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8.1 | 504030000 | 40 mm dia Val ves | [8 empty] | Nos. | 6 | 3684 | 0 | 3684 | 184.2 | 0 | 0 | 0 | 0 | 0 | 3868.2 | 23209 | 15 | 6 | 3315.6 | 0 | 3315.6 | 165.78 | 0 | 0 | 0 | 0 | 0 | 3481.38
8.2 | 504030000 | 32 mm dia Val ves | [8 empty] | Nos. | 6 | 3352 | 0 | 3352 | 167.6 | 0 | 0 | 0 | 0 | 0 | 3519.6 | 21118 | 15 | 6 | 3016.8 | 0 | 3016.8 | 150.84 | 0 | 0 | 0 | 0 | 0 | 3167.64
8.3 | 504030000 | 25 mm dia Valves | [8 empty] | Nos. | 8 | 2679 | 0 | 2679 | 133.95 | 0 | 0 | 0 | 0 | 0 | 2812.95 | 22504 | 15 | 8 | 3214.8 | 0 | 3214.8 | 160.74 | 0 | 0 | 0 | 0 | 0 | 3375.54
9 | 504030000 | Providing the following check valves : | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.1 | 504030000 | 200 mm dia valves | [8 empty] | Nos. | 3 | 11670 | 0 | 11670 | 583.5 | 0 | 0 | 0 | 0 | 0 | 12253.5 | 36761 | 15 | 3 | 5251.5 | 0 | 5251.5 | 262.575 | 0 | 0 | 0 | 0 | 0 | 5514.075
9.2 | 504030000 | 150 mm dia valves | [8 empty] | Nos. | 3 | 6467 | 0 | 6467 | 323.35 | 0 | 0 | 0 | 0 | 0 | 6790.35 | 20371 | 15 | 3 | 2910.15 | 0 | 2910.15 | 145.5075 | 0 | 0 | 0 | 0 | 0 | 3055.6575
9.3 | 504030000 | 125 mm dia valves | [8 empty] | Nos. | 6 | 5266 | 0 | 5266 | 263.3 | 0 | 0 | 0 | 0 | 0 | 5529.3 | 33176 | 15 | 6 | 4739.4 | 0 | 4739.4 | 236.97 | 0 | 0 | 0 | 0 | 0 | 4976.37
9.4 | 504030000 | 100 mm dia valves | [8 empty] | Nos. | 1 | 4059 | 0 | 4059 | 202.95 | 0 | 0 | 0 | 0 | 0 | 4261.95 | 4262 | 15 | 1 | 608.85 | 0 | 608.85 | 30.4425 | 0 | 0 | 0 | 0 | 0 | 639.2925
10 | 504030000 | Providing the following ‘Y’ Strainers : | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10.1 | 504030000 | 250 mm dia strainers | [8 empty] | Nos. | 1 | 25876 | 0 | 25876 | 1293.8 | 0 | 0 | 0 | 0 | 0 | 27169.8 | 27170 | 15 | 1 | 3881.4 | 0 | 3881.4 | 194.07 | 0 | 0 | 0 | 0 | 0 | 4075.47
10.2 | 504030000 | 200 mm dia strainers | [8 empty] | Nos. | 6 | 16719 | 0 | 16719 | 835.95 | 0 | 0 | 0 | 0 | 0 | 17554.95 | 105330 | 15 | 6 | 15047.1 | 0 | 15047.1 | 752.355 | 0 | 0 | 0 | 0 | 0 | 15799.455
10.3 | 504030000 | 150 mm dia strainers | [8 empty] | Nos. | 12 | 10281 | 0 | 10281 | 514.05 | 0 | 0 | 0 | 0 | 0 | 10795.05 | 129541 | 15 | 12 | 18505.8 | 0 | 18505.8 | 925.29 | 0 | 0 | 0 | 0 | 0 | 19431.09
10.4 | 504030000 | 125 mm dia strainers | [8 empty] | Nos. | 18 | 7555 | 0 | 7555 | 377.75 | 0 | 0 | 0 | 0 | 0 | 7932.75 | 142790 | 15 | 18 | 20398.5 | 0 | 20398.5 | 1019.925 | 0 | 0 | 0 | 0 | 0 | 21418.425
10.5 | 504030000 | 100 mm dia strainers | [8 empty] | Nos. | 2 | 6277 | 0 | 6277 | 313.85 | 0 | 0 | 0 | 0 | 0 | 6590.85 | 13182 | 15 | 2 | 1883.1 | 0 | 1883.1 | 94.155 | 0 | 0 | 0 | 0 | 0 | 1977.255
10.6 | 504030000 | 80 mm dia strainers | [8 empty] | Nos. | 1 | 5018 | 0 | 5018 | 250.9 | 0 | 0 | 0 | 0 | 0 | 5268.9 | 5269 | 15 | 1 | 752.7 | 0 | 752.7 | 37.635 | 0 | 0 | 0 | 0 | 0 | 790.335
10.7 | 504030000 | 65 mm dia strainers | [8 empty] | Nos. | 4 | 4469 | 0 | 4469 | 223.45 | 0 | 0 | 0 | 0 | 0 | 4692.45 | 18770 | 15 | 4 | 2681.4 | 0 | 2681.4 | 134.07 | 0 | 0 | 0 | 0 | 0 | 2815.47
10.8 | 504030000 | 50 mm dia strainers | [8 empty] | Nos. | 5 | 4043 | 0 | 4043 | 202.15 | 0 | 0 | 0 | 0 | 0 | 4245.15 | 21226 | 15 | 5 | 3032.25 | 0 | 3032.25 | 151.6125 | 0 | 0 | 0 | 0 | 0 | 3183.8625
10.9 | 504030000 | 40 mm dia strainers | [8 empty] | Nos. | 1 | 3113 | 0 | 3113 | 155.65 | 0 | 0 | 0 | 0 | 0 | 3268.65 | 3269 | 15 | 1 | 466.95 | 0 | 466.95 | 23.3475 | 0 | 0 | 0 | 0 | 0 | 490.2975
11 | 504030000 | Providing the following pot strainers | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11.1 | 504030000 | 250 mm dia pip es | [8 empty] | Nos. | 2 | 106334 | 0 | 106334 | 5316.7 | 0 | 0 | 0 | 0 | 0 | 111650.7 | 223301 | 15 | 2 | 31900.2 | 0 | 31900.2 | 1595.01 | 0 | 0 | 0 | 0 | 0 | 33495.21
12 | 504030000 | Supply of flexible connections of suitable pressure rating to be installed at pump suction, discharge and at pipes crossing building expansion joints. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12.1 | 504030000 | 250 mm dia pipes | [8 empty] | No. | 1 | 11943 | 0 | 11943 | 597.15 | 0 | 0 | 0 | 0 | 0 | 12540.15 | 12540 | 15 | 1 | 1791.45 | 0 | 1791.45 | 89.5725 | 0 | 0 | 0 | 0 | 0 | 1881.0225
12.2 | 504030000 | 200 mm dia pipes | [8 empty] | No. | 6 | 7091 | 0 | 7091 | 354.55 | 0 | 0 | 0 | 0 | 0 | 7445.55 | 44673 | 15 | 6 | 6381.9 | 0 | 6381.9 | 319.095 | 0 | 0 | 0 | 0 | 0 | 6700.995
12.3 | 504030000 | 150 mm dia pipes | [8 empty] | No. | 12 | 5264 | 0 | 5264 | 263.2 | 0 | 0 | 0 | 0 | 0 | 5527.2 | 66326 | 15 | 12 | 9475.2 | 0 | 9475.2 | 473.76 | 0 | 0 | 0 | 0 | 0 | 9948.96
12.4 | 504030000 | 125 mm dia pipes | [8 empty] | No. | 18 | 4657 | 0 | 4657 | 232.85 | 0 | 0 | 0 | 0 | 0 | 4889.85 | 88017 | 15 | 18 | 12573.9 | 0 | 12573.9 | 628.695 | 0 | 0 | 0 | 0 | 0 | 13202.595
12.5 | 504030000 | 100 mm dia pipes | [8 empty] | No. | 1 | 4149 | 0 | 4149 | 207.45 | 0 | 0 | 0 | 0 | 0 | 4356.45 | 4356 | 15 | 1 | 622.35 | 0 | 622.35 | 31.1175 | 0 | 0 | 0 | 0 | 0 | 653.4675
13 | 504030000 | Supplying of Auto air vents. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13.1 | 504030000 | 25 mm dia pipes | [8 empty] | Nos. | 11 | 1651 | 0 | 1651 | 82.55 | 0 | 0 | 0 | 0 | 0 | 1733.55 | 19069 | 15 | 11 | 2724.15 | 0 | 2724.15 | 136.2075 | 0 | 0 | 0 | 0 | 0 | 2860.3575
14 | 504030000 | Providing 80mm dia probe type flow meter to measure the flow in CHW & CDW pipe lines. The flow meter shall be provided with necessary fittings & electronic digital read out. | [8 empty] | Nos. | 2 | 89650 | 0 | 89650 | 12551 | 0 | 0 | 0 | 0 | 0 | 102201 | 204402 | 15 | 2 | 26895 | 0 | 26895 | 3765.3 | 0 | 0 | 0 | 0 | 0 | 30660.3
15 | 504030000 | Providing SS 304 the industrial dial type pressure gauges with gun metal valves. | [8 empty] | Nos. | 36 | 701 | 0 | 701 | 35.05 | 0 | 0 | 0 | 0 | 0 | 736.05 | 26498 | 15 | 36 | 3785.4 | 0 | 3785.4 | 189.27 | 0 | 0 | 0 | 0 | 0 | 3974.67
16 | 504030000 | Providing SS 304 the mercury-in- glass industrial dial type thermometers. | [8 empty] | Nos. | 24 | 1443 | 0 | 1443 | 72.15 | 0 | 0 | 0 | 0 | 0 | 1515.15 | 36364 | 15 | 24 | 5194.8 | 0 | 5194.8 | 259.74 | 0 | 0 | 0 | 0 | 0 | 5454.54
17 | 504030000 | Providing the following U-PVC pipes cut to required lengths and installed with all screwed joints, and providing and fixing in position the necessary elbows, tees and reducers as per specifications for AHU / FCU drain. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17.1 | 504030000 | 50 mm dia | [8 empty] | Rmt | 100 | 54 | 0 | 54 | 2.7 | 0 | 0 | 0 | 0 | 0 | 56.7 | 5670 | 15 | 100 | 810 | 0 | 810 | 40.5 | 0 | 0 | 0 | 0 | 0 | 850.5
17.2 | 504030000 | 40 mm dia | [8 empty] | Rmt | 110 | 36 | 0 | 36 | 1.8 | 0 | 0 | 0 | 0 | 0 | 37.8 | 4158 | 15 | 110 | 594 | 0 | 594 | 29.7 | 0 | 0 | 0 | 0 | 0 | 623.7
17.3 | 504030000 | 25 mm dia | [8 empty] | Rmt | 1500 | 20 | 0 | 20 | 1 | 0 | 0 | 0 | 0 | 0 | 21 | 31500 | 15 | 1500 | 4500 | 0 | 4500 | 225 | 0 | 0 | 0 | 0 | 0 | 4725
D. | 504030000 | AIR DISTRIBUTION | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | (FOR FACTORY FABRICATED DUCTS AS PER “SMACNA” STANDARDS & SPECIFICTIONS) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 504030000 | Supply of sheet metal ducts in accordance with the approved shop drawings and as required by the specifications. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | For Ducts with External SP upto 250 Pa (ESP upto 25mmWG) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Maximum Gauge Joint Type Bracing | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | Duct Size Spacing | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1 -500 mm 26 C&S Connector Nil | [8 empty] | sq.m | 3500 | 407 | 0 | 407 | 20.35 | 0 | 0 | 0 | 0 | 0 | 427.35 | 1495725 | 15 | 3500 | 213675 | 0 | 213675 | 10683.75 | 0 | 0 | 0 | 0 | 0 | 224358.75
| 504030000 | 501 -750 mm 26 C&S Connector Nil | [8 empty] | sq.m | 0 | 407 | 0 | 407 | 20.35 | 0 | 0 | 0 | 0 | 0 | 427.35 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 751 - 900 mm 26 TDF Flange Nil | [8 empty] | sq.m | 4000 | 447 | 0 | 447 | 22.35 | 0 | 0 | 0 | 0 | 0 | 469.35 | 1877400 | 15 | 4000 | 268200 | 0 | 268200 | 13410 | 0 | 0 | 0 | 0 | 0 | 281610
| 504030000 | 901 - 1200 mm 24 TDF Flange Nil | [8 empty] | sq.m | 1900 | 521 | 0 | 521 | 26.05 | 0 | 0 | 0 | 0 | 0 | 547.05 | 1039395 | 15 | 1900 | 148485 | 0 | 148485 | 7424.25 | 0 | 0 | 0 | 0 | 0 | 155909.25
| 504030000 | 1201 - 1500 mm 22 TDF Flange Nil | [8 empty] | sq.m | 0 | 614 | 0 | 614 | 30.7 | 0 | 0 | 0 | 0 | 0 | 644.7 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1501 - 1800 mm 22 TDF Flange JTR or ZEE BAR | [8 empty] | sq.m | 1000 | 614 | 0 | 614 | 30.7 | 0 | 0 | 0 | 0 | 0 | 644.7 | 644700 | 15 | 1000 | 92100 | 0 | 92100 | 4605 | 0 | 0 | 0 | 0 | 0 | 96705
| 504030000 | 1801 - 2100 mm 20 TDF Flange JTR or ZEE BAR | [8 empty] | sq.m | 750 | 741 | 0 | 741 | 37.05 | 0 | 0 | 0 | 0 | 0 | 778.05 | 583538 | 15 | 750 | 83362.5 | 0 | 83362.5 | 4168.125 | 0 | 0 | 0 | 0 | 0 | 87530.625
| 504030000 | 2101 - above 18 TDF Flange JTR or ZEE BAR | [8 empty] | sq.m | 1800 | 861 | 0 | 861 | 43.05 | 0 | 0 | 0 | 0 | 0 | 904.05 | 1627290 | 15 | 1800 | 232470 | 0 | 232470 | 11623.5 | 0 | 0 | 0 | 0 | 0 | 244093.5
2 | 504030000 | Kitchen ducting 1.2mm CRCA with Fire paint (Flame bar BW11)(heat resistent painting) and all accessories as per specifications. (with clean outs as per NFPA at base of vertical riser and change in direction and maximum at every 6.0 M in horizontal & every third floor of vertical riser and at sprinkler heads) with weather proof painting for outdoor application | [8 empty] | sq.m | 1750 | 1931 | 0 | 1931 | 96.55 | 0 | 0 | 0 | 0 | 0 | 2027.55 | 3548213 | 15 | 1750 | 506887.5 | 0 | 506887.5 | 25344.375 | 0 | 0 | 0 | 0 | 0 | 532231.875
4 | 504030000 | Supply the flexible connections constructed of fire resistance flexible double canvas sleeve with sandwitched 25 mm thick fibreglass insulation as per the approved shop drawings. | [8 empty] | sq.m | 4 | 6124 | 0 | 6124 | 857.36 | 0 | 0 | 0 | 0 | 0 | 6981.36 | 27925 | 15 | 4 | 3674.4 | 0 | 3674.4 | 514.416 | 0 | 0 | 0 | 0 | 0 | 4188.816
5 | 504030000 | Supply of motorised combined smoke & fire damper (CPRI Approved) complete with control panel, inter connecting wiring at locations shown in approved shop drawings and as per specifications. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.1 | 504030000 | Smoke & Fire Dampers. (Sizes Given Below) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 504030000 | 1800 x 1000 = 2 Sq.m. | [8 empty] | Nos. | 5 | 28286 | 0 | 28286 | 3960.04 | 0 | 0 | 0 | 0 | 0 | 32246.04 | 161230 | 15 | 5 | 21214.5 | 0 | 21214.5 | 2970.03 | 0 | 0 | 0 | 0 | 0 | 24184.53
| 504030000 | 1800 x 600 = 1 Sq.m. | [8 empty] | Nos. | 2 | 15368 | 0 | 15368 | 2151.52 | 0 | 0 | 0 | 0 | 0 | 17519.52 | 35039 | 15 | 2 | 4610.4 | 0 | 4610.4 | 645.456 | 0 | 0 | 0 | 0 | 0 | 5255.856
| 504030000 | 1700 x 400 = 1 Sq.m. | [8 empty] | Nos. | 2 | 12647 | 0 | 12647 | 1770.58 | 0 | 0 | 0 | 0 | 0 | 14417.58 | 28835 | 15 | 2 | 3794.1 | 0 | 3794.1 | 531.174 | 0 | 0 | 0 | 0 | 0 | 4325.274
| 504030000 | 1600 x 450 = 1 Sq.m. | [8 empty] | Nos. | 2 | 12918 | 0 | 12918 | 1808.52 | 0 | 0 | 0 | 0 | 0 | 14726.52 | 29453 | 15 | 2 | 3875.4 | 0 | 3875.4 | 542.556 | 0 | 0 | 0 | 0 | 0 | 4417.956
| 504030000 | 1400 x 500 = 1 Sq.m. | [8 empty] | Nos. | 2 | 12782 | 0 | 12782 | 1789.48 | 0 | 0 | 0 | 0 | 0 | 14571.48 | 29143 | 15 | 2 | 3834.6 | 0 | 3834.6 | 536.844 | 0 | 0 | 0 | 0 | 0 | 4371.444
| 504030000 | 1400 x 450 = 1 Sq.m. | [8 empty] | Nos. | 6 | 12306 | 0 | 12306 | 1722.84 | 0 | 0 | 0 | 0 | 0 | 14028.84 | 84173 | 15 | 6 | 11075.4 | 0 | 11075.4 | 1550.556 | 0 | 0 | 0 | 0 | 0 | 12625.956
| 504030000 | 1300 x 450 = 1 Sq.m. | [8 empty] | Nos. | 2 | 12000 | 0 | 12000 | 1680 | 0 | 0 | 0 | 0 | 0 | 13680 | 27360 | 15 | 2 | 3600 | 0 | 3600 | 504 | 0 | 0 | 0 | 0 | 0 | 4104
| 504030000 | 1250 x 600 = 1 Sq.m. | [8 empty] | Nos. | 2 | 13123 | 0 | 13123 | 1837.22 | 0 | 0 | 0 | 0 | 0 | 14960.22 | 29920 | 15 | 2 | 3936.9 | 0 | 3936.9 | 551.166 | 0 | 0 | 0 | 0 | 0 | 4488.066
| 504030000 | 1250 x 400 = 1 Sq.m. | [8 empty] | Nos. | 2 | 11422 | 0 | 11422 | 1599.08 | 0 | 0 | 0 | 0 | 0 | 13021.08 | 26042 | 15 | 2 | 3426.6 | 0 | 3426.6 | 479.724 | 0 | 0 | 0 | 0 | 0 | 3906.324
| 504030000 | 1200 x 400 = 0.5 Sq.m. | [8 empty] | Nos. | 4 | 11285 | 0 | 11285 | 1579.9 | 0 | 0 | 0 | 0 | 0 | 12864.9 | 51460 | 15 | 4 | 6771 | 0 | 6771 | 947.94 | 0 | 0 | 0 | 0 | 0 | 7718.94
| 504030000 | 1150 x 500 = 1 Sq.m. | [8 empty] | Nos. | 4 | 11932 | 0 | 11932 | 1670.48 | 0 | 0 | 0 | 0 | 0 | 13602.48 | 54410 | 15 | 4 | 7159.2 | 0 | 7159.2 | 1002.288 | 0 | 0 | 0 | 0 | 0 | 8161.488
| 504030000 | 1100 x 450 = 0.5 Sq.m. | [8 empty] | Nos. | 6 | 11388 | 0 | 11388 | 1594.32 | 0 | 0 | 0 | 0 | 0 | 12982.32 | 77894 | 15 | 6 | 10249.2 | 0 | 10249.2 | 1434.888 | 0 | 0 | 0 | 0 | 0 | 11684.088
| 504030000 | 1000 x 350 = 0.5 Sq.m. | [8 empty] | Nos. | 2 | 9550 | 0 | 9550 | 1337 | 0 | 0 | 0 | 0 | 0 | 10887 | 21774 | 15 | 2 | 2865 | 0 | 2865 | 401.1 | 0 | 0 | 0 | 0 | 0 | 3266.1
| 504030000 | 1000 x 400 = 0.5 Sq.m. | [8 empty] | Nos. | 6 | 10741 | 0 | 10741 | 1503.74 | 0 | 0 | 0 | 0 | 0 | 12244.74 | 73468 | 15 | 6 | 9666.9 | 0 | 9666.9 | 1353.366 | 0 | 0 | 0 | 0 | 0 | 11020.266
| 504030000 | 1000 x 500 = 1 Sq.m. | [8 empty] | Nos. | 3 | 11422 | 0 | 11422 | 1599.08 | 0 | 0 | 0 | 0 | 0 | 13021.08 | 39063 | 15 | 3 | 5139.9 | 0 | 5139.9 | 719.586 | 0 | 0 | 0 | 0 | 0 | 5859.486
| 504030000 | 950 x 1350 = 1 Sq.m. | [8 empty] | Nos. | 1 | 24765 | 0 | 24765 | 3467.1 | 0 | 0 | 0 | 0 | 0 | 28232.1 | 28232 | 15 | 1 | 3714.75 | 0 | 3714.75 | 520.065 | 0 | 0 | 0 | 0 | 0 | 4234.815
| 504030000 | 950 x 400 = 0.5 Sq.m. | [8 empty] | Nos. | 5 | 10605 | 0 | 10605 | 1484.7 | 0 | 0 | 0 | 0 | 0 | 12089.7 | 60449 | 15 | 5 | 7953.75 | 0 | 7953.75 | 1113.525 | 0 | 0 | 0 | 0 | 0 | 9067.275
| 504030000 | 950 x 350 = 0.5 Sq.m. | [8 empty] | Nos. | 1 | 9430 | 0 | 9430 | 1320.2 | 0 | 0 | 0 | 0 | 0 | 10750.2 | 10750 | 15 | 1 | 1414.5 | 0 | 1414.5 | 198.03 | 0 | 0 | 0 | 0 | 0 | 1612.53
| 504030000 | 900 x 900 = 1 Sq.m. | [8 empty] | Nos. | 4 | 13532 | 0 | 13532 | 1894.48 | 0 | 0 | 0 | 0 | 0 | 15426.48 | 61706 | 15 | 4 | 8119.2 | 0 | 8119.2 | 1136.688 | 0 | 0 | 0 | 0 | 0 | 9255.888
| 504030000 | 900 x 450 = 0.5 Sq.m. | [8 empty] | Nos. | 1 | 10775 | 0 | 10775 | 1508.5 | 0 | 0 | 0 | 0 | 0 | 12283.5 | 12284 | 15 | 1 | 1616.25 | 0 | 1616.25 | 226.275 | 0 | 0 | 0 | 0 | 0 | 1842.525
| 504030000 | 900 x 350 = 0.5 Sq.m. | [8 empty] | Nos. | 2 | 9311 | 0 | 9311 | 1303.54 | 0 | 0 | 0 | 0 | 0 | 10614.54 | 21229 | 15 | 2 | 2793.3 | 0 | 2793.3 | 391.062 | 0 | 0 | 0 | 0 | 0 | 3184.362
| 504030000 | 850 x 850 = 1 Sq.m. | [8 empty] | Nos. | 1 | 12936 | 0 | 12936 | 1811.04 | 0 | 0 | 0 | 0 | 0 | 14747.04 | 14747 | 15 | 1 | 1940.4 | 0 | 1940.4 | 271.656 | 0 | 0 | 0 | 0 | 0 | 2212.056
| 504030000 | 850 x 650 = 1 Sq.m. | [8 empty] | Nos. | 2 | 11779 | 0 | 11779 | 1649.06 | 0 | 0 | 0 | 0 | 0 | 13428.06 | 26856 | 15 | 2 | 3533.7 | 0 | 3533.7 | 494.718 | 0 | 0 | 0 | 0 | 0 | 4028.418
| 504030000 | 850 x 400 = 0.5 Sq.m. | [8 empty] | Nos. | 2 | 9481 | 0 | 9481 | 1327.34 | 0 | 0 | 0 | 0 | 0 | 10808.34 | 21617 | 15 | 2 | 2844.3 | 0 | 2844.3 | 398.202 | 0 | 0 | 0 | 0 | 0 | 3242.502
| 504030000 | 850 x 300 = 0.5 Sq.m. | [8 empty] | Nos. | 1 | 9073 | 0 | 9073 | 1270.22 | 0 | 0 | 0 | 0 | 0 | 10343.22 | 10343 | 15 | 1 | 1360.95 | 0 | 1360.95 | 190.533 | 0 | 0 | 0 | 0 | 0 | 1551.483
| 504030000 | 850 x 250 = 0.5 Sq.m. | [8 empty] | Nos. | 1 | 8614 | 0 | 8614 | 1205.96 | 0 | 0 | 0 | 0 | 0 | 9819.96 | 9820 | 15 | 1 | 1292.1 | 0 | 1292.1 | 180.894 | 0 | 0 | 0 | 0 | 0 | 1472.994
| 504030000 | 800 x 400 = 0.5 Sq.m. | [8 empty] | Nos. | 6 | 9345 | 0 | 9345 | 1308.3 | 0 | 0 | 0 | 0 | 0 | 10653.3 | 63920 | 15 | 6 | 8410.5 | 0 | 8410.5 | 1177.47 | 0 | 0 | 0 | 0 | 0 | 9587.97
| 504030000 | 800 x 350 = 0.5 Sq.m. | [8 empty] | Nos. | 2 | 9073 | 0 | 9073 | 1270.22 | 0 | 0 | 0 | 0 | 0 | 10343.22 | 20686 | 15 | 2 | 2721.9 | 0 | 2721.9 | 381.066 | 0 | 0 | 0 | 0 | 0 | 3102.966
| 504030000 | 750 x 700 = 1 Sq.m. | [8 empty] | Nos. | 2 | 11591 | 0 | 11591 | 1622.74 | 0 | 0 | 0 | 0 | 0 | 13213.74 | 26427 | 15 | 2 | 3477.3 | 0 | 3477.3 | 486.822 | 0 | 0 | 0 | 0 | 0 | 3964.122
| 504030000 | 750 x 500 = 0.5 Sq.m. | [8 empty] | Nos. | 1 | 10571 | 0 | 10571 | 1479.94 | 0 | 0 | 0 | 0 | 0 | 12050.94 | 12051 | 15 | 1 | 1585.65 | 0 | 1585.65 | 221.991 | 0 | 0 | 0 | 0 | 0 | 1807.641
| 504030000 | 750 x 300 = 0.5 Sq.m. | [8 empty] | Nos. | 2 | 8698 | 0 | 8698 | 1217.72 | 0 | 0 | 0 | 0 | 0 | 9915.72 | 19831 | 15 | 2 | 2609.4 | 0 | 2609.4 | 365.316 | 0 | 0 | 0 | 0 | 0 | 2974.716
| 504030000 | 700 x 500 = 0.5 Sq.m. | [8 empty] | Nos. | 2 | 9550 | 0 | 9550 | 1337 | 0 | 0 | 0 | 0 | 0 | 10887 | 21774 | 15 | 2 | 2865 | 0 | 2865 | 401.1 | 0 | 0 | 0 | 0 | 0 | 3266.1
| 504030000 | 700 x 450 = 0.5 Sq.m. | [8 empty] | Nos. | 2 | 9311 | 0 | 9311 | 1303.54 | 0 | 0 | 0 | 0 | 0 | 10614.54 | 21229 | 15 | 2 | 2793.3 | 0 | 2793.3 | 391.062 | 0 | 0 | 0 | 0 | 0 | 3184.362
| 504030000 | 700 x 400 = 0.5 Sq.m. | [8 empty] | Nos. | 2 | 9073 | 0 | 9073 | 1270.22 | 0 | 0 | 0 | 0 | 0 | 10343.22 | 20686 | 15 | 2 | 2721.9 | 0 | 2721.9 | 381.066 | 0 | 0 | 0 | 0 | 0 | 3102.966
| 504030000 | 650 x 300 = 0.5 Sq.m. | [8 empty] | Nos. | 2 | 8494 | 0 | 8494 | 1189.16 | 0 | 0 | 0 | 0 | 0 | 9683.16 | 19366 | 15 | 2 | 2548.2 | 0 | 2548.2 | 356.748 | 0 | 0 | 0 | 0 | 0 | 2904.948
| 504030000 | 600 x 650 = 0.5 Sq.m. | [8 empty] | Nos. | 2 | 10673 | 0 | 10673 | 1494.22 | 0 | 0 | 0 | 0 | 0 | 12167.22 | 24334 | 15 | 2 | 3201.9 | 0 | 3201.9 | 448.266 | 0 | 0 | 0 | 0 | 0 | 3650.166
| 504030000 | 600 x 400 = 0.5 Sq.m. | [8 empty] | Nos. | 2 | 8801 | 0 | 8801 | 1232.14 | 0 | 0 | 0 | 0 | 0 | 10033.14 | 20066 | 15 | 2 | 2640.3 | 0 | 2640.3 | 369.642 | 0 | 0 | 0 | 0 | 0 | 3009.942
| 504030000 | 600 x 350 = 0.5 Sq.m. | [8 empty] | Nos. | 13 | 8597 | 0 | 8597 | 1203.58 | 0 | 0 | 0 | 0 | 0 | 9800.58 | 127408 | 15 | 13 | 16764.15 | 0 | 16764.15 | 2346.981 | 0 | 0 | 0 | 0 | 0 | 19111.131
| 504030000 | 550 x 400 = 0.5 Sq.m. | [8 empty] | Nos. | 1 | 8665 | 0 | 8665 | 1213.1 | 0 | 0 | 0 | 0 | 0 | 9878.1 | 9878 | 15 | 1 | 1299.75 | 0 | 1299.75 | 181.965 | 0 | 0 | 0 | 0 | 0 | 1481.715
| 504030000 | 500 x 750 = 0.5 Sq.m. | [8 empty] | Nos. | 5 | 10571 | 0 | 10571 | 1479.94 | 0 | 0 | 0 | 0 | 0 | 12050.94 | 60255 | 15 | 5 | 7928.25 | 0 | 7928.25 | 1109.955 | 0 | 0 | 0 | 0 | 0 | 9038.205
| 504030000 | 500 x 400 = 0.5 Sq.m. | [8 empty] | Nos. | 3 | 8529 | 0 | 8529 | 1194.06 | 0 | 0 | 0 | 0 | 0 | 9723.06 | 29169 | 15 | 3 | 3838.05 | 0 | 3838.05 | 537.327 | 0 | 0 | 0 | 0 | 0 | 4375.377
| 504030000 | 500 x 300 = 0.5 Sq.m. | [8 empty] | Nos. | 35 | 8188 | 0 | 8188 | 1146.32 | 0 | 0 | 0 | 0 | 0 | 9334.32 | 326701 | 15 | 35 | 42987 | 0 | 42987 | 6018.18 | 0 | 0 | 0 | 0 | 0 | 49005.18
| 504030000 | 450 x 450 = 0.5 Sq.m. | [8 empty] | Nos. | 2 | 8545 | 0 | 8545 | 1196.3 | 0 | 0 | 0 | 0 | 0 | 9741.3 | 19483 | 15 | 2 | 2563.5 | 0 | 2563.5 | 358.89 | 0 | 0 | 0 | 0 | 0 | 2922.39
| 504030000 | 450 x 400 = 0.5 Sq.m. | [8 empty] | Nos. | 2 | 8392 | 0 | 8392 | 1174.88 | 0 | 0 | 0 | 0 | 0 | 9566.88 | 19134 | 15 | 2 | 2517.6 | 0 | 2517.6 | 352.464 | 0 | 0 | 0 | 0 | 0 | 2870.064
| 504030000 | 450 x 200 = 0.5 Sq.m. | [8 empty] | Nos. | 2 | 7848 | 0 | 7848 | 1098.72 | 0 | 0 | 0 | 0 | 0 | 8946.72 | 17893 | 15 | 2 | 2354.4 | 0 | 2354.4 | 329.616 | 0 | 0 | 0 | 0 | 0 | 2684.016
| 504030000 | 400 x 300 = 0.5 Sq.m. | [8 empty] | Nos. | 28 | 7985 | 0 | 7985 | 1117.9 | 0 | 0 | 0 | 0 | 0 | 9102.9 | 254881 | 15 | 28 | 33537 | 0 | 33537 | 4695.18 | 0 | 0 | 0 | 0 | 0 | 38232.18
| 504030000 | 400 x 250 = 0.5 Sq.m. | [8 empty] | Nos. | 5 | 7848 | 0 | 7848 | 1098.72 | 0 | 0 | 0 | 0 | 0 | 8946.72 | 44734 | 15 | 5 | 5886 | 0 | 5886 | 824.04 | 0 | 0 | 0 | 0 | 0 | 6710.04
| 504030000 | 400 x 200 = 0.5 Sq.m. | [8 empty] | Nos. | 2 | 7848 | 0 | 7848 | 1098.72 | 0 | 0 | 0 | 0 | 0 | 8946.72 | 17893 | 15 | 2 | 2354.4 | 0 | 2354.4 | 329.616 | 0 | 0 | 0 | 0 | 0 | 2684.016
| 504030000 | 350 x 900 = 0.5 Sq.m. | [8 empty] | Nos. | 6 | 10163 | 0 | 10163 | 1422.82 | 0 | 0 | 0 | 0 | 0 | 11585.82 | 69515 | 15 | 6 | 9146.7 | 0 | 9146.7 | 1280.538 | 0 | 0 | 0 | 0 | 0 | 10427.238
| 504030000 | 350 x 200 = 0.5 Sq.m. | [8 empty] | Nos. | 1 | 7848 | 0 | 7848 | 1098.72 | 0 | 0 | 0 | 0 | 0 | 8946.72 | 8947 | 15 | 1 | 1177.2 | 0 | 1177.2 | 164.808 | 0 | 0 | 0 | 0 | 0 | 1342.008
| 504030000 | 300 x 300 = 0.5 Sq.m. | [8 empty] | Nos. | 4 | 7848 | 0 | 7848 | 1098.72 | 0 | 0 | 0 | 0 | 0 | 8946.72 | 35787 | 15 | 4 | 4708.8 | 0 | 4708.8 | 659.232 | 0 | 0 | 0 | 0 | 0 | 5368.032
| 504030000 | 250 x 250 = 0.5 Sq.m. | [8 empty] | Nos. | 2 | 7848 | 0 | 7848 | 1098.72 | 0 | 0 | 0 | 0 | 0 | 8946.72 | 17893 | 15 | 2 | 2354.4 | 0 | 2354.4 | 329.616 | 0 | 0 | 0 | 0 | 0 | 2684.016
| 504030000 | 250 x 200 = 0.5 Sq.m. | [8 empty] | Nos. | 2 | 7848 | 0 | 7848 | 1098.72 | 0 | 0 | 0 | 0 | 0 | 8946.72 | 17893 | 15 | 2 | 2354.4 | 0 | 2354.4 | 329.616 | 0 | 0 | 0 | 0 | 0 | 2684.016
| 504030000 | 200 x 150 = 0.5 Sq.m. | [8 empty] | Nos. | 20 | 7848 | 0 | 7848 | 1098.72 | 0 | 0 | 0 | 0 | 0 | 8946.72 | 178934 | 15 | 20 | 23544 | 0 | 23544 | 3296.16 | 0 | 0 | 0 | 0 | 0 | 26840.16
| 504030000 | 200 x 100 = 0.5 Sq.m. | [8 empty] | Nos. | 47 | 7848 | 0 | 7848 | 1098.72 | 0 | 0 | 0 | 0 | 0 | 8946.72 | 420496 | 15 | 47 | 55328.4 | 0 | 55328.4 | 7745.976 | 0 | 0 | 0 | 0 | 0 | 63074.376
| 504030000 | 100 x 100 = 0.5 Sq.m. | [8 empty] | Nos. | 15 | 7848 | 0 | 7848 | 1098.72 | 0 | 0 | 0 | 0 | 0 | 8946.72 | 134201 | 15 | 15 | 17658 | 0 | 17658 | 2472.12 | 0 | 0 | 0 | 0 | 0 | 20130.12
| 504030000 | Total Qty. | [8 empty] | Sq.M. | 37 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.2 | 504030000 | Actuators (above 1600mm size to be provided with 2 actuators) | [8 empty] | Nos. | 21 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.3 | 504030000 | Control Panel & Wiring (cost for all 6.1 to 6.2) | [8 empty] | Nos. | 21 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.4 | 504030000 | Fire damper with fusible links to be provided in duct collars. | [8 empty] | sq.m | 2 | 7375 | 0 | 7375 | 1032.5 | 0 | 0 | 0 | 0 | 0 | 8407.5 | 16815 | 15 | 2 | 2212.5 | 0 | 2212.5 | 309.75 | 0 | 0 | 0 | 0 | 0 | 2522.25
6 | 504030000 | Supply of powder coated Extruded Aluminium exhaust air Grilles with volume control dampers in accordance with the approved shop drawings and specifications. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6.1 | 504030000 | With adjustable double louvers. | [8 empty] | sq.m | 1 | 7379 | 0 | 7379 | 1033.06 | 0 | 0 | 0 | 0 | 0 | 8412.06 | 8412 | 15 | 1 | 1106.85 | 0 | 1106.85 | 154.959 | 0 | 0 | 0 | 0 | 0 | 1261.809
6.2 | 504030000 | With horizontal fixed bars (For Toilet Exhaust) | [8 empty] | sq.m | 20 | 5969 | 0 | 5969 | 835.66 | 0 | 0 | 0 | 0 | 0 | 6804.66 | 136093 | 15 | 20 | 17907 | 0 | 17907 | 2506.98 | 0 | 0 | 0 | 0 | 0 | 20413.98
7 | 504030000 | Supply of Air Grilles without volume control dampers. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7.1 | 504030000 | With adjustable double louvers powder coated extruded aluminium. | [8 empty] | sq.m | 100 | 4652 | 0 | 4652 | 651.28 | 0 | 0 | 0 | 0 | 0 | 5303.28 | 530328 | 15 | 100 | 69780 | 0 | 69780 | 9769.2 | 0 | 0 | 0 | 0 | 0 | 79549.2
7.2 | 504030000 | With horizontal fixed bars for Guest Room FCU powder coated extruded aluminium (subject to final interior design). | [8 empty] | sq.m | 100 | 3242 | 0 | 3242 | 453.88 | 0 | 0 | 0 | 0 | 0 | 3695.88 | 369588 | 15 | 100 | 48630 | 0 | 48630 | 6808.2 | 0 | 0 | 0 | 0 | 0 | 55438.2
8 | 504030000 | Supply of square shape ceiling diffusers with removable core & anti smudge ring & volume control dampers as per approved drawings and specifications. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8.1 | 504030000 | Powder coated extruded aluminium construction. | [8 empty] | sq.m | 40 | 8312 | 0 | 8312 | 1163.68 | 0 | 0 | 0 | 0 | 0 | 9475.68 | 379027 | 15 | 40 | 49872 | 0 | 49872 | 6982.08 | 0 | 0 | 0 | 0 | 0 | 56854.08
8.2 | 504030000 | Powder coated MS construction.l | [8 empty] | sq.m | 1 | 8312 | 0 | 8312 | 1163.68 | 0 | 0 | 0 | 0 | 0 | 9475.68 | 9476 | 15 | 1 | 1246.8 | 0 | 1246.8 | 174.552 | 0 | 0 | 0 | 0 | 0 | 1421.352
9 | 504030000 | Supply of square shape return air diffusers with removable core, antismudge ring & without volume control damper as per specifications. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.1 | 504030000 | Powder coated extruded aluminiumm construction | [8 empty] | sq.m | 25 | 5584 | 0 | 5584 | 781.76 | 0 | 0 | 0 | 0 | 0 | 6365.76 | 159144 | 15 | 25 | 20940 | 0 | 20940 | 2931.6 | 0 | 0 | 0 | 0 | 0 | 23871.6
9.2 | 504030000 | Powder coated MS construction | [8 empty] | sq.m | 1 | 5584 | 0 | 5584 | 781.76 | 0 | 0 | 0 | 0 | 0 | 6365.76 | 6366 | 15 | 1 | 837.6 | 0 | 837.6 | 117.264 | 0 | 0 | 0 | 0 | 0 | 954.864
10 | 504030000 | Supply of supply air and return air grilles in accordance with the approved shop drawings and specifications for Parking, Mechanical and Back of the house areas. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10.1 | 504030000 | Powder coated MS Grilles with volume control dampers and adjustable louvers. | [8 empty] | sq.m | 45 | 7379 | 0 | 7379 | 1033.06 | 0 | 0 | 0 | 0 | 0 | 8412.06 | 378543 | 15 | 45 | 49808.25 | 0 | 49808.25 | 6973.155 | 0 | 0 | 0 | 0 | 0 | 56781.405
11 | 504030000 | Supply of supply air and return air, square / round shaped diffusers volume damper as per specifications for back of the house areas. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11.1 | 504030000 | Powder coated MS Diffusers with volume control damper for supply air. | [8 empty] | sq.m | 3 | 8312 | 0 | 8312 | 1163.68 | 0 | 0 | 0 | 0 | 0 | 9475.68 | 28427 | 15 | 3 | 3740.4 | 0 | 3740.4 | 523.656 | 0 | 0 | 0 | 0 | 0 | 4264.056
11.2 | 504030000 | Powder coated MS Diffusers without volume control damper for return air. | [8 empty] | sq.m | 5 | 5584 | 0 | 5584 | 781.76 | 0 | 0 | 0 | 0 | 0 | 6365.76 | 31829 | 15 | 5 | 4188 | 0 | 4188 | 586.32 | 0 | 0 | 0 | 0 | 0 | 4774.32
12 | 504030000 | Supply of constant volume damper as per specifications for guest rooms with the air flow capacity mentioned below. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12.1 | 504030000 | 50 cfm | [8 empty] | Nos. | 225 | 1943 | 0 | 1943 | 272.02 | 0 | 0 | 0 | 0 | 0 | 2215.02 | 498380 | 15 | 225 | 65576.25 | 0 | 65576.25 | 9180.675 | 0 | 0 | 0 | 0 | 0 | 74756.925
12.2 | 504030000 | 60 cfm | [8 empty] | Nos. | 225 | 1943 | 0 | 1943 | 272.02 | 0 | 0 | 0 | 0 | 0 | 2215.02 | 498380 | 15 | 225 | 65576.25 | 0 | 65576.25 | 9180.675 | 0 | 0 | 0 | 0 | 0 | 74756.925
13 | 504030000 | Supply of Linear Grilles with removable core and volume control damper as per approved drawings and specifications (subject to final interior design). | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13.1 | 504030000 | Powder coated extruded aluminium construction..n | [8 empty] | sq.m | 5 | 5969 | 0 | 5969 | 835.66 | 0 | 0 | 0 | 0 | 0 | 6804.66 | 34023 | 15 | 5 | 4476.75 | 0 | 4476.75 | 626.745 | 0 | 0 | 0 | 0 | 0 | 5103.495
13.2 | 504030000 | Powder coated MS constructions | [8 empty] | sq.m | 1 | 5969 | 0 | 5969 | 835.66 | 0 | 0 | 0 | 0 | 0 | 6804.66 | 6805 | 15 | 1 | 895.35 | 0 | 895.35 | 125.349 | 0 | 0 | 0 | 0 | 0 | 1020.699
14 | 504030000 | Supply of Powder Coated Extruded Aluminium Linear supply Air Multi Slot Diffuser complete with air pattern controllers & Hit & Miss volume control damper with acoustically line 22 G G.I plenum as per specifications and approved drawings. | [8 empty] | sq.m | 90 | 7456 | 0 | 7456 | 1043.84 | 0 | 0 | 0 | 0 | 0 | 8499.84 | 764986 | 15 | 90 | 100656 | 0 | 100656 | 14091.84 | 0 | 0 | 0 | 0 | 0 | 114747.84
15 | 504030000 | Supply of Powder Coated Extruded Aluminium Multi Slot return Air Diffuser with air pattern controller as per specification and approved drawings. | [8 empty] | sq.m | 135 | 6410 | 0 | 6410 | 897.4 | 0 | 0 | 0 | 0 | 0 | 7307.4 | 986499 | 15 | 135 | 129802.5 | 0 | 129802.5 | 18172.35 | 0 | 0 | 0 | 0 | 0 | 147974.85
16 | 504030000 | Supplying of opposed blade volume control dampers in supply air duct collars as per approved drawings and specifications. Damper shall be with 18G GSS body and blades shall be with aluminium airfoil construction. | [8 empty] | sq.m | 80 | 7700 | 0 | 7700 | 1078 | 0 | 0 | 0 | 0 | 0 | 8778 | 702240 | 15 | 80 | 92400 | 0 | 92400 | 12936 | 0 | 0 | 0 | 0 | 0 | 105336
17 | 504030000 | Supply of inlet air louvers with bird screen and volume damper for fresh air as per specifications and approved shop drawings. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17.1 | 504030000 | Powder coated/Anodised extruded aluminium construction. | [8 empty] | sq.m | 140 | 6628 | 0 | 6628 | 927.92 | 0 | 0 | 0 | 0 | 0 | 7555.92 | 1057829 | 15 | 140 | 139188 | 0 | 139188 | 19486.32 | 0 | 0 | 0 | 0 | 0 | 158674.32
17.2 | 504030000 | Powder coated MS constructionm | [8 empty] | sq.m | 1 | 6628 | 0 | 6628 | 927.92 | 0 | 0 | 0 | 0 | 0 | 7555.92 | 7556 | 15 | 1 | 994.2 | 0 | 994.2 | 139.188 | 0 | 0 | 0 | 0 | 0 | 1133.388
18 | 504030000 | Supply of louvers with bird screen for exhaust air as per specifications and approved drawings. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18.1 | 504030000 | Powder coated/Anodised extruded aluminium constructionn. | [8 empty] | sq.m | 30 | 3900 | 0 | 3900 | 546 | 0 | 0 | 0 | 0 | 0 | 4446 | 133380 | 15 | 30 | 17550 | 0 | 17550 | 2457 | 0 | 0 | 0 | 0 | 0 | 20007
18.2 | 504030000 | Powder coated MS constructionn | [8 empty] | sq.m | 1 | 3900 | 0 | 3900 | 546 | 0 | 0 | 0 | 0 | 0 | 4446 | 4446 | 15 | 1 | 585 | 0 | 585 | 81.9 | 0 | 0 | 0 | 0 | 0 | 666.9
19 | 504030000 | Motorised fresh air dampers with controllers. Damper actuator shall work on 230 V supply (derived from AHU starter panel). Controller shall receive 4-20 mA / 0-10 V control signal from remote BMS system & accordingly modulate fresh air quantity to the AHU. Control shall give feed back signal to remote BMS System. Fresh air dampers shall be modulated based on signal recieved from CO2 sensors. (CO2 sensors shall be by others). | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19.1 | 504030000 | Fresh Air Damper | [8 empty] | sq.m | 5 | 7700 | 0 | 7700 | 1078 | 0 | 0 | 0 | 0 | 0 | 8778 | 43890 | 15 | 5 | 5775 | 0 | 5775 | 808.5 | 0 | 0 | 0 | 0 | 0 | 6583.5
19.2 | 504030000 | Control Panel & Wiringee | [8 empty] | Nos. | 17 | 1803 | 0 | 1803 | 252.42 | 0 | 0 | 0 | 0 | 0 | 2055.42 | 34942 | 15 | 17 | 4597.65 | 0 | 4597.65 | 643.671 | 0 | 0 | 0 | 0 | 0 | 5241.321
19.3 | 504030000 | Actuatorr | [8 empty] | Nos. | 17 | 6541 | 0 | 6541 | 915.74 | 0 | 0 | 0 | 0 | 0 | 7456.74 | 126765 | 15 | 17 | 16679.55 | 0 | 16679.55 | 2335.137 | 0 | 0 | 0 | 0 | 0 | 19014.687
20 | 504030000 | Motorised dampers with controllers for smoke Management in basements. Damper actuator shall work on 230 V supply (derived from fan starter panel). Controller shall receive 4-20 mA / 0-10 V control signal from remote Fire alarm system & accordingly open the dampers for required operation. Control shall give feed back signal to remote BMS System. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20.1 | 504030000 | Dampers | [8 empty] | sq.m | 12 | 7700 | 0 | 7700 | 1078 | 0 | 0 | 0 | 0 | 0 | 8778 | 105336 | 15 | 12 | 13860 | 0 | 13860 | 1940.4 | 0 | 0 | 0 | 0 | 0 | 15800.4
20.2 | 504030000 | Control Panel & Wiring | [8 empty] | Nos. | 10 | 1803 | 0 | 1803 | 252.42 | 0 | 0 | 0 | 0 | 0 | 2055.42 | 20554 | 15 | 10 | 2704.5 | 0 | 2704.5 | 378.63 | 0 | 0 | 0 | 0 | 0 | 3083.13
20.3 | 504030000 | Actuator | [8 empty] | Nos. | 10 | 6541 | 0 | 6541 | 915.74 | 0 | 0 | 0 | 0 | 0 | 7456.74 | 74567 | 15 | 10 | 9811.5 | 0 | 9811.5 | 1373.61 | 0 | 0 | 0 | 0 | 0 | 11185.11
E - 1 | 504030000 | THERMAL INSULATION | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 504030000 | Supplying of 19 mm thick Closed cell nitrile rubber Class O with factory laminated black treated woven glass cloth on chilled water and condensate drain piping and fitting like valves, flanges union, etc. as per the approved shop drawings and specifications. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.1 | 504030000 | 50 mm dia pipes | [8 empty] | RM | 100 | 305 | 0 | 305 | 42.7 | 0 | 0 | 0 | 0 | 0 | 347.7 | 34770 | 15 | 100 | 4575 | 0 | 4575 | 640.5 | 0 | 0 | 0 | 0 | 0 | 5215.5
1.2 | 504030000 | 40 mm dia pipese | [8 empty] | RM | 110 | 271 | 0 | 271 | 37.94 | 0 | 0 | 0 | 0 | 0 | 308.94 | 33983 | 15 | 110 | 4471.5 | 0 | 4471.5 | 626.01 | 0 | 0 | 0 | 0 | 0 | 5097.51
1.3 | 504030000 | 25 mm dia pipes | [8 empty] | RM | 1100 | 233 | 0 | 233 | 32.62 | 0 | 0 | 0 | 0 | 0 | 265.62 | 292182 | 15 | 1100 | 38445 | 0 | 38445 | 5382.3 | 0 | 0 | 0 | 0 | 0 | 43827.3
2 | 504030000 | Supply of External Thermal insulation with protective coating on ducts as per the specifications. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.1 | 504030000 | Insulation with 50mm thick 32 kg/cu.mtr density fiber glass winsulation with factory laminated Alu glass external surface. | [8 empty] | sq.mtr | 11000 | 331 | 0 | 331 | 16.55 | 0 | 0 | 0 | 0 | 0 | 347.55 | 3823050 | 15 | 11000 | 546150 | 0 | 546150 | 27307.5 | 0 | 0 | 0 | 0 | 0 | 573457.5
2.2 | 504030000 | Insulation with 50mm thick 32 kg/cu.mtr density fiber glass insulation with factory laminated Alu glass external surface. | [8 empty] | Sq.mtr | 750 | 331 | 0 | 331 | 16.55 | 0 | 0 | 0 | 0 | 0 | 347.55 | 260663 | 15 | 750 | 37237.5 | 0 | 37237.5 | 1861.875 | 0 | 0 | 0 | 0 | 0 | 39099.375
2.3 | 504030000 | Supply of Fibreglass insulation, 24 kg / m3 density, and Alu Glass lamination face as per specifications for kitchen exhaust ducting. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.3.1 | 504030000 | 50 mm thick | [8 empty] | sq.m | 1750 | 274 | 0 | 274 | 13.7 | 0 | 0 | 0 | 0 | 0 | 287.7 | 503475 | 15 | 1750 | 71925 | 0 | 71925 | 3596.25 | 0 | 0 | 0 | 0 | 0 | 75521.25
3 | 504030000 | Supply of acoustic insulation. Material shall be Class 1 open cell nitrile rubber and all accessories as per specification. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.1 | 504030000 | 15mm thick | [8 empty] | sq.m | 1200 | 1062 | 0 | 1062 | 53.1 | 0 | 0 | 0 | 0 | 0 | 1115.1 | 1338120 | 15 | 1200 | 191160 | 0 | 191160 | 9558 | 0 | 0 | 0 | 0 | 0 | 200718
| 504030000 | All walls and ceiling of the room shall be provided with acoustic lining of resin bonded fiberglass/ mineral wool with minimum density @ 48 Kg / M3 as per Schedule of Quantities. The surface shall be cleaned and frame work of 22 gage GI fabricated Channels 50 mm x 75 mm screwed back to back at 60 cm centres shall be provided vertically and horizontally so that 60 x 60 cm squares are formed. The gaps between frames shall be filled with 75 mm thick about 60 cm x 60 cm cut panels of resin bonded fiberglass /mineral wool slabs. The entire surface shall then be covered with fibreglass tissue and 22 gauge perforated aluminium sheet, 60 cm or 120 cm wide having atleast 15 percent perforations, fixed with sheet metal screws.(Rivets with powder coating) Over-lapping of sheets shall be covered with Aluminium beading. Acoustic lining of walls shall be terminated approximately 15 cm above the finished floor to prevent damage to insulation due to accidental water-logging. A minimum airgap of 25mm shall be provided between the wall and wall insulation material. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 504030000 | 50mm thick | [8 empty] | sq.m | 356 | 712 | 0 | 712 | 35.6 | 0 | 0 | 0 | 0 | 0 | 747.6 | 266146 | 15 | 356 | 38020.8 | 0 | 38020.8 | 1901.04 | 0 | 0 | 0 | 0 | 0 | 39921.84
| 504030000 | [9 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4.1 | 504030000 | 100mm thick | [8 empty] | sq.m | 95 | 1039 | 0 | 1039 | 51.95 | 0 | 0 | 0 | 0 | 0 | 1090.95 | 103640 | 15 | 95 | 14805.75 | 0 | 14805.75 | 740.2875 | 0 | 0 | 0 | 0 | 0 | 15546.0375
5 | 504030000 | Supply of 25 mm thick Closed cell nitrile rubber Class O with factory laminated black treated woven glass cloth on chilled water pipes and fittings like valves, flanges and unions, etc. as per approved shop drawings and specifications. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.1 | 504030000 | 100 mm dia pipesg | [8 empty] | RM | 100 | 778 | 0 | 778 | 108.92 | 0 | 0 | 0 | 0 | 0 | 886.92 | 88692 | 15 | 100 | 11670 | 0 | 11670 | 1633.8 | 0 | 0 | 0 | 0 | 0 | 13303.8
5.2 | 504030000 | 80 mm dia pipes | [8 empty] | RM | 160 | 555 | 0 | 555 | 77.7 | 0 | 0 | 0 | 0 | 0 | 632.7 | 101232 | 15 | 160 | 13320 | 0 | 13320 | 1864.8 | 0 | 0 | 0 | 0 | 0 | 15184.8
5.3 | 504030000 | 65 mm dia pipes | [8 empty] | RM | 290 | 496 | 0 | 496 | 69.44 | 0 | 0 | 0 | 0 | 0 | 565.44 | 163978 | 15 | 290 | 21576 | 0 | 21576 | 3020.64 | 0 | 0 | 0 | 0 | 0 | 24596.64
5.4 | 504030000 | 50 mm dia pipes | [8 empty] | RM | 695 | 448 | 0 | 448 | 62.72 | 0 | 0 | 0 | 0 | 0 | 510.72 | 354950 | 15 | 695 | 46704 | 0 | 46704 | 6538.56 | 0 | 0 | 0 | 0 | 0 | 53242.56
5.5 | 504030000 | 40 mm dia pipes | [8 empty] | RM | 325 | 371 | 0 | 371 | 51.94 | 0 | 0 | 0 | 0 | 0 | 422.94 | 137456 | 15 | 325 | 18086.25 | 0 | 18086.25 | 2532.075 | 0 | 0 | 0 | 0 | 0 | 20618.325
5.6 | 504030000 | 32 mm dia pipes | [8 empty] | RM | 550 | 343 | 0 | 343 | 48.02 | 0 | 0 | 0 | 0 | 0 | 391.02 | 215061 | 15 | 550 | 28297.5 | 0 | 28297.5 | 3961.65 | 0 | 0 | 0 | 0 | 0 | 32259.15
5.7 | 504030000 | 25 mm dia pipes;d | [8 empty] | RM | 2500 | 328 | 0 | 328 | 45.92 | 0 | 0 | 0 | 0 | 0 | 373.92 | 934800 | 15 | 2500 | 123000 | 0 | 123000 | 17220 | 0 | 0 | 0 | 0 | 0 | 140220
6 | 504030000 | Supply of 32 mm thick Closed cell nitrile rubber Class O with factory laminated black treated woven glass cloth on chilled water pipes and fittings like valves, flanges and unions, etc. as per approved shop drawings and specifications. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6.1 | 504030000 | 250 mm dia pipes | [8 empty] | RM | 1 | 1057 | 0 | 1057 | 52.85 | 0 | 0 | 0 | 0 | 0 | 1109.85 | 1110 | 15 | 1 | 158.55 | 0 | 158.55 | 7.9275 | 0 | 0 | 0 | 0 | 0 | 166.4775
6.2 | 504030000 | 200 mm dia pipesl | [8 empty] | RM | 145 | 895 | 0 | 895 | 44.75 | 0 | 0 | 0 | 0 | 0 | 939.75 | 136264 | 15 | 145 | 19466.25 | 0 | 19466.25 | 973.3125 | 0 | 0 | 0 | 0 | 0 | 20439.5625
6.3 | 504030000 | 150 mm dia pipese | [8 empty] | RM | 225 | 733 | 0 | 733 | 36.65 | 0 | 0 | 0 | 0 | 0 | 769.65 | 173171 | 15 | 225 | 24738.75 | 0 | 24738.75 | 1236.9375 | 0 | 0 | 0 | 0 | 0 | 25975.6875
6.4 | 504030000 | 125 mm dia pipes | [8 empty] | RM | 70 | 652 | 0 | 652 | 32.6 | 0 | 0 | 0 | 0 | 0 | 684.6 | 47922 | 15 | 70 | 6846 | 0 | 6846 | 342.3 | 0 | 0 | 0 | 0 | 0 | 7188.3

## COP Facesheet
CHARTERED HOTELS PVT. LTD.
CERTIFICATE OF PAYMENT
COP No.:- |  |  |  |  | Date.:- 13/03/2015
Project Code:- |  | 006 |  |  | Not For Payment
Project:- |  | Proposed Five Star Hotel at Lucknow
Work: | Installation, testing & commisioning of low side HVAC work |  |  | M/s HITACHI HOME & LIFE SOLUTIONS (INDIA) LIMITED.
Budget Code:- |  |  |  | B-43, SECTOR-65, NOIDA, U.P-201301, India
W.O. / P.O. No. & Date:- |  |  | CHPL/ 006/WO/14-15/0576 | PAN No.:- AABCA2392K
Original W.O. Value:- |  |  | 12028725 | UPVAT No.:- 09989100985 CST NO- Service Tax No:-
WO Amendment No.:- |  |  |  | Invoice No. dated
Amended or WO/PO Value:- |  |  | 56562003
Balance Work Yet to be done |  |  | 48077703.333
Sr. No. | Description of Work |  |  | Previous Certified Amount INR | Current Certified Amount INR | Cumulative Certified Amount INR
| Certificate Type:- |  |  |  | I
| Certificate No.:- |  |  |  | COP-R001
A | Work Done Amount
1 | Supply Amount (Basic + Excise) |  |  |  | 7701827.85 | 7701827.85
2 | VAT/CST |  |  |  | 782471.817 | 782471.817
3 | Freight |  |  |  | 0 | 0
4 | Octroi / LBT, Insurance & Packing and Forwarding |  |  |  | 0 | 0
5 | Other Payments |  |  |  | 0 | 0
A | Gross Amount for Work Done As per this Bill |  |  | 0 | 8484299.667 | 8484299.667
B | Recoveries:-
1 | Recovery of Advance (@13.333%) |  |  |  | 0
2 | Recovery of water Charges for Water Consumed |  |  |  | 0
3 | Recovery of Power ( For Electricity Consumed) |  |  |  | 0
4 | Recovery of Monthly Advance ( if any) |  |  |  | 0
5 | Recovery of unsecured Advance( Including Expired Bank Guarantee |  |  |  | 0
6 | Recovery of Insurance Premium |  |  |  | 0
7 | Debit for Non removing of debris |  |  |  | 0
8 | Retention Amount (as per Contract Conditions 5%) |  |  |  | 0
9 | Non Conformity of Concrete |  |  |  | 0
10 | Miscellaneous |  |  |  | 0
B | Total Gross Recoveries:- |  |  | 0 | 0 | 0
C | Other Payments |  |  |  | 0
1 | Mobilisation Advance |  |  |  | 0
2 | Ad-Hoc Certification |  |  |  | 0
3 | Secured Advance |  |  |  | 0
4 | Travel Reimbursement |  |  |  | 0
| Net Amount of Other Payments |  |  |  | 0
| Service Tax ON Other Payments, if any. |  |  |  | 0
C | Gross Amount for Other Payments |  |  | 0 | 0 | 0
| Gross Certified as Per This Bill A-B+C |  |  |  | 8484299.667 | 8484299.667
Rs. (In Words):
Mode of Payment:-
Remarks:-
Prepared By |  | Checked By |  | Approved By | Approved By
QS and Contracts |  | Asst.GM - Contracts |  | GM -Project | GM -Contracts
CHPL
CHPL
CHPL