## Order
Scenario 3
Local Supply
|  | UNIQUE IDENTIFIERS | [8 empty] | UOM | QTY | RATE (can be entered directly or summed up for totals)
Sr. No. | Item Range Code | Description | Area | Make | Model No./ Product Code | Tag/ Item No. | ITC HS Code | Country of Origin | Port of Loading | User defined column |  |  | Local supply rate | [5 empty] | Installation Rate |  |  |  | Amount
[13 empty] | Basic Rate | Excise | Subtotal = Basic + Excise | VAT/CST on Subtotal | Others | Supply Rate Total (sum or direct entry) | Basic Rate | Service Tax | Other | Installation Rate Total (sum or direct entry) | LOCAL SUPPLY AMOUNT | INSTALLATION AMOUNT | TOTAL AMOUNT
A. | 303000000 | CIRCUIT CUM POINT WIRING | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
I | 303000000 | Public & BOH Areas | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 303000000 | Wiring of following light points with 2.5 sq.mm PVC insulated copper conductor 1100 volts grade stranded flexible FRLS wires surface mounted and or embeded in 25mm dia. heavy duty FRLS PVC conduit as per IS 9537 part-3 including providing and fixing of 6 amps single pole rocker operated flush mounted switches of approved quality colour make and design in 1.6 mm thick GI box and earthing of fixture and the outlet box with 2.5 Sq.mm PVC insulated copper conductor stranded flexible FRLS wire. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.1 | 303000000 | MCB controlled Primary point (from DB to switch board - cost of switch & board NOT included) | [8 empty] | Pt | 130 | 1779.785 | 0 | 1779.785 | 133.5373 | 0 | 1913.3223 | 472.64 | 58.4183 | 0 | 531.0583 | 248731.8949 | 69037.5795 | 317769
1.2 | 303000000 | Secondary point with switch ( from switch board to first point - cost of switch & board included) | [8 empty] | Pt | 215 | 629.835 | 0 | 629.835 | 47.2565 | 0 | 677.0915 | 125.545 | 15.5174 | 0 | 141.0624 | 145574.6768 | 30328.4078 | 175903
1.3 | 303000000 | Secondary point without switch ( from light point to light point - cost of switch & board NOT included) | [8 empty] | Pt | 320 | 475.805 | 0 | 475.805 | 35.6996 | 0 | 511.5046 | 176.185 | 21.7765 | 0 | 197.9615 | 163681.4877 | 63347.6691 | 227029
1.4 | 303000000 | Primary point without switch (from switch board to switch board looping- cost of switch & board NOT included) | [8 empty] | Pt | 40 | 1423.195 | 0 | 1423.195 | 106.7823 | 0 | 1529.9773 | 377.69 | 46.6825 | 0 | 424.3725 | 61199.0928 | 16974.8994 | 78174
2 | 303000000 | Wiring for the twin control light points with 2.5 sq.mm PVC insulated copper conductor 1100 volts grade stranded flexible FRLS wires surface mounted and or embeded in 25mm dia. heavy duty FRLS PVC conduit as per IS 9537 part-3 including providing and fixing 2 Nos.6 amps 2 way rocker operated flush mounted switches of approved quality colour make and design in 1.6 mm thick GI box and earthing of fixture and the outlet box with 2.5 Sq.mm PVC insulated copper conductor stranded flexible FRLS wire. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.1 | 303000000 | MCB controlled Primary point (from DB to switch board - cost of switch & board NOT included) | [8 empty] | Pt | 5 | 2372.695 | 0 | 2372.695 | 178.0233 | 0 | 2550.7183 | 629.835 | 77.8476 | 0 | 707.6826 | 12753.5915 | 3538.413 | 16292
2.2 | 303000000 | six point controlled by 2 Nos. two way switches. | [8 empty] | set | 5 | 4207.34 | 0 | 4207.34 | 315.6767 | 0 | 4523.0167 | 1065.55 | 131.702 | 0 | 1197.252 | 22615.0836 | 5986.2599 | 28601
2.3 | 303000000 | Eight points controlled by 2 Nos two way switches. | [8 empty] | set | 5 | 4907.86 | 0 | 4907.86 | 368.2367 | 0 | 5276.0967 | 1232.24 | 152.3049 | 0 | 1384.5449 | 26380.4837 | 6922.7243 | 33303
3 | 303000000 | Wiring for following 250 volt single phase and neutral 6 amps switch socket outlet with 2.5 sq.mm PVC insulated copper conductor 1100 volts grade stranded flexible FRLS wires in surface mounted and or embeded in 25mm dia. heavy duty FRLS PVC conduit as per IS 9537 part-3, including providing and fixing of 6 amps switch and 6A 3 pin socket of approved make colour and design in 1.6 mm thick GI box with grid plate and earthing of third pin of the socket outlet and the GI box with 2.5 Sq.mm PVC insulated copper conductor stranded flexible FRLS wire. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.1 | 303000000 | 2 nos. switched socket outlet connected on one circuit. | [8 empty] | set | 5 | 1900 | 0 | 1900 | 142.557 | 0 | 2042.557 | 554.93 | 68.5893 | 0 | 623.5193 | 10212.785 | 3117.5967 | 13330
3.2 | 303000000 | 4 nos. switched socket outlet connected on one circuit. | [8 empty] | set | 5 | 1900 | 0 | 1900 | 142.557 | 0 | 2042.557 | 567.59 | 70.1541 | 0 | 637.7441 | 10212.785 | 3188.7206 | 13402
4 | 303000000 | Wiring for 250 volts single phase and neutral 6/16 amps switch and socket outlet with 4 sq.mm PVC insulated copper conductor 1100 volts grade stranded flexible FRLS wires in surface mounted or embeded in 25mm dia. heavy duty FRLS PVC conduit as per IS 9537 part-3 , including providing and fixing of 16 amps switch and 5 pin socket of approved make and design in 1.6 mm thick GI boxes with grid plates and earthing the third pin of socket outlet with 4 Sq. mm PVC insulated copper conductor stranded flexible FRLS wire. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4.1 | 303000000 | 1 nos. switched socket outlet connected on one circuit. | [8 empty] | Pts. | 12 | 1068.715 | 0 | 1068.715 | 80.1857 | 0 | 1148.9007 | 334.435 | 41.3362 | 0 | 375.7712 | 13786.8082 | 4509.254 | 18296
4.2 | 303000000 | 2 nos. switched socket outlet connected on one circuit. | [8 empty] | sets | 115 | 1306.09 | 0 | 1306.09 | 97.9959 | 0 | 1404.0859 | 396.68 | 49.0296 | 0 | 445.7096 | 161469.8823 | 51256.6095 | 212726
4.3 | 303000000 | 3 nos. switched socket outlet connected on one circuit. | [8 empty] | sets | 55 | 1661.625 | 0 | 1661.625 | 124.6717 | 0 | 1786.2967 | 491.63 | 60.7655 | 0 | 552.3955 | 98246.3198 | 30381.7507 | 128628
4.4 | 303000000 | 4 nos. switched socket outlet connected on one circuit. | [8 empty] | sets | 8 | 2217.61 | 0 | 2217.61 | 166.3873 | 0 | 2383.9973 | 680.475 | 84.1067 | 0 | 764.5817 | 19071.9782 | 6116.6537 | 25189
5 | 303000000 | Wiring for following 250 volt single phase and neutral with 2 nos 6/16 amps 5 pin socket outlet controlled by 1 nos 16 Amps switch for work stations with 4 sq.mm PVC insulated copper conductor 1100 volts grade stranded flexible FRLS wires in surface mounted or embeded 25mm dia. heavy duty FRLS PVC conduit as per IS 9537 part-3, including providing and fixing of 2 nos. 6/16A 5 pin sockets and one 16 amps switch of approved make colour and design in 1.6 mm thick GI box with grid plate and earthing of third pin of the socket outlet and the GI box with 4 Sq.mm PVC insulated copper conductor stranded flexible FRLS wire. (Max of 4 sets of item as described shall be connected on one circuit.) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.1 | 303000000 | Primary point. | [8 empty] | Sets | 115 | 1306.09 | 0 | 1306.09 | 97.9959 | 0 | 1404.0859 | 396.68 | 49.0296 | 0 | 445.7096 | 161469.8823 | 51256.6095 | 212726
5.2 | 303000000 | Same as Item No. 5 above but secondary point. | [8 empty] | Sets | 130 | 475.805 | 0 | 475.805 | 35.6996 | 0 | 511.5046 | 176.185 | 21.7765 | 0 | 197.9615 | 66495.6044 | 25734.9906 | 92231
6 | 303000000 | Wiring for following dimmer/MCB controlled point with 2.5 sq.mm PVC insulated copper conductor 1100 volts grade stranded flexible FRLS wires in surface mounted and or embeded in 25mm dia. heavy duty FRLS PVC conduit as per IS 9537 part-3 s, including fixing electronic dimmer of approved mak in 1.6 mm thick GI box and earthing of outlet box and lighting fixture with 2.5 sq. mm. PVC insulated copper conductor stranded flexible FRLS wire (Dimmer/MCB not included). | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6.1 | 303000000 | MCB controlled Primary point (from MCB to first light point) | [8 empty] | Pt | 450 | 1899 | 0 | 1899 | 142.482 | 0 | 2041.482 | 504.29 | 62.3302 | 0 | 566.6202 | 918666.8865 | 254979.1098 | 1173646
6.2 | 303000000 | MCB controlled Secondary point (from point to point of same circuit) | [8 empty] | Pt | 1595 | 474.75 | 0 | 474.75 | 35.6205 | 0 | 510.3705 | 125.545 | 15.5174 | 0 | 141.0624 | 814040.9355 | 224994.4674 | 1039035
7 | 303000000 | Wiring for 250 volts single phase and neutral 16 amps polycarbonate splash proof (IP-65) 3 pin industrial socket outlet with 16 amps interlocked rotary switch in polycarbonate enclosure of approved size and design with 4 sq.mm PVC insulated copper conductor 1100 volts grade stranded flexible FRLS wires in surface mounted or embeded 25mm dia. heavy duty FRLS PVC conduit as per IS 9537 part-3 s, including providing and fixing of 3 pin industrial socket and earthing of third pin of the socket outlet with 4 Sq. mm PVC insulated copper conductor stranded flexible FRLS wire. | [8 empty] | Pts. | 245 | 4703.19 | 0 | 4703.19 | 352.8803 | 0 | 5056.0703 | 354.48 | 43.8137 | 0 | 398.2937 | 1238737.2347 | 97581.9634 | 1336319
8 | 303000000 | Wiring for 250 volts single phase and neutral 32 amps polycarbonate splash proof (IP-65) 3 pin industrial socket outlet with 32 amps interlocked rotary switch in polycarbonate enclosure of approved size and design with 6 sq. mm PVC insulated copper conductor 1100 volts grade stranded flexible FRLS wires in embeded or surface mounted 25 mm dia heavy duty FRLS PVC conduit, including providing and fixing of 3 pin industrial socket and earthing of third pin of the socket and outlet with 6 sq. mm PVC insulated copper conductor stranded flexible FRLS wire. | [8 empty] | Pts. | 5 | 7094.875 | 0 | 7094.875 | 532.3285 | 0 | 7627.2035 | 428.33 | 52.9416 | 0 | 481.2716 | 38136.0174 | 2406.3579 | 40542
9 | 303000000 | Wiring for 415 volts three phase and neutral 16 amps polycarbonate splash proof (IP-65) industrial socket outlet with 16 amps interlocked rotary switch in polycarbonate enclosure of approved size and design with 4 x 4 sq.mm PVC insulated copper conductor 1100 volts grade stranded flexible FRLS wires in 25mm dia. 2mm thick embeded or surface mounted PVC conduit including providing and fixing of 5 pin industrial socket and earthing of earth pin of the socket outlet with 4 Sq. mm PVC insulated copper conductor stranded flexible FRLS wire. | [8 empty] | Pts. | 50 | 6517.79 | 0 | 6517.79 | 489.0298 | 0 | 7006.8198 | 404.065 | 49.9424 | 0 | 454.0074 | 350340.9892 | 22700.3717 | 373041
10 | 303000000 | Wiring for 415 volts three phase and neutral 32 amps polycarbonate splash proof (IP-65/66) industrial socket outlet with 32 amps interlocked rotary switch in polycarbonate enclosure of approved size and design with 4 x 6 sq.mm PVC insulated copper conductor 1100 volts grade stranded flexible FRLS wires in 25mm dia. 2mm thick embeded or surface mounted PVC conduit, including earthing of earth pin of the socket with 6 sq mm PVC insulated copper conductor stranded flexible FRLS wires. | [8 empty] | Pts. | 15 | 8811.36 | 0 | 8811.36 | 661.1163 | 0 | 9472.4763 | 559.15 | 69.1109 | 0 | 628.2609 | 142087.1451 | 9423.9141 | 151511
11 | 303000000 | Wiring for Exhaust fan point with 2.5 sq. mm. Insulated copper conductor 1100 volts grade stranded flexible FRLS wires of approved make in 25mm dia. 2mm thick embeded or surface mounted PVC conduit including providing and fixing of 6 amps flush mounted switch at the normal switch level in 2 mm thick GI box and 6 amps 3 pin flush mounted socket outlet near exhaust fan and earthing of exhaust fan through the third pin of the socket outlet and GI box with 2.5 sq. mm. PVC insulated copper conductor strande flexible FRLS wire. (As per HVAC boq) | [8 empty] | Pts. | 15 | 1410.535 | 0 | 1410.535 | 105.8324 | 0 | 1516.3674 | 385.075 | 47.5953 | 0 | 432.6703 | 22745.5116 | 6490.054 | 29236
12 | 303000000 | Wiring for fan coil unit with 2.5 sq. mm. PVC insulated Copper conductor 1100 volts grade stranded flexible FRLS wires of approved make in embeded or surface mounted 25mm dia. heavy duty FRLS PVC conduit as per IS 9537 part-3 and terminating the wire into the HVAC control box (control box and wiring shall be in scope of HVAC contractor) including conduiting (length of conduit approx. 3 – 5 metre) from fan coil unit to thermostat including 2 mm thick GI box, providing and fixing of 6A switch socket, earthing of GI box with 2.5 sq. mm. PVC insulated copper conductor stranded flexible FRLS wires. | [8 empty] | Pts. | 38 | 1195.315 | 0 | 1195.315 | 89.6845 | 0 | 1284.9995 | 302.785 | 37.4242 | 0 | 340.2092 | 48829.9804 | 12927.9506 | 61758
13 | 303000000 | Wiring for DB controlled Chandelier point with 4 sq. mm. PVC insulated copper conductor 1100 volts grade stranded flexible FRLS wires of approved make in embeded or surface mounted 25mm dia. heavy duty FRLS PVC conduit as per IS 9537 part-3 including providing of fixing hook for down rod etc. and earthing with 4 sq. mm. PVC insulated copper conductor stranded flexible FRLS wire. | [8 empty] | Nos. | 15 | 9055.065 | 0 | 9055.065 | 679.4015 | 0 | 9734.4665 | 953.72 | 117.8798 | 0 | 1071.5998 | 146016.9979 | 16073.9969 | 162091
14 | 303000000 | Supply, installation, testing and commissioning of 415 volts 3 phase and neutral 16 amps polycarbonate splash proof (IP-55) industrial socket outlets with 16 amps interlocked rotary switch in weather proof polycarbonate enclosure of approved size and design. (Near swimming pool) | [8 empty] | Pts. | 2 | 5068.22 | 0 | 5068.22 | 380.2685 | 0 | 5448.4885 | 126.6 | 15.6478 | 0 | 142.2478 | 10896.9771 | 284.4955 | 11181
15 | 303000000 | Wiring for 250 volts single phase and neutral 16 amps recessed in floor polycarbonate socket outlet wiring with 4 sq.mm PVC insulated copper conductor 1100 volts grade stranded flexible FRLS wire in embeded or surface mounted 25mm dia. heavy duty FRLS PVC conduit as per IS 9537 part-3, including providing and fixing of 16 amps 3 Pin socket of approved make and design polycarbonate water tight box (IP-65) for kitchen area including providing and fixing socket and earthing of third pin of the socket outlet with 4 sq.mm PVC insulated copper conductor stranded flexible FRLS wire. | [8 empty] | Pts. | 5 | 5803.555 | 0 | 5803.555 | 435.4407 | 0 | 6238.9957 | 777.535 | 96.1033 | 0 | 873.6383 | 31194.9787 | 4368.1916 | 35563
16 | 303000000 | Wiring for guest room shafts lighting with 2.5 sq.mm PVC insulated copper conductor 1100 volts grade stranded flexible FRLS wire in 25 mm dia 2 mm thich heavy duty FRLS PVC conduit embeded or surface mounted as asked for controlled by 1 no. 6 amps switch located in the each shaft. | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16.1 | 303000000 | 12 points on one circuit | [8 empty] | Set | 13 | 5852.085 | 0 | 5852.085 | 439.0819 | 0 | 6291.1669 | 1562.455 | 193.1194 | 0 | 1755.5744 | 81785.1702 | 22822.4677 | 104608
II | 303000000 | LIFT SHAFTS | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 303000000 | Wiring for 250 volts single phase and neutral 16 amps switched socket outlet for lift shafts ONE AT EACH FLOOR LEVEL with 4 sq.mm PVC insulated copper conductor 1100 volts grade stranded flexible FRLS wires in surface mounted 25 mm dia 16 gauge GI conduit including providing and fixing of 16 amps 3 pin switched socket of approved make and design in 2 mm thick GI boxes with grid plates and earthing of third pin of socket outlet and GI box with 4 sq.mm PVC insulated copper conductor stranded flexible FRLS wire. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.1 | 303000000 | 9 points on one circuit | [8 empty] | Set | 4 | 9156.345 | 0 | 9156.345 | 687.0006 | 0 | 9843.3456 | 1789.28 | 221.155 | 0 | 2010.435 | 39373.3823 | 8041.74 | 47415
1.2 | 303000000 | 8 points on one circuit | [8 empty] | Set | 4 | 8223.725 | 0 | 8223.725 | 617.0261 | 0 | 8840.7511 | 1608.875 | 198.8569 | 0 | 1807.7319 | 35363.0043 | 7230.9278 | 42594
1.3 | 303000000 | 5 points on one circuit | [8 empty] | Set | 2 | 5421.645 | 0 | 5421.645 | 406.786 | 0 | 5828.431 | 1066.605 | 131.8324 | 0 | 1198.4374 | 11656.862 | 2396.8748 | 14054
2 | 303000000 | Installation & wiring of 230 V bulk head lamp with on/off switch for Lift shafts ONE AT EACH FLOOR LEVEL with 2.5 sq.mm PVC insulated copper conductor 1100V grade stranded flexible FRLS wires in 25 mm dia 16 guage GI surface mounted conduits including providing and fixing of 6A switch AT EACH FLOOR LEVEL with 2.5 sq.mm. PVC insulated copper conductor stranded flexible earth wire. (Supply of fixture considered elsewere in the Boq) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.1 | 303000000 | 9 points on one circuit | [8 empty] | Set | 4 | 7259.455 | 0 | 7259.455 | 544.6769 | 0 | 7804.1319 | 2643.83 | 326.7774 | 0 | 2970.6074 | 31216.5276 | 11882.4296 | 43099
2.2 | 303000000 | 8 points on one circuit | [8 empty] | Set | 4 | 6531.505 | 0 | 6531.505 | 490.0588 | 0 | 7021.5638 | 2368.475 | 292.7435 | 0 | 2661.2185 | 28086.2553 | 10644.874 | 38731
2.3 | 303000000 | 5 points on one circuit | [8 empty] | Set | 2 | 4348.71 | 0 | 4348.71 | 326.2837 | 0 | 4674.9937 | 1541.355 | 190.5115 | 0 | 1731.8665 | 9349.9874 | 3463.733 | 12814
A II | 303000000 | Guest Rooms | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | CIRCUIT CUM POINT WIRING (WITH HARD WIRED LIGHTING CONTROL) Note: switch and socket shall be client supplied item except for item no A.II. 5 | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 303000000 | Wiring for the following light points including wiring from energy saver to switch board, with 1.5 sq.mm PVC insulated copper conductor 1100 volts grade stranded flexible FRLS wires of approved make in embeded or surface mounted 25mm dia. heavy duty FRLS PVC conduit as per IS 9537 part-3 including fixing of 6 amps single pole rocker operted flush mounted switch of approved quality, colour, make & design in 1.6 mm thick GI box and earthing of fixtures and the outlet box with 1.5 sq.mm PVC insulated copper conductor stranded flexible FRLS wire. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.1 | 303000000 | Two point (Down light at vanity) , 1 nos JB for Magnifier glass & 1 nos JB for Heater Pad controlled by one 6 amps switch | [8 empty] | set | 200 | 400.9 | 0 | 400.9 | 30.0795 | 0 | 430.9795 | 176.185 | 21.7765 | 0 | 197.9615 | 86195.9054 | 39592.2932 | 125788
1.2 | 303000000 | Two points (Down light in toilet), 2 nos JB for FTL lights controlled by one 6 amps switch | [8 empty] | set | 200 | 400.9 | 0 | 400.9 | 30.0795 | 0 | 430.9795 | 176.185 | 21.7765 | 0 | 197.9615 | 86195.9054 | 39592.2932 | 125788
1.3 | 303000000 | One no reading light controlled by Electronic Dimmer switch suitable for 5 W led Adjustable down light. | [8 empty] | Pts | 400 | 500.07 | 0 | 500.07 | 37.5203 | 0 | 537.5903 | 207.835 | 25.6884 | 0 | 233.5234 | 215036.1008 | 93409.3624 | 308445
1.4 | 303000000 | one points controlled by one 6 amps switch (Bed side light) | [8 empty] | Pts | 400 | 400.9 | 0 | 400.9 | 30.0795 | 0 | 430.9795 | 176.185 | 21.7765 | 0 | 197.9615 | 172391.8108 | 79184.5864 | 251576
2 | 303000000 | Wiring for the twin control light points with 1.5 sq.mm PVC insulated copper conductor 1100 volts grade stranded flexible FRLS wires in embeded or surface mounted 25mm dia. heavy duty FRLS PVC conduit as per IS 9537 part-3 . Light point shall be controlled by 2 nos. 6 amps 2 way rocker operated flush mounted switch of approved quality, colour, make & design in 1.6 mm thick GI box and earthing of fixture and the outlet box with 1.5 Sq.mm PVC insulated copper conductor stranded flexible FRLS wire. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.1 | 303000000 | Five point controlled by 2 Nos. 6 amp switch | [8 empty] | set. | 200 | 1041.285 | 0 | 1041.285 | 78.1276 | 0 | 1119.4126 | 351.315 | 43.4225 | 0 | 394.7375 | 223882.5227 | 78947.5068 | 302830
2.2 | 303000000 | Six point controlled by 2 Nos. 6 amp switch | [8 empty] | set. | 0 | 2255.59 | 0 | 2255.59 | 169.2369 | 0 | 2424.8269 | 648.825 | 80.1948 | 0 | 729.0198 | 0 | 0 | 0
2.3 | 303000000 | Three point controlled by 2 nos. 6 amp switch | [8 empty] | set. | 200 | 899.915 | 0 | 899.915 | 67.5206 | 0 | 967.4356 | 334.435 | 41.3362 | 0 | 375.7712 | 193487.1245 | 75154.2332 | 268641
3 | 303000000 | Wiring for 250 volt single phase and neutral 6 amps switch socket outlet with 1.5 sq.mm PVC insulated copper conductor 1100 volts grade stranded flexible FRLS wires in surface mounted and or embeded 25mm dia. heavy duty FRLS PVC conduit as per IS 9537 part-3, including fixing of approved make and design in 1.6 mm thick GI box and fixing of 6 amps switch socket outlet with cover plate and earthing of third pin of the socket outlet and the GI box with 1.5 Sq.mm PVC insulated copper conductor stranded flexible FRLS wire. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.1 | 303000000 | 1 nos switch socket outlet | [8 empty] | Nos | 200 | 500.07 | 0 | 500.07 | 37.5203 | 0 | 537.5903 | 207.835 | 25.6884 | 0 | 233.5234 | 107518.0504 | 46704.6812 | 154223
3.2 | 303000000 | 2 nos switch socket outlet | [8 empty] | Set | 400 | 699.465 | 0 | 699.465 | 52.4809 | 0 | 751.9459 | 271.135 | 33.5123 | 0 | 304.6473 | 300778.3436 | 121858.9144 | 422637
3.3 | 303000000 | 3 nos switch socket outlet | [8 empty] | Set | 200 | 899.915 | 0 | 899.915 | 67.5206 | 0 | 967.4356 | 334.435 | 41.3362 | 0 | 375.7712 | 193487.1245 | 75154.2332 | 268641
3.4 | 303000000 | 4 nos switch socket outlet | [8 empty] | Set | 0 | 1397.875 | 0 | 1397.875 | 104.8826 | 0 | 1502.7576 | 491.63 | 60.7655 | 0 | 552.3955 | 0 | 0 | 0
4 | 303000000 | Wiring for 250 volts single phase and neutral 6/16 amps switched socket outlet with 4 sq.mm PVC insulated copper conductor 1100 volts grade stranded flexible FRLS wires in surface mounted and or embeded 25mm dia. heavy duty FRLS PVC conduit as per IS 9537 part-3, including fixing in 1.6 mm thick GI boxes nd earthing the third pin of socket outlet with 4 Sq. mm PVC insulated copper conductor standard flexible FRLS wire | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4.1 | 303000000 | 1 nos switch socket outlet | [8 empty] | Nos | 200 | 877.76 | 0 | 877.76 | 65.8583 | 0 | 943.6183 | 227.88 | 28.166 | 0 | 256.046 | 188723.6666 | 51209.1936 | 239933
4.2 | 303000000 | 2 nos switch socket outlet | [8 empty] | Set | 400 | 1002.25 | 0 | 1002.25 | 75.1988 | 0 | 1077.4488 | 260.585 | 32.2083 | 0 | 292.7933 | 430979.527 | 117117.3224 | 548097
5 | 303000000 | Wiring for fan coil unit including providing & fixing of 2 nos 250 volts single phase and neutral 6 amps switched socket outlet with 1.5 sq. mm. PVC insulated Copper conductor 1100 volts grade stranded flexible FRLS wires of approved make in 25mm dia. 2mm thick embeded and or surface mounted heavy duty FRLS PVC conduit and terminating the wire into the HVAC control box, (box to be provided by HVAC contractor free of cost) including the control wiring with 10 nos 1 sqmm PVC insulated Copper conductor 1100 volts grade stranded flexible FRLS wires from thermostat to FCU control box and wiring from Keytag holder to Energy saver unit above vestibult. | [8 empty] | set | 200 | 299.62 | 0 | 299.62 | 22.4805 | 0 | 322.1005 | 94.95 | 11.7358 | 0 | 106.6858 | 64420.0977 | 21337.164 | 85757
6 | 303000000 | Wiring for light point for the ward robe with 1.5 sq.mm PVC insulated copper conductor 1100 volts grade stranded flexible FRLS Wires of approved make in embeded and or surface mounted 25mm dia. heavy duty FRLS PVC conduit as per IS 9537 part-3 including providing and fixing of 6 amps SP Micro switch | [8 empty] | Pts | 200 | 299.62 | 0 | 299.62 | 22.4805 | 0 | 322.1005 | 94.95 | 11.7358 | 0 | 106.6858 | 64420.0977 | 21337.164 | 85757
7 | 303000000 | Receiving, storing, handling, fixing and connecting of energy saving unit for each Guest Room including embeded 25mm dia. heavy duty FRLS PVC conduit as per IS 9537 part-3 and wiring from energy saving unit to Key tag and earthing of box with 4 sq.mm PVC insulated copper conductor standed flexible FRLS wire. ( Unit will be supplied by the owner free of cost) | [8 empty] | Nos. | 200 | 450.485 | 0 | 450.485 | 33.7999 | 0 | 484.2849 | 147.7 | 18.2557 | 0 | 165.9557 | 96856.9779 | 33191.144 | 130048
8 | 303000000 | Wiring for shaver unit with 2.5 sq. mm. PVC insulated copper conductor 1100 volts grade stranded flexible FRLS Wire of approved make in embeded 25mm dia. heavy duty FRLS PVC conduit as per IS 9537 part-3 including fixing of 1.6 MM thick GI box and fixing of shaver socket outlet with grid plate. Outlet box shall be earthed by 2.5 sq. mm. PVC insulated copper conductor stranded flexible FRLS wire. | [8 empty] | Nos. | 200 | 356.59 | 0 | 356.59 | 26.7549 | 0 | 383.3449 | 145.59 | 17.9949 | 0 | 163.5849 | 76668.9895 | 32716.9848 | 109386
9 | 303000000 | Wiring for bell points with 1.5 sq. mm. PVC insulated copper conductor 1100 volts grade stranded flexible FRLS Wires in embeded and or surface mounted 25mm dia. heavy duty FRLS PVC conduit as per IS 9537 part-3 including fixing of electronic call bell and earthing of GI box with 1.5 sq mm PVC insulated copper conductor stranded flexible FRLS Wire. including receiving, storing, handling, installation, testing and commissioning of call bell | [8 empty] | Pts | 200 | 400.9 | 0 | 400.9 | 30.0795 | 0 | 430.9795 | 176.185 | 21.7765 | 0 | 197.9615 | 86195.9054 | 39592.2932 | 125788
10 | 303000000 | Wiring for 250 volts single phase and neutral 16 amps switched socket outlet for hair dryer with 4 sq.mm PVC insulated copper conductor 1100 volts grade stranded flexible FRLS wires in surface mounted and or embeded 25mm dia. heavy duty FRLS PVC conduit as per IS 9537 part-3 including fixing of 1.6 mm thick GI box and fixing of 16 amps switch socket outlet with grid plate and earthing the third pin of socket outlet and GI box with 4 sq.mm PVC insulated copper conductor stranded flexible FRLS wire. | [8 empty] | Pts. | 200 | 450.485 | 0 | 450.485 | 33.7999 | 0 | 484.2849 | 147.7 | 18.2557 | 0 | 165.9557 | 96856.9779 | 33191.144 | 130048
11 | 303000000 | Wiring for Do not disturb cum bell points with 1.5 sqmm PVC insulated copper conductor 1100 volts grade stranded flexible FRLS wires in surface mounted and or embeded 25mm dia. heavy duty FRLS PVC conduit as per IS 9537 part-3 and fixing of electronic call bell, bell will not operate when the DND switch is ON, neon indicating lamps on the plate of bell push button, two way switch with LED indicator on the suitable location and earthing of GI box with 1.5 sqmm PVC insulated copper conductor stranded flexible FRLS wire. | [8 empty] | Pts. | 200 | 600.295 | 0 | 600.295 | 45.0401 | 0 | 645.3351 | 239.485 | 29.6003 | 0 | 269.0853 | 129067.0268 | 53817.0692 | 182884
12 | 303000000 | Wiring for forward and Reverse operation of Motorised Curtain point & centre off switch for forward and reverse operation of motor with 1.5 sq.mm PVC insulated copper conductor 1100 volts grade stranded flexible FRLS wire in 25mm dia. 2mm thick embeded or surface mounted PVC conduit in 1.6 mm thick GI box and earthing of GI box with 1.5 Sqmm PVC insulated copper conductor stranded flexible ZHFR wire. | [8 empty] | Pts. | 200 | 798.635 | 0 | 798.635 | 59.9216 | 0 | 858.5566 | 302.785 | 37.4242 | 0 | 340.2092 | 171711.3168 | 68041.8452 | 239753
13 | 303000000 | Supply and fixing of surface mounted/embeded FRLS heavy duty PVC conduit in following sizes including cost of junction boxes, bends, elbows, sockets, tees etc. laying in slab cutting chasis and making good including all fixing hardware ( Ceiling conduits in corridor) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
13.1 | 303000000 | a 25 mm dia | [8 empty] | RM | 2500 | 40.09 | 0 | 40.09 | 3.008 | 0 | 43.098 | 25.32 | 3.1296 | 0 | 28.4496 | 107744.8818 | 71123.88 | 178869
13.2 | 303000000 | b 32 mm dia | [8 empty] | RM | 350 | 65.41 | 0 | 65.41 | 4.9077 | 0 | 70.3177 | 31.65 | 3.9119 | 0 | 35.5619 | 24611.1993 | 12446.679 | 37058
14 | 303000000 | Providing and laying of PVC insulated copper conductor 1100 volt grade stranded flexible FRLS Wire in already laid conduit (Wiring from Floor Panel to Room DB, for Kitchen equipment) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14.1 | 303000000 | 3 nos - 4 sq.mm PVC insulated stranded flexible copper wires in conduit | [8 empty] | RM | 5000 | 93.895 | 0 | 93.895 | 7.0449 | 0 | 100.9399 | 32.705 | 4.0423 | 0 | 36.7473 | 504699.7092 | 183736.69 | 688436
14.2 | 303000000 | 3 nos - 6 sq.mm PVC insulated stranded flexible copper wires in conduit | [8 empty] | RM | 400 | 174.075 | 0 | 174.075 | 13.0608 | 0 | 187.1358 | 39.035 | 4.8247 | 0 | 43.8597 | 74854.3389 | 17543.8904 | 92398
14.3 | 303000000 | 3 nos - 10 sq.mm PVC insulated stranded flexible copper wires in conduit | [8 empty] | RM | 150 | 323.885 | 0 | 323.885 | 24.3011 | 0 | 348.1861 | 50.64 | 6.2591 | 0 | 56.8991 | 52227.9137 | 8534.8656 | 60763
A | 303000000 | CARPARK | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 303000000 | Wiring for following MCB controlled point for car park area with 2.5 sq.mm PVC insulated copper conductor 1100 volts grade stranded flexible FRLS wires in surface mounted 25mm dia heavy duty FRLS PVC conduit, including earthing of lighting fixture with 2.5 sq. mm. PVC insulated copper conductor stranded flexible FRLS wire (MCB not included). | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.1 | 303000000 | MCB controlled Primary point (from MCB to first light point) | [8 empty] | Pt | 28 | 4187.295 | 0 | 4187.295 | 314.1727 | 0 | 4501.4677 | 945 | 116.802 | 0 | 1061.802 | 126041.0968 | 29730.456 | 155772
1.2 | 303000000 | MCB controlled Secondary point ( from point to point of same circuit) | [8 empty] | Pt | 90 | 976.93 | 0 | 976.93 | 73.2991 | 0 | 1050.2291 | 220 | 27.192 | 0 | 247.192 | 94520.6152 | 22247.28 | 116768
B | 303000000 | RACEWAY & JUNCTION BOXES | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 303000000 | GI Raceway & Junction boxes | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.1 | 303000000 | Providing and fixing of overhead race way made from 1.6 mm thick pregalvenised steel sheet, factory fabricated, with internal partition of the following sizes including providing removable double folded cover of 1.6mm thick, knock out holes at regular interval, junction boxes and fixing accessories, earthing stud for terminating 8 SWG copper earth wire complete as required including supports, bends etc as per site requirement. The pregalvenised sheet shall be as per IS 277 or BS 2989 having tensile strength of minimum 500 N/sq.m. and minimum zinc coating of 275 GSM. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
a | 303000000 | 100 mm wide x 40 mm deep single compartment raceway | [8 empty] | RM | 730 | 339.71 | 0 | 339.71 | 25.4884 | 0 | 365.1984 | 164.58 | 20.3421 | 0 | 184.9221 | 266594.8621 | 134993.1242 | 401588
b | 303000000 | 200 mm wide x 40 mm deep single compartment raceway | [8 empty] | RM | 50 | 610.845 | 0 | 610.845 | 45.8317 | 0 | 656.6767 | 177.24 | 21.9069 | 0 | 199.1469 | 32833.835 | 9957.3432 | 42791
2 | 303000000 | Providing and fixing of 2 mm thick pregavanised sheet outlet junction box including providing cover with provision to adjust overall height, knock outs on four sides to accept raceways of specified sizes and cutouts to fix required outlets for following size of race ways. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
a | 303000000 | 150 mm wide x 40 mm deep single compatment raceway | [8 empty] | Nos | 12 | 490.575 | 0 | 490.575 | 36.8078 | 0 | 527.3828 | 164.58 | 20.3421 | 0 | 184.9221 | 6328.5941 | 2219.0651 | 8548
b | 303000000 | 100 mm wide x 40 mm deep single compartment raceway | [8 empty] | Nos | 2 | 385.075 | 0 | 385.075 | 28.8922 | 0 | 413.9672 | 126.6 | 15.6478 | 0 | 142.2478 | 827.9344 | 284.4955 | 1112
C. | 303000000 | CABLES, MAINS, SUB MAINS AND CABLE TRAYS | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 303000000 | Supplying & laying of following 1100 volt grade XLPE insulated PVC inner sheathed and FRLS PVC outer sheathed aluminium conductor armoured cables as per specification in existing trenches, buried in soft soil, cable trays, ducts, clamped to wall with suitable clamps including, saddles fixing bolts, connecting testing and commissioning. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.1 | 303000000 | 3.1/2 core 300 sq. mm | [8 empty] | RM | 2400 | 1029.68 | 0 | 1029.68 | 77.2569 | 0 | 1106.9369 | 82.29 | 10.171 | 0 | 92.461 | 2656648.537 | 221906.5056 | 2878555
1.2 | 303000000 | 3.1/2 core 240 sq. mm. | [8 empty] | RM | 2350 | 845.055 | 0 | 845.055 | 63.4045 | 0 | 908.4595 | 75.96 | 9.3887 | 0 | 85.3487 | 2134879.7701 | 200569.3416 | 2335449
1.3 | 303000000 | 3.1/2 core 185 sq. mm. | [8 empty] | RM | 350 | 667.815 | 0 | 667.815 | 50.1062 | 0 | 717.9212 | 75.96 | 9.3887 | 0 | 85.3487 | 251272.4058 | 29872.0296 | 281144
1.4 | 303000000 | 3.1/2 core 120 sq.mm | [8 empty] | RM | 300 | 463.145 | 0 | 463.145 | 34.7498 | 0 | 497.8948 | 69.63 | 8.6063 | 0 | 78.2363 | 149368.4308 | 23470.8804 | 172839
1.5 | 303000000 | 3.1/2 core 50 sq. mm | [8 empty] | RM | 650 | 218.385 | 0 | 218.385 | 16.3854 | 0 | 234.7704 | 56.97 | 7.0415 | 0 | 64.0115 | 152600.7773 | 41607.4698 | 194208
1.6 | 303000000 | 4 core 35 sq. mm | [8 empty] | RM | 100 | 192.01 | 0 | 192.01 | 14.4065 | 0 | 206.4165 | 44.31 | 5.4767 | 0 | 49.7867 | 20641.651 | 4978.6716 | 25620
1.7 | 303000000 | 4 core 25 sq. mm | [8 empty] | RM | 4750 | 151.92 | 0 | 151.92 | 11.3986 | 0 | 163.3186 | 25.32 | 3.1296 | 0 | 28.4496 | 775763.1486 | 135135.372 | 910899
2 | 303000000 | Supplying & laying of following 1100 volt grade XLPE insulated FRLS PVC outer sheathed copper conductor armoured cable as per specification in existing trenches, cable trays ducts , clamped to wall with suitable clamps, including fixing bolts, connecting testing and commissioning. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.1 | 303000000 | 4 core 16 sq.mm | [8 empty] | RM | 50 | 597.13 | 0 | 597.13 | 44.8027 | 0 | 641.9327 | 27.43 | 3.3903 | 0 | 30.8203 | 32096.6332 | 1541.0174 | 33638
2.2 | 303000000 | 4 core 10 sq.mm | [8 empty] | RM | 100 | 405.12 | 0 | 405.12 | 30.3962 | 0 | 435.5162 | 23.21 | 2.8688 | 0 | 26.0788 | 43551.6154 | 2607.8756 | 46159
2.3 | 303000000 | 4 core 4 sq.mm | [8 empty] | RM | 1950 | 188.845 | 0 | 188.845 | 14.169 | 0 | 203.014 | 14.77 | 1.8256 | 0 | 16.5956 | 395877.3787 | 32361.3654 | 428239
2.4 | 303000000 | 3 core 4 sq.mm | [8 empty] | RM | 1450 | 149.81 | 0 | 149.81 | 11.2402 | 0 | 161.0502 | 14.77 | 1.8256 | 0 | 16.5956 | 233522.8542 | 24063.5794 | 257586
2.5 | 303000000 | 4 core 2.5 sq.mm control cable | [8 empty] | RM | 25 | 129.765 | 0 | 129.765 | 9.7363 | 0 | 139.5013 | 14.77 | 1.8256 | 0 | 16.5956 | 3487.5317 | 414.8893 | 3902
2.6 | 303000000 | 7 core 2.5 sq.mm control cable | [8 empty] | RM | 50 | 216.275 | 0 | 216.275 | 16.2271 | 0 | 232.5021 | 23.21 | 2.8688 | 0 | 26.0788 | 11625.1057 | 1303.9378 | 12929
2.7 | 303000000 | 12 core 2.5 sq.mm control cable | [8 empty] | RM | 150 | 301.73 | 0 | 301.73 | 22.6388 | 0 | 324.3688 | 25.32 | 3.1296 | 0 | 28.4496 | 48655.3203 | 4267.4328 | 52923
2.8 | 303000000 | 3 core 2.5 sq.mm (Flexible copper cable for swimming pool ltg) | [8 empty] | RM | 100 | 70.685 | 0 | 70.685 | 5.3035 | 0 | 75.9885 | 14.77 | 1.8256 | 0 | 16.5956 | 7598.8496 | 1659.5572 | 9258
3 | 303000000 | Cable end termination of the following XLPE insulated FRLS PVC outer sheathed aluminium/copper conductor armoured cables of 1100 volt grade including supplying and fixing of bimettalic crimping lugs, double compression glands with earthing. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.1 | 303000000 | 3.1/2 core 300 sq. mm.Aluminium Cable | [8 empty] | Nos. | 100 | 2137.43 | 0 | 2137.43 | 160.3714 | 0 | 2297.8014 | 506.4 | 62.591 | 0 | 568.991 | 229780.1373 | 56899.104 | 286679
3.2 | 303000000 | 3.1/2 core 240 sq. mm. Aluminium Cable | [8 empty] | Nos. | 100 | 1826.205 | 0 | 1826.205 | 137.0202 | 0 | 1963.2252 | 443.1 | 54.7672 | 0 | 497.8672 | 196322.5161 | 49786.716 | 246109
3.3 | 303000000 | 3.1/2 core 185 sq. mm. Aluminium Cable | [8 empty] | Nos. | 14 | 1795.61 | 0 | 1795.61 | 134.7246 | 0 | 1930.3346 | 379.8 | 46.9433 | 0 | 426.7433 | 27024.6847 | 5974.4059 | 32999
3.4 | 303000000 | 3.1/2 core 120 sq. mm. Aluminium Cable | [8 empty] | Nos. | 10 | 1113.025 | 0 | 1113.025 | 83.5103 | 0 | 1196.5353 | 284.85 | 35.2075 | 0 | 320.0575 | 11965.3527 | 3200.5746 | 15166
3.5 | 303000000 | 3.1/2 core 50 sq. mm. Aluminium Cable | [8 empty] | Nos. | 56 | 651.99 | 0 | 651.99 | 48.9188 | 0 | 700.9088 | 189.9 | 23.4716 | 0 | 213.3716 | 39250.8933 | 11948.8118 | 51200
3.6 | 303000000 | 4 core 35 sq. mm Aluminium Cable | [8 empty] | Nos. | 10 | 445.21 | 0 | 445.21 | 33.4041 | 0 | 478.6141 | 158.25 | 19.5597 | 0 | 177.8097 | 4786.1411 | 1778.097 | 6564
3.7 | 303000000 | 4 core 25 sq. mm Aluminium Cable | [8 empty] | Nos. | 266 | 432.55 | 0 | 432.55 | 32.4542 | 0 | 465.0042 | 158.25 | 19.5597 | 0 | 177.8097 | 123691.1242 | 47297.3802 | 170989
3.8 | 303000000 | 4 core 16 sq. mm copper cable | [8 empty] | Nos. | 4 | 418.835 | 0 | 418.835 | 31.4252 | 0 | 450.2602 | 126.6 | 15.6478 | 0 | 142.2478 | 1801.0408 | 568.991 | 2370
3.9 | 303000000 | 4 core 10 sq. mm copper cable | [8 empty] | Nos. | 8 | 291.18 | 0 | 291.18 | 21.8472 | 0 | 313.0272 | 126.6 | 15.6478 | 0 | 142.2478 | 2504.2179 | 1137.9821 | 3642
3.1 | 303000000 | 4 core 4 sq. mm copper cable | [8 empty] | Nos. | 112 | 290.125 | 0 | 290.125 | 21.7681 | 0 | 311.8931 | 94.95 | 11.7358 | 0 | 106.6858 | 34932.0248 | 11948.8118 | 46881
3.11 | 303000000 | 3 core 4 sq.mm copper cable | [8 empty] | Nos. | 66 | 285.905 | 0 | 285.905 | 21.4515 | 0 | 307.3565 | 94.95 | 11.7358 | 0 | 106.6858 | 20285.5258 | 7041.2641 | 27327
3.12 | 303000000 | 4 core 2.5 sq.mm copper cable | [8 empty] | Nos. | 8 | 285.905 | 0 | 285.905 | 21.4515 | 0 | 307.3565 | 94.95 | 11.7358 | 0 | 106.6858 | 2458.8516 | 853.4866 | 3312
3.13 | 303000000 | 7 core 2.5 sq.mm copper cable | [8 empty] | Nos. | 8 | 286.96 | 0 | 286.96 | 21.5306 | 0 | 308.4906 | 94.95 | 11.7358 | 0 | 106.6858 | 2467.9249 | 853.4866 | 3321
3.14 | 303000000 | 12 core 2.5 sq.mm copper cable | [8 empty] | Nos. | 4 | 291.18 | 0 | 291.18 | 21.8472 | 0 | 313.0272 | 158.25 | 19.5597 | 0 | 177.8097 | 1252.1089 | 711.2388 | 1963
4 | 303000000 | Supply and installation of following RCC (NP-2 class) Hume pipe under paved areas, including providing 75 mm thick cement concrete all around pipe 1:3:6 (1 cement, 3 coarse sand and 6 crushed stone aggregate). | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4.1 | 303000000 | 100 mm dia ID | [8 empty] | RM | 25 | 327.05 | 0 | 327.05 | 24.5386 | 0 | 351.5886 | 126.6 | 15.6478 | 0 | 142.2478 | 8789.714 | 3556.194 | 12346
4.2 | 303000000 | 150 mm dia ID | [8 empty] | RM | 25 | 392.46 | 0 | 392.46 | 29.4463 | 0 | 421.9063 | 139.26 | 17.2125 | 0 | 156.4725 | 10547.6568 | 3911.8134 | 14459
5 | 303000000 | Providing and fixing of the following size medium class PVC pipe sleeves. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.1 | 303000000 | 100 mm. dia. | [8 empty] | RM | 25 | 327.05 | 0 | 327.05 | 24.5386 | 0 | 351.5886 | 126.6 | 15.6478 | 0 | 142.2478 | 8789.714 | 3556.194 | 12346
6 | 303000000 | Supply and fixing of factory fabricated Pregalvanized ( 120 GSM) GI ladder type cable trays, with radial bends, suspenders and supports as per specification and of the following sizes. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6.1 | 303000000 | 1200 mm wide | [8 empty] | RM | 200 | 1796.665 | 0 | 1796.665 | 134.8038 | 0 | 1931.4688 | 227.88 | 28.166 | 0 | 256.046 | 386293.755 | 51209.1936 | 437503
6.2 | 303000000 | 1000 mm wide | [8 empty] | RM | 325 | 1674.285 | 0 | 1674.285 | 125.6216 | 0 | 1799.9066 | 221.55 | 27.3836 | 0 | 248.9336 | 584969.6462 | 80903.4135 | 665873
6.3 | 303000000 | 750 mm wide | [8 empty] | RM | 25 | 1136.235 | 0 | 1136.235 | 85.2517 | 0 | 1221.4867 | 202.56 | 25.0364 | 0 | 227.5964 | 30537.1678 | 5689.9104 | 36227
6.4 | 303000000 | 600 mm wide | [8 empty] | RM | 75 | 1081.375 | 0 | 1081.375 | 81.1356 | 0 | 1162.5106 | 189.9 | 23.4716 | 0 | 213.3716 | 87188.2925 | 16002.873 | 103191
6.5 | 303000000 | 450 mm wide | [8 empty] | RM | 285 | 783.865 | 0 | 783.865 | 58.8134 | 0 | 842.6784 | 170.91 | 21.1245 | 0 | 192.0345 | 240163.3414 | 54729.8257 | 294893
7 | 303000000 | Supply and fixing of perforated type factory fabricatedPregalvanized(120 GSM) GI cable trays of the following sizes including providing GI suspenders and supports as per specifications.. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7.1 | 303000000 | 300 mm wide | [8 empty] | RM | 400 | 643.55 | 0 | 643.55 | 48.2856 | 0 | 691.8356 | 151.92 | 18.7773 | 0 | 170.6973 | 276734.2226 | 68278.9248 | 345013
7.2 | 303000000 | 150 mm wide | [8 empty] | RM | 650 | 434.66 | 0 | 434.66 | 32.6125 | 0 | 467.2725 | 113.94 | 14.083 | 0 | 128.023 | 303727.1509 | 83214.9396 | 386942
D. | 303000000 | DISTRIBUTION BOARDS / RISING MAINS | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
a | 303000000 | Design, fabrication, assembling, supply, installation, testing and commissioning of Main LT panel, Main Distribution Panels, Sub Distribution panels and Final Distribution panels suitable for 415 V, 3 phase, 50 Hz, 4 wire power supply system.Panels shall be fabricated out of 2 mm thick CRCA sheet steel in cubical formation, compartmentalized in Form 3b Construction, floor mounted, free standing and shall be dust and vermin proof. 3 mm thick cable gland plate, shall be provided both at the top and the bottom of the panel.Final distribution panels shall be fabricated out of 1.2mm & 1.6 mm thick CRCA sheet steel for SPN & TPN db respectively and shall be wall mounted. All large panels shall be provided with lifting hooks. Distribution panels shall be fabricated in accordance with the specifications. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 303000000 | Main LT Panel | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.1 | 303000000 | Section – I | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
A. | 303000000 | Incoming Air Circuit Breaker A For DG supply | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 303000000 | 1600 amps 4P manually operated fully drawout type air circuit breaker with built in microprocessor based release unit for protection and measurment as per specification and with following accessories : | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | Phase indicating light protected by 2 amps MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | Breaker ON / OFF / TRIP indicating lights with control MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | Under voltage release (only provision required) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iv. | 303000000 | 24 V DC Shunt trip coil | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
v. | 303000000 | 3 Nos. 96 x 96 mm sq. 0- 1600/ 5 amps CTR digital ammeter with 3 nos. 1600/ 5 amps 15 VA CL : 1 CTs | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
vi. | 303000000 | 96 x 96 mm sq. 0-500 Volt digital voltmeter with selector switch protected by 2 amp TP MCBs | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
vii. | 303000000 | Load Manager with RS 485 port | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
viii. | 303000000 | Breaker control switch | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
B. | 303000000 | Incoming Air Circuit Breaker B For Transformer supply | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 303000000 | 1600 amps 4 pole electrically operated fully drawout type air circuit breaker with built in microprocessor based release unit for protection and measurment as per specification and with following accessories : | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | Phase indicating light protected by 2 amps MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | Breaker ON / OFF / TRIP indicating lights with control MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | Under voltage release | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iv. | 303000000 | 24 V DC Shunt trip coil | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
v | 303000000 | Under voltage relay with timer (27) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
vi. | 303000000 | Over voltage relay with timer (59) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
vii. | 303000000 | Load Manager with RS 485 port | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
viii | 303000000 | Breaker control switch | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ix. | 303000000 | 3 Nos. 96 x 96 sq.mm 0- 1600 / 5 amps CTR digital ammeter with 3 nos 1600 / 5 amps, 15 VA Class I CTs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
x. | 303000000 | 96 x 96 mm sq. 0-500 Volt digital voltmeter with selector switch protected by 2 amp TP MCBs | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
xi. | 303000000 | Class – B surge arrestor (Lines to Neutral) & (Neutral to Earth) suitable for 3 phases. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 1600 Amps rating Auto Transfer Switch with overlapping neutral , In phase open transition, without Bypass and with required WCR suitable for main lt panel application with 25 KA as per specification. ASCO 7000 series or equivalent. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | DELETED on 06.05.13 | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Bus Bars | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 1600 amps 4 pole (25 KA) copper bus bars with colour coded heat shrinkable insulating sleeves | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
C. | 303000000 | Outgoing | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | 800 amps 4 pole manually operated fully drawout type air circuit breaker with ON/OFF/TRIP indicating lamps with MCBs and microprocessor based release for protection & indication as per specification. (for HVAC panel) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | 630 amps 4 pole MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | 400 amps 4 pole MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iv. | 303000000 | 250 amps 4 pole MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 303000000 | Spare MCCBs for the following : | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | 250 amps 4 pole MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | 400 amps 4 pole MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
D. | 303000000 | Bus Coupler : Breaker C | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 303000000 | 1600 amps 4 pole manually Electrically operated fully drawout type air circuit breaker with ON / OFF / TRIP indicating lamps with control MCBs, shunt trip, breaker control switch etc. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.1 | 303000000 | Changed on 06.05.13 | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E. | 303000000 | Incoming Air Circuit Breaker D For transformer supply | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 303000000 | 1600 amps 4P electrically operated fully drawout type air circuit breaker with built in microprocessor based release unit for protection & measurment as per specification and with following accessories : | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | Phase indicating light protected by 2 amps MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | Breaker ON / OFF / TRIP indicating lights with control MCBs | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | Under voltage release | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iv. | 303000000 | 24 V DC Shunt trip coil. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
v | 303000000 | Under voltage relay with timer (27) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
vi. | 303000000 | Over voltage relay with timer (59) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
vii. | 303000000 | Load Manager with RS 485 port | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
viii. | 303000000 | Breaker control switch | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ix. | 303000000 | 3 Nos. 96 x 96 sq.mm 0- 1600 / 5 amps CTR digital ammeter with 3 nos 1600 / 5 amps, 15 VA Class I CTs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
x. | 303000000 | 96 x 96 mm sq. 0-500 Volt digital voltmeter with selector switch protected by 2 amp TP MCBs | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
xi. | 303000000 | Class – B surge arrestor (Lines to Neutral) & (Neutral to Earth) suitable for 3 phases. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 1600 Amps rating Auto Transfer Switch with overlapping neutral , In phase open transition, without Bypass and with required WCR suitable for main lt panel application with 25 KA as per specification. ASCO 7000 series or equivalent. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Deleted on 06.05.13 | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
F. | 303000000 | Incoming Air Circuit Breaker E (For DG Supply) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 303000000 | 1600 amps 4P manually Electrically operated fully drawout type air circuit breaker with built in microprocessor based release unit for protection and measurment as per specification and with following accessories : | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.1 | 303000000 | changed on 06.05.13 | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | Phase indicating light protected by 2 amps MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | Breaker ON / OFF / TRIP indicating lights with control MCBs | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | Under voltage release (only provision required) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iv. | 303000000 | 24 V DC Shunt trip coil | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
v | 303000000 | 3 Nos. 96 x 96 mm sq. 0-1600/ 5 amps CTR digital ammeter with 3 Nos. 1600/ 5 amps 15 VA CL:1 CTs | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
vi. | 303000000 | 96 x 96 mm sq 0-500 Volt digital voltmeter with selector switch PTs shall be protected by 2 amp TP MCBs | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
vii. | 303000000 | Load Manager with RS 485 port | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
viii. | 303000000 | Breaker control switch | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Bus Bars | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 1600 amps 4 pole manually operated fully drawout type air circuit breaker with ON / OFF / TRIP indicating lamps with control MCBs, shunt trip, breaker control switch etc. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
G. | 303000000 | Outgoing | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | 1000 amps 4 pole manually operated fully drawout type air circuit breaker with ON/OFF/TRIP indicating lamps with MCBs and microprocessor based release for protection & indication as per specification. (for fire emergency panel) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | 800 amps 4 pole manually operated fully drawout type air circuit breaker with ON/OFF/TRIP indicating lamps with MCBs and microprocessor based release for protection & indication as per specification. (for HVAC panel ) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | 630 amps 4 pole MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iv. | 303000000 | 400 amps 4 pole MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
v. | 303000000 | 250 amps 4 pole MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Spare MCCBs for the following : | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | 250 amps 4 pole MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | 400 amps 4 pole MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Notes : | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | All outgoing feeders shall have suitable range of followings (except capacitor feeders) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | a. Digital electronic KWH meter with RS 485 port including spare. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | b. Digital electronic ammeter with selector switch and 3 Nos. CTs including spare. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | c. Three phase indicating lamps protected by 2 amps SP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | d. Nos. 630 / 5, 15 VA CTs shall be provided for APFCR | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | All breakers shall be electrically/ mechanically interlocked as per schematic diagram. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | All MCCBs shall be suitable for 25 KA (ICS) breaking capacity. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iv. | 303000000 | All ACBs shall be suitable for 25 kA( Icu=Ics=Icw for 1 sec.) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
v. | 303000000 | 415 / 110 V suitable rating control transformer shall be provided for aux. Control supply | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
vi. | 303000000 | Wiring with space heater, thermostat and control MCBs shall be provided all vertical sections of main LT panel. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
vii. | 303000000 | All outgoing MCCBs feeders shall be provided with built-in microprocessor release unit with earth fault protection and time delay. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
viii. | 303000000 | All incoming as well as outgoing feeders shall have pad locking facility. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ix. | 303000000 | suitable danger board shall be provided. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
x. | 303000000 | All bus bar section / backside panels shall have pad locking facility and hinged type door. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Main LT Panel as described above. | [8 empty] | Set | 1 | 6631568.585 | 0 | 6631568.585 | 497566.5909 | 0 | 7129135.1759 | 101280 | 12518.208 | 0 | 113798.208 | 7129135.1759 | 113798.208 | 7242933
2 | 303000000 | FIRE EMERGENCY PANEL | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 303000000 | Incoming | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.1 | 303000000 | 2 Nos. 1000 amps 4P manually operated drawout type ACB electromechanically and castle key interlocked. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.2 | 303000000 | i) 0-500 volts digital volt meter with selector switch be protected by 2 amps TP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.3 | 303000000 | ii) 0-1000. digital ammeter with selector switch and digital type KWH meter with 1000 / 5 amps 15 VA, CL 1 epoxy cast resin CTs | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.4 | 303000000 | iii) .Phase indicating light protected by 2 amps SP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.5 | 303000000 | Bus Bars | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.6 | 303000000 | 1000 amps TPN (25 KA for 1 Sec.) copper bus bars with Heat Shrinkable insulated sleeves | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 303000000 | Outgoings | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.1 | 303000000 | 400 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.2 | 303000000 | 250 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.3 | 303000000 | 160 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.4 | 303000000 | 100 amps TPN MCCBs | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.5 | 303000000 | Spare MCCBs of the following : | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.6 | 303000000 | 100 amps TPN MCCBs | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.7 | 303000000 | All outgoing MCCBs shall be of 25 KA breaking capacity | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.8 | 303000000 | FIRE EMERGENCY PANEL as described above | [8 empty] | No. | 1 | 969119.835 | 0 | 969119.835 | 72713.0612 | 0 | 1041832.8962 | 18990 | 2347.164 | 0 | 21337.164 | 1041832.8962 | 21337.164 | 1063170
3 | 303000000 | MDB PUBLIC & COMMON AREA LIGHTING | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 303000000 | Incoming | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | 400 Amps rating power Manual Change over switch suitable for 25 kA system fault level as per specification. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | 400 amps TPN MCCB with following accessories: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | 0-500 volts digital volt meter with selector switch be protected by 2 amps TP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iv. | 303000000 | 0- 400 Amps digital electronic ammeter with selector switch and 400 /5 amps 15 VA, CL 1 CTs . | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
v. | 303000000 | Phase indicating light protected by 2 amps SP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Bus Bars | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 400 amps TPN aluminium bus bars with coloured heat shrinkable insulated sleeve. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 303000000 | Outgoing | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 250 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 100 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Spare MCCBs of the following : | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 100 amps TPN MCCBs | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | All MCCBs shall be of 25 KA (Ics) breaking capacity. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | MDB LIGHTING described as above | [8 empty] | Set | 1 | 198234.5 | 0 | 198234.5 | 14873.5345 | 0 | 213108.0345 | 10128 | 1251.8208 | 0 | 11379.8208 | 213108.0345 | 11379.8208 | 224488
4 | 303000000 | MDB POWER -1 | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Incoming | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 630 amps TPN MCCB with following accessories: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | 0-500 volts digital volt meter with selector switch be protected by 2 amps TP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | 0- 630 Amps digital electronic ammeter with selector switch and 630 /5 amps 15 VA, CL 1 CTs . | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | Phase indicating light protected by 2 amps SP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Bus Bars | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 630 amps (25 KA) TPN aluminium bus bars with heat shrinkable insulation sleeve. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Outgoing | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 200 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 160 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Spare MCCBs of the following: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 160 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | All MCCBs shall be of 25KA( Ics) breaking capacity. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | MD POWER- 1 described as above | [8 empty] | No. | 1 | 221686.095 | 0 | 221686.095 | 16633.1077 | 0 | 238319.2027 | 10128 | 1251.8208 | 0 | 11379.8208 | 238319.2027 | 11379.8208 | 249699
5 | 303000000 | MDB POWER -2 | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Incoming | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 250 amps TPN MCCB (25 KA) with following accessories: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | 0-500 volts digital volt meter with selector switch be protected by 2 amps TP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | 0- 250 Amps digital electronic ammeter with selector switch and 3 nos 250/5 amps 15 VA, CL 1 CTs . | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | Phase indicating light protected by 2 amps SP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Bus Bars | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 250 amps TPN aluminium bus bars with heat shrinkable insulation sleeve. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Outgoing | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 100 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 amps TPN MCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Spare MCCBs of the following: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 100 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 amps TPN MCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | All MCCBs shall be of 25KA(Ics) breaking capacity. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | MD POWER -2 described as above | [8 empty] | No. | 1 | 96645.385 | 0 | 96645.385 | 7251.3032 | 0 | 103896.6882 | 10128 | 1251.8208 | 0 | 11379.8208 | 103896.6882 | 11379.8208 | 115277
6 | 303000000 | MDB POWER -3 | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Incoming | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 250 amps TPN MCCB (25 KA) with following accessories: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | 0-500 volts digital volt meter with selector switch be protected by 2 amps TP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | 0- 250 Amps digital electronic ammeter with selector switch and 3 nos 250/5 amps 5 VA, CL 1 CTs . | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | Phase indicating light protected by 2 amps SP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Bus Bars | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 250 amps TPN aluminium bus bars with heat shrinkable insulation sleeve. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Outgoing | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 100 amps TPN MCCB (FOR UPS BYPASS) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 amps TPN MCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Spare MCCBs of the following: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 amps TPN MCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | All MCCBs shall be of 25 KA(Ics) breaking capacity. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | MD POWER -3 described as above | [8 empty] | No. | 1 | 94850.83 | 0 | 94850.83 | 7116.6578 | 0 | 101967.4878 | 10128 | 1251.8208 | 0 | 11379.8208 | 101967.4878 | 11379.8208 | 113347
7 | 303000000 | MDB AHU & VENTILATION | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Incoming | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 400 amps TPN MCCB (25KA) with following accessories: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | 0-500 volts digital volt meter with selector switch be protected by 2 amps TP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | 0- 400 Amps digital electronic ammeter with selector switch and 3 nos 400/5 amps 5 VA, CL 1 CTs . | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | Phase indicating light protected by 2 amps SP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Bus Bars | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 400 amps (25 KA) TPN aluminium bus bars with heat shrinkable insulation sleeve. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Outgoing | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 160 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 100 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Spare MCCBs of the following: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 100 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | All MCCBs shall be of 25 KA(Ics) breaking capacity. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | MDB AHU & VENTILATION described as above | [8 empty] | No. | 1 | 146089.015 | 0 | 146089.015 | 10961.0588 | 0 | 157050.0738 | 11394 | 1408.2984 | 0 | 12802.2984 | 157050.0738 | 12802.2984 | 169852
8 | 303000000 | MDB KITCHEN | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Incoming | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 630 amps TPN MCCB (25KA) with following accessories: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | 0-500 volts digital volt meter with selector switch be protected by 2 amps TP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | 0- 630 Amps digital electronic ammeter with selector switch and 3 nos 630/5 amps 15 VA, CL 1 CTs . | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | Phase indicating light protected by 2 amps SP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Bus Bars | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 630 amps (25 KA) TPN aluminium bus bars with heat shrinkable insulation sleeve. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Outgoing | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 315 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 250 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 200 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Spare MCCBs of the following: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 160 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 100 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | All MCCBs shall be of 25 KA(Ics) breaking capacity. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | MDB KITCHEN described as above | [8 empty] | No. | 1 | 218191.935 | 0 | 218191.935 | 16370.9409 | 0 | 234562.8759 | 8862 | 1095.3432 | 0 | 9957.3432 | 234562.8759 | 9957.3432 | 244520
9 | 303000000 | FIRE VENTILATION DB. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Incoming | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 400 amps TPN MCCB (25KA) with following accessories: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | 0-500 volts digital volt meter with selector switch be protected by 2 amps TP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | 0- 400 Amps digital electronic ammeter with selector switch and 3 nos 400/5 amps 15 VA, CL 1 CTs . | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | Phase indicating light protected by 2 amps SP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Bus Bars | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 400 amps (25 KA) TPN aluminium bus bars with heat shrinkable insulation sleeve. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Outgoing | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 100 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 80 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 25 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Spare MCCBs of the following: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | All MCCBs shall be of 25 KA(Ics) breaking capacity. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | FIRE VENTILATION DB described as above | [8 empty] | No. | 1 | 143765.905 | 0 | 143765.905 | 10786.7559 | 0 | 154552.6609 | 8862 | 1095.3432 | 0 | 9957.3432 | 154552.6609 | 9957.3432 | 164510
10 | 303000000 | MDB ELEVATOR. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Incoming | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 250 amps TPN MCCB (25KA) with following accessories: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | 0-500 volts digital volt meter with selector switch be protected by 2 amps TP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | 0- 250 Amps digital electronic ammeter with selector switch and 3 nos 250/5 amps 15 VA, CL 1 CTs . | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | Digital electronic KWH meter with RS 485 port . | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iv. | 303000000 | Phase indicating light protected by 2 amps SP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Bus Bars | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 250 amps (25 KA) TPN aluminium bus bars with heat shrinkable insulation sleeve. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Outgoing | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 40 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Spare MCCBs of the following: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Note: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | a. All MCCBs shall be of 25 KA(Ics) breaking capacity. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | b. Digital electronic ammeter with selector switch and 3 Nos. CTs | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | MDB ELEVATOR described as above | [8 empty] | No. | 1 | 161166.02 | 0 | 161166.02 | 12092.2865 | 0 | 173258.3065 | 11394 | 1408.2984 | 0 | 12802.2984 | 173258.3065 | 12802.2984 | 186061
11 | 303000000 | SDB FIRE EMERGENCY TERRACE. (IP 55) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Incoming | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 160 amps TPN MCCB (25KA) with following accessories: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | 0-500 volts digital volt meter with selector switch be protected by 2 amps TP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | 0- 160 Amps digital electronic ammeter with selector switch and 3 nos 160/5 amps 15 VA, CL 1 CTs . | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | Phase indicating light protected by 2 amps SP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Bus Bars | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 160 amps (25 KA) TPN aluminium bus bars with heat shrinkable insulation sleeve. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Outgoing | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 25 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 32 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Spare MCCBs of the following: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 40 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | All MCCBs shall be of 25 KA(Ics) breaking capacity. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | SDB FIRE EMERGENCY TERRACE described as above | [8 empty] | No. | 1 | 184020.485 | 0 | 184020.485 | 13807.057 | 0 | 197827.542 | 11394 | 1408.2984 | 0 | 12802.2984 | 197827.542 | 12802.2984 | 210630
12 | 303000000 | SDB EMRGENCY LTG GUEST FLOOR | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Incoming | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 amps TPN MCCB (25KA) with following accessories: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | 0-500 volts digital volt meter with selector switch be protected by 2 amps TP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | 0- 63 Amps digital electronic ammeter with selector switch and 3 nos 63/5 amps 15 VA, CL 1 CTs . | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | Phase indicating light protected by 2 amps SP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Bus Bars | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 amps 4 pole aluminium bus bars with heat shrinkable insulation sleeve. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Outgoing | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 25 Amps DP MCBs | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Spare MCCBs of the following: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 25 Amps DP MCBs | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | SDB EMRGENCY LTG GUEST FLOOR described as above | [8 empty] | No. | 1 | 49518.535 | 0 | 49518.535 | 3715.3757 | 0 | 53233.9107 | 5064 | 625.9104 | 0 | 5689.9104 | 53233.9107 | 5689.9104 | 58924
13 | 303000000 | SDB LTG-1 PUBLIC AREA | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Incoming | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 250 amps TPN MCCB (25KA) (Thermal magnetic release) with following accessories: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | 0-500 volts digital volt meter with selector switch be protected by 2 amps TP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | 0- 250 Amps digital electronic ammeter with selector switch and 3 nos 250/5 amps 15 VA, CL 1 CTs . | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | [9 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | Phase indicating light protected by 2 amps SP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | [9 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iv | 303000000 | Class – C surge arrestor (Lines to Neutral) & (Neutral to Earth) suitable for 3 phases with backup MCB protection of suitable rating. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Bus Bars | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 250 amps TPN aluminium bus bars with heat shrinkable insulation sleeve. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Outgoing | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 40 Amps 4P MCB and 40 Amps DP RCCB of 30 mA | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 40 amps TPN MCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Spare MCCBs of the following: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 40 amps TPN MCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 40 Amps 4P MCB and 40 Amps DP RCCB of 30 mA | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | SDB LTG PUBLIC AREA described as above | [8 empty] | No. | 1 | 139696.77 | 0 | 139696.77 | 10481.4487 | 0 | 150178.2187 | 8862 | 1095.3432 | 0 | 9957.3432 | 150178.2187 | 9957.3432 | 160136
14 | 303000000 | SDB LTG-2 BOH AREA | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Incoming | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 100 amps TPN MCCB (25KA) with following accessories: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | 0-500 volts digital volt meter with selector switch be protected by 2 amps TP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | 0- 100 Amps digital electronic ammeter with selector switch and 3 nos 100/5 amps 5 VA, CL 1 CTs . | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | Phase indicating light protected by 2 amps SP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iv | 303000000 | Class – C surge arrestor (Lines to Neutral) & (Neutral to Earth) suitable for 3 phases with backup MCB protection of suitable rating. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Bus Bars | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 100 amps TPN aluminium bus bars with heat shrinkable insulation sleeve. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Outgoing | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 40 amps TPN MCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Spare MCCBs of the following: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 40 amps TPN MCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | SDB LTG-2 BOH AREA described as above | [8 empty] | No. | 1 | 76348.24 | 0 | 76348.24 | 5728.4084 | 0 | 82076.6484 | 6330 | 782.388 | 0 | 7112.388 | 82076.6484 | 7112.388 | 89189
15 | 303000000 | SDB LAUNDRY | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Incoming | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 160 amps TPN MCCB (25KA) with following accessories: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | 0-500 volts digital volt meter with selector switch be protected by 2 amps TP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | 0- 160 Amps digital electronic ammeter with selector switch and 3 nos 160/5 amps 5 VA, CL 1 CTs . | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | Phase indicating light protected by 2 amps SP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iv | 303000000 | Class – C surge arrestor (Lines to Neutral) & (Neutral to Earth) suitable for 3 phases with backup MCB protection of suitable rating. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Bus Bars | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 160 amps TPN aluminium bus bars with heat shrinkable insulation sleeve. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Outgoing | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 amps TPN MCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Spare MCCBs of the following: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 amps TPN MCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | SDB LAUNDRY described as above | [8 empty] | No. | 1 | 64980.615 | 0 | 64980.615 | 4875.4955 | 0 | 69856.1105 | 6330 | 782.388 | 0 | 7112.388 | 69856.1105 | 7112.388 | 76968
16 | 303000000 | MDB UPS. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Incoming | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 100 amps TPN MCCB ISOLATOR with following accessories: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | 0-500 volts digital volt meter with selector switch be protected by 2 amps TP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | 0- 1000 Amps digital electronic ammeter with selector switch and 3 nos 100/5 amps 15 VA, CL 1 CTs . | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | Digital electronic KWH meter with RS 485 port . | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iv. | 303000000 | Phase indicating light protected by 2 amps SP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Bus Bars | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 160 amps (10 KA) TPN aluminium bus bars with heat shrinkable insulation sleeve. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Outgoing | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 amps TPN MCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Spare MCBs of the following: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | MDB UPS described as above | [8 empty] | No. | 1 | 73500.795 | 0 | 73500.795 | 5514.7646 | 0 | 79015.5596 | 7596 | 938.8656 | 0 | 8534.8656 | 79015.5596 | 8534.8656 | 87550
17 | 303000000 | SDB AHU & VENTILATION BASEMENT-2. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Incoming | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 100 amps TPN MCCB (25KA) with following accessories: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | 0-500 volts digital volt meter with selector switch be protected by 2 amps TP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | 0- 100 Amps digital electronic ammeter with selector switch and 3 nos 100/5 amps 15 VA, CL 1 CTs . | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | Phase indicating light protected by 2 amps SP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Bus Bars | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 100 amps TPN aluminium bus bars with heat shrinkable insulation sleeve. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Outgoing | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 25 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Spare MCCBs of the following: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 25 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | All MCCBs shall be of 25 KA(Ics) breaking capacity. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | SDB AHU & VENTILATION BASEMENT-2 described as above | [8 empty] | No. | 1 | 136226.875 | 0 | 136226.875 | 10221.1024 | 0 | 146447.9774 | 8862 | 1095.3432 | 0 | 9957.3432 | 146447.9774 | 9957.3432 | 156405
18 | 303000000 | SDB AHU & VENTILATION BASEMENT-1. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Incoming | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 100 amps TPN MCCB (25KA) with following accessories: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | 0-500 volts digital volt meter with selector switch be protected by 2 amps TP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | 0- 100 Amps digital electronic ammeter with selector switch and 3 nos 100/5 amps 15 VA, CL 1 CTs . | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | Phase indicating light protected by 2 amps SP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Bus Bars | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 100 amps TPN aluminium bus bars with heat shrinkable insulation sleeve. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Outgoing | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 25 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Spare MCCBs of the following: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 25 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | All MCCBs shall be of 25 KA(Ics) breaking capacity. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | SDB AHU & VENTILATION BASEMENT-1 described as above | [8 empty] | No. | 1 | 148090.35 | 0 | 148090.35 | 11111.219 | 0 | 159201.569 | 8862 | 1095.3432 | 0 | 9957.3432 | 159201.569 | 9957.3432 | 169159
19 | 303000000 | SDB AHU & VENTILATION GROUND. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Incoming | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 100 amps TPN MCCB (25KA) with following accessories: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | 0-500 volts digital volt meter with selector switch be protected by 2 amps TP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | 0- 100 Amps digital electronic ammeter with selector switch and 3 nos 100/5 amps 15 VA, CL 1 CTs . | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | Phase indicating light protected by 2 amps SP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Bus Bars | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 100 amps TPN aluminium bus bars with heat shrinkable insulation sleeve. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Outgoing | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 25 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Spare MCCBs of the following: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 25 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | All MCCBs shall be of 25 KA(Ics) breaking capacity. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | SDB AHU & VENTILATION GROUND described as above | [8 empty] | No. | 1 | 125936.405 | 0 | 125936.405 | 9449.0085 | 0 | 135385.4135 | 8862 | 1095.3432 | 0 | 9957.3432 | 135385.4135 | 9957.3432 | 145343
20 | 303000000 | SDB AHU & VENTILATION TRANSFER FLOOR-01. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Incoming | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 160 amps TPN MCCB (25KA) with following accessories: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | 0-500 volts digital volt meter with selector switch be protected by 2 amps TP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | 0- 160 Amps digital electronic ammeter with selector switch and 3 nos 160/5 amps 15 VA, CL 1 CTs . | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | Phase indicating light protected by 2 amps SP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Bus Bars | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 160 amps TPN aluminium bus bars with heat shrinkable insulation sleeve. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Outgoing | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 32 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 25 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Spare MCCBs of the following: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 25 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | All MCCBs shall be of 25 KA(Ics) breaking capacity. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | SDB AHU & VENTILATION TRANSFER FLOOR-01described as above | [8 empty] | No. | 1 | 219891.54 | 0 | 219891.54 | 16498.4622 | 0 | 236390.0022 | 10128 | 1251.8208 | 0 | 11379.8208 | 236390.0022 | 11379.8208 | 247770
21 | 303000000 | SDB AHU & VENTILATION TRANSFER FLOOR-02. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Incoming | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 160 amps TPN MCCB (25KA) with following accessories: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | 0-500 volts digital volt meter with selector switch be protected by 2 amps TP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | 0- 160 Amps digital electronic ammeter with selector switch and 3 nos 160/5 amps 15 VA, CL 1 CTs . | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | Phase indicating light protected by 2 amps SP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Bus Bars | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 160 amps TPN aluminium bus bars with heat shrinkable insulation sleeve. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Outgoing | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 40 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 32 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 25 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Spare MCCBs of the following: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 25 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | All MCCBs shall be of 25 KA(Ics) breaking capacity. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | SDB AHU & VENTILATION TRANSFER FLOOR-02 described as above | [8 empty] | No. | 1 | 218934.655 | 0 | 218934.655 | 16426.6672 | 0 | 235361.3222 | 10128 | 1251.8208 | 0 | 11379.8208 | 235361.3222 | 11379.8208 | 246741
22 | 303000000 | SDB COMMISSIONARY KITCHEN-01 | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Incoming | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 200 amps TPN MCCB (25KA ) with following accessories: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | 0-500 volts digital volt meter with selector switch be protected by 2 amps TP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | 0- 200Amps digital electronic ammeter with selector switch and 200/5 amps 15 VA, CL 1 CTs . | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | Phase indicating light protected by 2 amps SP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Bus Bars | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 200 amps TPN Aluminium bus bars with heat shrinkable insulation sleeve. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Outgoing | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 25 Amps 4P RCBO of 30 mA | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 40 Amps 4P RCBO of 30 mA | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 Amps 4P RCBO of 30 mA ( BA-31) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 amps TPN MCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Spare MCCBs of the following: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 amps TPN MCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 25 Amps 4P RCBO of 30 mA | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | SDB COMMISSIONARY KITCHEN-01 described as above | [8 empty] | No. | 1 | 143644.58 | 0 | 143644.58 | 10777.6528 | 0 | 154422.2328 | 8862 | 1095.3432 | 0 | 9957.3432 | 154422.2328 | 9957.3432 | 164380
23 | 303000000 | SDB COMMISSIONARY KITCHEN-02 | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Incoming | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 200 amps TPN MCCB (25KA) with following accessories: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | 0-500 volts digital volt meter with selector switch be protected by 2 amps TP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | 0- 200Amps digital electronic ammeter with selector switch and 200/5 amps 5 VA, CL 1 CTs . | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | Phase indicating light protected by 2 amps SP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Bus Bars | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 200 amps TPN Aluminium bus bars with heat shrinkable insulation sleeve. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Outgoing | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 25 Amps 4P RCBO of 30 mA | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 40 Amps 4P RCBO of 30 mA | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 Amps 4P RCBO of 30 mA (BA-30) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 amps TPN MCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Spare MCCBs of the following: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 amps TPN MCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 25 Amps 4P RCBO of 30 mA | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | SDB COMMISSIONARY KITCHEN-02 described as above | [8 empty] | No. | 1 | 145440.19 | 0 | 145440.19 | 10912.3775 | 0 | 156352.5675 | 8862 | 1095.3432 | 0 | 9957.3432 | 156352.5675 | 9957.3432 | 166310
24 | 303000000 | SDB GROUND KITCHEN-03 | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Incoming | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 250 amps TPN MCCB (25KA) with following accessories (TMD): | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | 0-500 volts digital volt meter with selector switch be protected by 2 amps TP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | 0- 250Amps digital electronic ammeter with selector switch and 250/5 amps 15 VA, CL 1 CTs . | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | Phase indicating light protected by 2 amps SP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Bus Bars | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 250 amps TPN Aluminium bus bars with heat shrinkable insulation sleeve. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Outgoing | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 amps TPN MCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 40 Amps 4P RCBO of 30 mA | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 Amps 4P RCBO of 30 mA | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Spare MCCBs of the following: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | SDB GROUND KITCHEN-03 described as above | [8 empty] | No. | 1 | 131200.855 | 0 | 131200.855 | 9844.0002 | 0 | 141044.8552 | 8862 | 1095.3432 | 0 | 9957.3432 | 141044.8552 | 9957.3432 | 151002
25 | 303000000 | SDB FIRST FLOOR KITCHEN-04 | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Incoming | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 315 amps TPN MCCB (25KA) with following accessories: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | 0-500 volts digital volt meter with selector switch be protected by 2 amps TP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | 0- 315 Amps digital electronic ammeter with selector switch and 315/5 amps 15 VA, CL 1 CTs . | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | Phase indicating light protected by 2 amps SP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Bus Bars | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 315 amps TPN Aluminium bus bars with heat shrinkable insulation sleeve. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Outgoing | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 amps TPN MCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 100 Amps 4P RCBO of 30 mA | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 40 Amps 4P RCBO of 30 mA | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Spare MCCBs of the following: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 amps TPN MCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | SDB FIRST FLOOR KITCHEN-04 described as above | [8 empty] | No. | 1 | 105593.895 | 0 | 105593.895 | 7922.7099 | 0 | 113516.6049 | 8862 | 1095.3432 | 0 | 9957.3432 | 113516.6049 | 9957.3432 | 123474
26 | 303000000 | SDB GUEST ROOM 3RD TO 12TH FLOOR | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Incoming | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 100 amps TPN MCCB (25KA) with following accessories: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | 0-500 volts digital volt meter with selector switch be protected by 2 amps TP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | 0- 100 Amps digital electronic ammeter with selector switch and 3 nos 100/5 amps 15 VA, CL 1 CTs . | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | Phase indicating light protected by 2 amps SP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iv | 303000000 | Class – C surge arrestor (Lines to Neutral) & (Neutral to Earth) suitable for 3 phases with backup MCB protection of suitable rating. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Bus Bars | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 100 amps TPN aluminium bus bars with heat shrinkable insulation sleeve. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Outgoing | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 32 Amps DP RCBO of 30 mA | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 25 Amps DP RCBO of 30 mA | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 40 amps TPN MCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Spare MCCBs of the following: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 25 Amps DP RCBO of 30 mA | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | SDB GUEST ROOM 3RD TO 12TH FLOOR guest floor described as above | [8 empty] | No. | 10 | 122106.755 | 0 | 122106.755 | 9161.6698 | 0 | 131268.4248 | 8862 | 1095.3432 | 0 | 9957.3432 | 1312684.2483 | 99573.432 | 1412258
27 | 303000000 | SDB GUEST ROOM 2ND FLOOR | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Incoming | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 amps TPN MCCB (25KA) with following accessories: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | 0-500 volts digital volt meter with selector switch be protected by 2 amps TP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | 0- 63 Amps digital electronic ammeter with selector switch and 3 nos 63/5 amps 15 VA, CL 1 CTs . | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | Phase indicating light protected by 2 amps SP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iv | 303000000 | Class – C surge arrestor (Lines to Neutral) & (Neutral to Earth) suitable for 3 phases with backup MCB protection of suitable rating. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Bus Bars | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 amps TPN aluminium bus bars with heat shrinkable insulation sleeve. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Outgoing | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 25 Amps DP RCBO of 30 mA | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 40 amps TPN MCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Spare MCCBs of the following: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 25 Amps DP RCBO of 30 mA | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 40 amps TPN MCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | SDB GUEST ROOM 2ND FLOOR described as above | [8 empty] | No. | 1 | 78647.085 | 0 | 78647.085 | 5900.8908 | 0 | 84547.9758 | 7596 | 938.8656 | 0 | 8534.8656 | 84547.9758 | 8534.8656 | 93083
28 | 303000000 | SDB GUEST ROOM DB PENTH HOUSE FLOOR | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Incoming | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 100 amps TPN MCCB (25KA) with following accessories: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | 0-500 volts digital volt meter with selector switch be protected by 2 amps TP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | 0- 100 Amps digital electronic ammeter with selector switch and 3 nos 100/5 amps 15 VA, CL 1 CTs . | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | Phase indicating light protected by 2 amps SP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iv | 303000000 | Class – C surge arrestor (Lines to Neutral) & (Neutral to Earth) suitable for 3 phases with backup MCB protection of suitable rating. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Bus Bars | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 100 amps TPN aluminium bus bars with heat shrinkable insulation sleeve. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Outgoing | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 40 Amps DP RCBO of 100 mA | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 25 Amps DP RCBO of 30 mA | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 40 amps TPN MCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Spare MCCBs of the following: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 40 Amps DP RCBO of 100 mA | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 25 Amps DP RCBO of 30 mA | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 40 amps TPN MCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | SDB GUEST ROOM DB PENTH HOUSE FLOOR described as above | [8 empty] | No. | 1 | 76732.26 | 0 | 76732.26 | 5757.2215 | 0 | 82489.4815 | 7596 | 938.8656 | 0 | 8534.8656 | 82489.4815 | 8534.8656 | 91024
29 | 303000000 | SDB POWER FOR BOH AREA | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Incoming | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 160 amps TPN MCCB (25KA) with following accessories: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | 0-500 volts digital volt meter with selector switch be protected by 2 amps TP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | 0- 100 Amps digital electronic ammeter with selector switch and 3 nos 100/5 amps 15 VA, CL 1 CTs . | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | Phase indicating light protected by 2 amps SP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Bus Bars | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 160 amps TPN aluminium bus bars with heat shrinkable insulation sleeve. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Outgoing | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 amps TPN MCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Spare MCCBs of the following: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 amps TPN MCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | All MCCBs shall be of 25 KA(Ics) breaking capacity. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | SDB AHU & VENTILATION BASEMENT-1 described as above | [8 empty] | No. | 1 | 62134.225 | 0 | 62134.225 | 4661.9309 | 0 | 66796.1559 | 7596 | 938.8656 | 0 | 8534.8656 | 66796.1559 | 8534.8656 | 75331
30 | 303000000 | supply, installation, testing and commissioning of following rating ACB panel fabricated out of 2 mm thick CRCA sheet steel in cubical formation, compartmentalized in Form 3b Construction, floor mounted, free standing and shall be dust and vermin proof. 3 mm thick cable gland plate, shall be provided at the bottom of the panel suitable for 415 V, 3 phase, 50 Hz, 4 wire power supply system. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30.1 | 303000000 | 1600 amps 4 pole Manually operated fully drawout type air circuit breaker with built in microprocessor based release unit for protection (LSIG only) and indication as per specification and with following accessories : | [8 empty] | Nos. | 2 | 339624.545 | 0 | 339624.545 | 25482.0296 | 0 | 365106.5746 | 13926 | 1721.2536 | 0 | 15647.2536 | 730213.1492 | 31294.5072 | 761508
i. | 303000000 | Phase indicating light protected by 2 amps MCBs. 3 Sets | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | Breaker ON / OFF / TRIP indicating lights with control MCBs. 1 Set | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | 303000000 | Rising Mains (In sandwich Construction) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Design, manufacture, supply, installation, testing and commissioning of 630 amps rating ( 25 KA for 1 Sec) 4 pole rising mains in sandwich construction of aluminium bus bar with tap-off connection points at every 1000 mm intervals, expansion joints, fire barriers including necessary support and louvers for ventilation, fabricated out of GI sheet painted with approved paint shade including 2 Nos. of 50 x 6 mm mm external GI earthing conductor through out the length of the rising mains (Phase sequence shall match the sequence of the incoming breaker provided at the LT Panel). Thrust pad shall be provided for each rising main for necessary support to rising main and to prevent the bus bar expansion in downward direction. Also provide end cover to close the end of rising main and to provide extra end supports to the bus bars. (IP 55 required). | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Rising Mains in sandwich construction described as above | [8 empty] | RM | 40 | 10478.26 | 0 | 10478.26 | 786.1838 | 0 | 11264.4438 | 1012.8 | 125.1821 | 0 | 1137.9821 | 450577.7539 | 45519.2832 | 496097
32 | 303000000 | Supply, installation, testing and commissioning of tap off of following rating with boxes made out of 14 gauge GI sheet duly painted and mounted on the rising mains including providing of following MCCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32.1 | 303000000 | 100 amps TPN MCCB of 25 KA (Ics). | [8 empty] | No. | 11 | 10447.665 | 0 | 10447.665 | 783.8883 | 0 | 11231.5533 | 1899 | 234.7164 | 0 | 2133.7164 | 123547.0864 | 23470.8804 | 147018
32.2 | 303000000 | 63 amps TPN MCCB of 25 KA (Ics). | [8 empty] | No. | 1 | 10435.005 | 0 | 10435.005 | 782.9384 | 0 | 11217.9434 | 1266 | 156.4776 | 0 | 1422.4776 | 11217.9434 | 1422.4776 | 12640
33 | 303000000 | Supply, installation, testing and commissioning of 630 Amps 4 pole Isolator MCCB with castle key , operating handle and with Aluminium busbar arragement suitable for termination of 3 nos 240 sqmm Al. Armoured cable on the incoming side and suitable for busduct termination on the outgoing in enclosure fabricated out of 14 gauge GI sheet duly painted with approved paint shade and with 2 nos of earth terminal suitable for 32 x 6mm GI earth strip. | [8 empty] | Nos. | 2 | 57203.155 | 0 | 57203.155 | 4291.9527 | 0 | 61495.1077 | 6330 | 782.388 | 0 | 7112.388 | 122990.2154 | 14224.776 | 137215
34 | 303000000 | Supply, installation, testing and commissioning of 630 Amps 4 pole MCCB (25 KA Ics) with castle key , operating handle and suitable for busduct termination on the Incoming/outgoing in enclosure fabricated out of 14 gauge GI sheet duly painted with approved paint shade and with 2 nos of earth terminal suitable for 32 x 6mm GI earth strip. | [8 empty] | Nos. | 1 | 57203.155 | 0 | 57203.155 | 4291.9527 | 0 | 61495.1077 | 6330 | 782.388 | 0 | 7112.388 | 61495.1077 | 7112.388 | 68607
35 | 303000000 | FINAL DISTRIBUTION BOARDS | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Supply, installation, testing and commissioning of the following FDBs fabricated out of 1.2 mm & 1.6 mm thick CRCA sheet steel for SPN & TPN db respectively , double door construction, powder coated with approved shade and partitions to segregate phases. Approved lockable covers with padlocking arrangement for each phase, recessed in wall or surface mounted final distribution boards of the following description: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35.1 | 303000000 | Type A (LDB) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 12 way TPN DB, 12 Nos. 10 amps SP MCBs per phase with 3 Nos. 63 amps DP RCCBs of 30 mA leakage current and 1 no. 63 amps 4 pole MCB isolator as incomer with separate neutral link for each phase. | [8 empty] | Nos. | 1 | 14541.065 | 0 | 14541.065 | 1091.0161 | 0 | 15632.0811 | 2532 | 312.9552 | 0 | 2844.9552 | 15632.0811 | 2844.9552 | 18477
35.2 | 303000000 | Type B (LDB) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 10 way TPN DB, 10 Nos. 10 amps SP MCBs per phase with 3 Nos. 40 amps DP RCCBs of 30 mA leakage current and 1 no. 40 amps 4 pole MCB isolator as incomer with separate neutral link for each phase. | [8 empty] | Nos. | 2 | 12896.32 | 0 | 12896.32 | 967.6109 | 0 | 13863.9309 | 2532 | 312.9552 | 0 | 2844.9552 | 27727.8618 | 5689.9104 | 33418
35.3 | 303000000 | Type C (LDB) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 8 way TPN DB, 8 Nos. 10 amps SP MCBs per phase with 3 Nos. 40 amps DP RCCBs of 30 mA leakage current and 1 No. 40 amps 4 pole MCB isolator as incomer with separate neutral link for each phase. | [8 empty] | Nos. | 1 | 11841.32 | 0 | 11841.32 | 888.4542 | 0 | 12729.7742 | 2532 | 312.9552 | 0 | 2844.9552 | 12729.7742 | 2844.9552 | 15575
35.4 | 303000000 | Type D (LDB) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 6 way TPN DB, 6 Nos. 10 amps SP MCBs per phase with 3 Nos. 40 amps DP RCCBs of 30 mA leakage current and 1 No. 40 amps 4 pole MCB isolator as incomer with separate neutral link for each phase. | [8 empty] | Nos. | 8 | 10605.915 | 0 | 10605.915 | 795.7618 | 0 | 11401.6768 | 2532 | 312.9552 | 0 | 2844.9552 | 91213.4144 | 22759.6416 | 113973
35.5 | 303000000 | Type E (LDB) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 4 way TPN DB, 4 Nos. 10 amps SP MCBs per phase with 3 Nos. 40 amps DP RCCBs of 30 mA leakage current and 1 No. 40 amps 4 pole MCB isolator as incomer separate neutral link for each phase. | [8 empty] | Nos. | 1 | 10033.05 | 0 | 10033.05 | 752.7797 | 0 | 10785.8297 | 2532 | 312.9552 | 0 | 2844.9552 | 10785.8297 | 2844.9552 | 13631
35.6 | 303000000 | Type F (PDB) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 12 way TPN DB, 12 Nos. 16/20 amps SP MCB per phase with 3 Nos. 63 amps DP RCCBs of 30 mA leakage current and 1 No. 63 amps 4 pole MCB isolator as incomer with separate neutral link for each phase. | [8 empty] | Nos. | 1 | 14690.875 | 0 | 14690.875 | 1102.2564 | 0 | 15793.1314 | 2532 | 312.9552 | 0 | 2844.9552 | 15793.1314 | 2844.9552 | 18638
35.7 | 303000000 | Type F (PDB, L+PDB) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 10 way TPN DB, 10 Nos. 16/20 amps SP MCB per phase with 3 Nos. 63 amps DP RCCBs of 30 mA leakage current and 1 No. 63 amps 4 pole MCB isolator as incomer with separate neutral link for each phase. | [8 empty] | Nos. | 0 | 13901.735 | 0 | 13901.735 | 1043.0472 | 0 | 14944.7822 | 2532 | 312.9552 | 0 | 2844.9552 | 0 | 0 | 0
35.8 | 303000000 | Type (L+PDB for Penth house floor) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 10 way TPN DB, 10 Nos. 16/20 amps SP MCB per phase with 3 Nos. 63 amps DP RCCBs of 30 mA leakage current with 1 nos 63 amp DP contactor controlled through 0-24 hr timer in R phase and 1 No. 63 amps 4 pole MCB isolator as incomer with separate neutral link for each phase. | [8 empty] | Nos. | 1 | 19135.59 | 0 | 19135.59 | 1435.7433 | 0 | 20571.3333 | 2532 | 312.9552 | 0 | 2844.9552 | 20571.3333 | 2844.9552 | 23416
35.9 | 303000000 | Type F ( L+PDB for 3rd to 12th Guest floor) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 8 way TPN DB, 8 Nos. 16/20 amps SP MCBs per phase with 3 Nos. 63 amps DP RCCBs of 30 mA leakage current with 1 nos 63 amp DP contactor controlled through 0-24 hr timer in R phase and 1 No.63 amps 4 pole MCB isolator as incomer with separate neutral link for each phase. | [8 empty] | Nos. | 11 | 17691.295 | 0 | 17691.295 | 1327.3779 | 0 | 19018.6729 | 2532 | 312.9552 | 0 | 2844.9552 | 209205.4015 | 31294.5072 | 240500
35.1 | 303000000 | Type F (PDB) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 8 way TPN DB, 8 Nos. 16/20 amps SP MCBs per phase with 3 Nos. 63 amps DP RCCBs of 30 mA leakage current and 1 No.63 amps 4 pole MCB isolator as incomer with separate neutral link for each phase. | [8 empty] | Nos. | 6 | 12191.58 | 0 | 12191.58 | 914.7342 | 0 | 13106.3142 | 2532 | 312.9552 | 0 | 2844.9552 | 78637.8855 | 17069.7312 | 95708
35.11 | 303000000 | Type G (PDB) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 6 way TPN DB, 6 Nos. 16/20 amps SP MCBs per phase with 3 Nos. 63 amps DP RCCBs of 30 mA leakage current and 1 No. 63 amps 4 Pole MCB isolator as incomer with separate neutral link for each phase. | [8 empty] | Nos. | 3 | 11402.44 | 0 | 11402.44 | 855.5251 | 0 | 12257.9651 | 2532 | 312.9552 | 0 | 2844.9552 | 36773.8952 | 8534.8656 | 45309
35.12 | 303000000 | Type H (L+PDB for Transfer Floor & Substation) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 4 way TPN DB, 4 Nos. 16/20 amps SP MCBs per phase with 3 Nos. 40 amps DP RCCBs of 30 mA leakage current and 1 No. 40 amps 4 Pole MCB isolator as incomer with separate neutral link for each phase. | [8 empty] | Nos. | 2 | 11552.25 | 0 | 11552.25 | 866.7653 | 0 | 12419.0153 | 2532 | 312.9552 | 0 | 2844.9552 | 24838.0306 | 5689.9104 | 30528
35.13 | 303000000 | Type J ( ELDB ) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Incomer : 1no. 25A DP RCBO | [8 empty] | Nos. | 0 | 7323.81 | 0 | 7323.81 | 549.5055 | 0 | 7873.3155 | 1519.2 | 187.7731 | 0 | 1706.9731 | 0 | 0 | 0
| 303000000 | Out Going: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Set 1 having 6 nos 6 amps SP MCB with 25 amps DP insulated copper busbars. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Set 2 having 6 nos 6 amps SP MCB with 240 Volts, 50 Hz voltage sensing relay & 230Volts, 10 Amps DP contactor, 230 Volts No volt coil and with 25 amps DP insulated copper busbars. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35.14 | 303000000 | Type J ( ELDB + elevator lift shaft ltg DB ) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 6 way SPN DB, 6 Nos. 6 amps SP MCBs with 1 No. 25 amps DP RCBO of 30 mA leakage current as incomer including cu. Busbars | [8 empty] | Nos. | 10 | 3254.675 | 0 | 3254.675 | 244.1983 | 0 | 3498.8733 | 1519.2 | 187.7731 | 0 | 1706.9731 | 34988.7327 | 17069.7312 | 52058
35.15 | 303000000 | Type K ( STAIRCASE DB WITH TIMER ) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 6 way SPN DB, 4 Nos. 6 amps SP MCBs with 1 No. 25 amps DP RCBO of 30 mA leakage current as incomer including cu. Busbars and with 25 amps DP contactor controlled through 0-24 hr timer | [8 empty] | Nos. | 4 | 7680.4 | 0 | 7680.4 | 576.2604 | 0 | 8256.6604 | 1519.2 | 187.7731 | 0 | 1706.9731 | 33026.6416 | 6827.8925 | 39855
35.16 | 303000000 | Type L ( ELDB for Guest floor) ) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 4 way SPN DB, 4 Nos. 6 amps SP MCBs with 1 No. 25 amps DP RCBO of 30 mA leakage current as incomer including cu. Busbars | [8 empty] | Nos. | 10 | 2990.925 | 0 | 2990.925 | 224.4091 | 0 | 3215.3341 | 1519.2 | 187.7731 | 0 | 1706.9731 | 32153.341 | 17069.7312 | 49223
35.17 | 303000000 | Type M (For Kitchen/Laundry/Gym) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 6 way TPN DB, 6 Nos. 20 amps DP MCB and 25 amps RCCBs of 30 mA leakage current per phase as outgoing with 3 Nos. 63 amps DP MCBs and 1 No. 63 amps 4 pole MCB isolator as incomer including cu bus bars | [8 empty] | Nos. | 15 | 20420.58 | 0 | 20420.58 | 1532.1561 | 0 | 21952.7361 | 2532 | 312.9552 | 0 | 2844.9552 | 329291.0418 | 42674.328 | 371965
35.18 | 303000000 | Type R (For Kitchen/Laundry/spa/sump pump DB/stack park DB) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | TPN DB, 6 Nos. 20 / 32 amps 4 Pole MCB and 40 amps 4 pole RCCBs of 30 mA leakage current as outgoing and 1 No. 63 amps 4 pole MCB isolator as incomer including cu.bus bars. | [8 empty] | Nos. | 17 | 19762.26 | 0 | 19762.26 | 1482.7624 | 0 | 21245.0224 | 2532 | 312.9552 | 0 | 2844.9552 | 361165.3803 | 48364.2384 | 409530
35.19 | 303000000 | Type R (For Elevator ltg db) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | TPN DB, 6 Nos. 20 / 32 amps 4 Pole MCB as outgoing and 1 No. 63 amps 4 pole MCB isolator as incomer including cu.bus bars. | [8 empty] | Nos. | 2 | 8918.97 | 0 | 8918.97 | 669.1903 | 0 | 9588.1603 | 2532 | 312.9552 | 0 | 2844.9552 | 19176.3206 | 5689.9104 | 24866
35.2 | 303000000 | Type-S (for external lighting with IP-55) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 6 way TPN DB, 6 Nos. 10 amps SP MCBs per phase as outgoing with 3 Nos. 40 amps DP RCCBs of 30 mA leakage current with 3 nos 40 amp DP contactor controlled through 0-24 hr timer and 1 no. 40 amps 4 pole MCB isolator as incomer with separate neutral link for each phase. | [8 empty] | Nos. | 2 | 23924.235 | 0 | 23924.235 | 1795.0354 | 0 | 25719.2704 | 2785.2 | 344.2507 | 0 | 3129.4507 | 51438.5407 | 6258.9014 | 57697
35.21 | 303000000 | Type-S (for Façade lighting with IP-55) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 6 way TPN DB 6 Nos. 10 amps SP MCB per phase as outgoing with 3 nos. 40 amps DP RCCB of 30 mA leakage current plus 1 No. 40 amps TP Contactor controlled through 0-24 hour timer and 1 No. 40 amps 4 pole isolator as incomer. | [8 empty] | Nos. | 1 | 15082.28 | 0 | 15082.28 | 1131.6235 | 0 | 16213.9035 | 2785.2 | 344.2507 | 0 | 3129.4507 | 16213.9035 | 3129.4507 | 19343
35.22 | 303000000 | Type T (DB for work station fed by UPS) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 6 way TPN DB, 6 Nos. 16/20 amps SP MCBs per phase with 3 Nos. SI TYPE 63 amps DP RCCBs of 30 mA leakage current and 1 No. 63 amps 4 Pole MCB isolator as incomer with separate neutral link for each phase. | [8 empty] | Nos. | 8 | 14401.805 | 0 | 14401.805 | 1080.5674 | 0 | 15482.3724 | 2785.2 | 344.2507 | 0 | 3129.4507 | 123858.9794 | 25035.6058 | 148895
36 | 303000000 | Distribution Board for Hotel Guest Room | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36.1 | 303000000 | Supply, installation, testing and commissioning of 4 way SPN, MCB, DB with 4 Nos. 20 amps SPMCB through energy saving unit and 1 No. 25 DP MCB as incomer. | [8 empty] | Nos. | 200 | 1809.325 | 0 | 1809.325 | 135.7537 | 0 | 1945.0787 | 1519.2 | 187.7731 | 0 | 1706.9731 | 389015.731 | 341394.624 | 730410
36.2 | 303000000 | Supply, installation, testing and commissioning of 4 way SPN, MCB, DB with 6 Nos. 20 amps SPMCB through energy saving unit and 1 No. 32 DP MCB as incomer. | [8 empty] | Nos. | 22 | 2073.075 | 0 | 2073.075 | 155.5428 | 0 | 2228.6178 | 1519.2 | 187.7731 | 0 | 1706.9731 | 49029.592 | 37553.4086 | 86583
37 | 303000000 | Supply, installation, testing and commissioning of 3 nos. 100 amps 4 pole MCCB with operating handle (25 KA Ics) breaking capacity in 1.6 mm thick CRCA sheet steel enclosure of approved make design and painted with approved paint shade (for UPS & bypass system.) | [8 empty] | Nos. | 3 | 8392.525 | 0 | 8392.525 | 629.6912 | 0 | 9022.2162 | 633 | 78.2388 | 0 | 711.2388 | 27066.6485 | 2133.7164 | 29200
38 | 303000000 | Supply, installation, testing and commissioning of 63 amps 4 pole MCB in 1..6 mm thick MS enclosure of approved make design and painted with approved paint shade. (for gym ups) | [8 empty] | Nos. | 2 | 1497.045 | 0 | 1497.045 | 112.3233 | 0 | 1609.3683 | 189.9 | 23.4716 | 0 | 213.3716 | 3218.7366 | 426.7433 | 3645
39 | 303000000 | Supply, installation, testing and commissioning of 63 amps 4 pole MCB in 1..6 mm thick MS enclosure of approved make design and painted with approved paint shade. (for Inverter) | [8 empty] | Nos. | 2 | 1497.045 | 0 | 1497.045 | 112.3233 | 0 | 1609.3683 | 189.9 | 23.4716 | 0 | 213.3716 | 3218.7366 | 426.7433 | 3645
40 | 303000000 | Supply, installation, testing and commissioning of 63 amps 4P ELMCB of 300 mA leakage current suitable for AC3VF elevator drive in 1.6 mm thick CRCA sheet steel enclosure of approved make design and painted with approved paint shade. ( FOR SERVICE & GUEST ELEVATOR) | [8 empty] | Nos. | 6 | 2545.715 | 0 | 2545.715 | 191.005 | 0 | 2736.72 | 189.9 | 23.4716 | 0 | 213.3716 | 16420.32 | 1280.2298 | 17701
41 | 303000000 | Supply, installation, testing and commissioning of 63 amps 4 pole MCB in 1.6 mm thick CRCA sheet steel enclosure of approved make design and painted with approved paint shade. ( FOR DIMMER DB) | [8 empty] | Nos. | 10 | 1497.045 | 0 | 1497.045 | 112.3233 | 0 | 1609.3683 | 189.9 | 23.4716 | 0 | 213.3716 | 16093.6829 | 2133.7164 | 18227
42 | 303000000 | Supply, installation, testing and commissioning of 40 amps DP MCB in 1.6 mm thick CRCA sheet steel enclosure of approved make design and painted with approved paint shade. ( FOR DIMMER DB) | [8 empty] | Nos. | 2 | 891.475 | 0 | 891.475 | 66.8874 | 0 | 958.3624 | 189.9 | 23.4716 | 0 | 213.3716 | 1916.7247 | 426.7433 | 2343
42 | 303000000 | Supply, installation, testing and commissioning of 63 amps 4 pole Isolator MCB in IP 65 polycarbonate enclosure of approved make design. ( FOR Kitchen power equipment) | [8 empty] | Nos. | 6 | 1824.095 | 0 | 1824.095 | 136.8618 | 0 | 1960.9568 | 189.9 | 23.4716 | 0 | 213.3716 | 11765.7411 | 1280.2298 | 13046
43 | 303000000 | Supply, installation, testing and commissioning of following dry type step down transformer having safety isolating transformer confirming to BS 3535 in 1.6 mm thick MS enclosure of approved make and design. Input voltage 240 volts + 10% and multiple output voltage of 12/14/16 volts (for external & swimming pool lighting) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
43.1 | 303000000 | 250 VA | [8 empty] | Nos. | 5 | 1953.86 | 0 | 1953.86 | 146.5981 | 0 | 2100.4581 | 316.5 | 39.1194 | 0 | 355.6194 | 10502.2906 | 1778.097 | 12280
43.2 | 303000000 | 500 VA | [8 empty] | Nos. | 4 | 3252.565 | 0 | 3252.565 | 244.04 | 0 | 3496.605 | 316.5 | 39.1194 | 0 | 355.6194 | 13986.4198 | 1422.4776 | 15409
43.3 | 303000000 | 750 VA | [8 empty] | Nos. | 3 | 5201.15 | 0 | 5201.15 | 390.2423 | 0 | 5591.3923 | 316.5 | 39.1194 | 0 | 355.6194 | 16774.1769 | 1066.8582 | 17841
43.4 | 303000000 | 1000 VA | [8 empty] | Nos. | 2 | 6499.855 | 0 | 6499.855 | 487.6841 | 0 | 6987.5391 | 316.5 | 39.1194 | 0 | 355.6194 | 13975.0782 | 711.2388 | 14686
44 | 303000000 | Supply and fixing in position 1000 mm wide rubber matting of 1100 volts grade as per IS-15652:2006 (exact length of rubber mat to be worked out as per site requirement). | [8 empty] | RM | 110 | 1820 | 0 | 1820 | 136.5546 | 0 | 1956.5546 | 76 | 9.3936 | 0 | 85.3936 | 215221.006 | 9393.296 | 224614
E. | 303000000 | CAPACITOR BANKS WITH DETUNED FILTER IN AUTOMATIC CONTROL UNITS | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Design, fabrication, assembling, wiring, supply, installation, testing and commissioning of Automatic control panels with MPP type capacitors, fabricated out of 14 gauge CRCA sheet steel in cubicle compartmentised, free standing, floor mounted, dust and vermin proof with reinforcement of suitable size, angle iron, channel, T sections and / or flats wherever necessary. Cable gland plates shall be provided on top as well as at the bottom of the panels. Panels shall be treated with all anticorrosive process before powder coating as per specifications and final approved shade. 2 Nos. earthing terminals shall be provided for all distrtibution panels. Panels shall be suitable for 415V, 3 phase, 4 wire, 50 HZ supply system. Lifting hooks shall also be provided in case of large panels. Approval shall be taken for each panel in the form of shop drawings before fabrication. Galvanised hardwares with zinc passivation shall be used in fabrication of panels. The system shall be provided with | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | [9 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | It shall provide rated 300 KVAR in suitable nos. of steps & of suitable rating of capacitors (minimum 8 steps up to 250 kVAR and 12 steps for above 250 kVAR bank), as per specification. The panel shall also comply with following : | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 303000000 | 630 Amps TPN MCCB incomer with 25 KA breaking capacity to be provided : | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 303000000 | Microprocessor APFC controller shall continuously monitor all three phases and displays various Electrical Parameters like voltage, input current, capacitive current, KVA demand,KW, Power Factor, self diagnostic error code indication with printout facility of the above with RS 232C/485 port. Controller should mounted on the front side of the panel. It shall have data logging for minimum 2 months, it shall provide thyristor output for maximum 16 stages. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 303000000 | Fast response time of ON capacitors 20-60 miliseconds. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 303000000 | Super fast electronic fuse and links of the proper rating to be used for grouping the capacitor banks. Capacitor shall be connected with fast discharge resistances. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 303000000 | Thyristor having suitable capacity to carry expected current continuosly. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 303000000 | Necessary control and firing card with proper wiring and lugs of the required rating to be provided. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 303000000 | Heavy duty exhaust fans to be provided for cooling Thyristors. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 303000000 | LED indication for number of capacitor banks ON. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 303000000 | LED indication of Power Factor lagging or leading. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 303000000 | Auto/manual selector switch with necessary wiring to operate APFC panel in manual mode bypassing APFC relay. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 303000000 | The APFC system shall be provided with following : | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Protections : | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
a. | 303000000 | Over voltage. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
b. | 303000000 | Voltage imbalance. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
c. | 303000000 | Over temperature-system should be in standby mode and automatically restart after above condition restored. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
d. | 303000000 | Total Harmonic Distortion | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 303000000 | 7% value series reactor with iron core | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 303000000 | Capacitor Units shall have 525 V and rating shall be suitably increased considering reactors into account. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Capacitor automatic control panel ( 300 KVAR) as described above. | [8 empty] | Sets | 2 | 711034.13 | 0 | 711034.13 | 53348.8908 | 0 | 764383.0208 | 31650 | 3911.94 | 0 | 35561.94 | 1528766.0415 | 71123.88 | 1599890
| 303000000 | Note: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Total watt-losses excluding discharge resistors shall be lessthan or equal to 0.45 W / kVAr for MPP capacitors. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Test certificate shall be provided confirming the watt-loss/KVAR | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
F. | 303000000 | EARTHING INSTALLATION (FOR POWER DISTRIBUTION SYSTEMS, UPS SYSTEM, DG SETS & EPABX | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 303000000 | Supply and fixing of following bare copper /GI tapes / wires including all necessary fixing accessories and effecting connections as per specifications. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.1 | 303000000 | 50 x 6 mm thick GI tape. | [8 empty] | RM | 850 | 182.515 | 0 | 182.515 | 13.6941 | 0 | 196.2091 | 69.63 | 8.6063 | 0 | 78.2363 | 166777.7354 | 66500.8278 | 233279
1.2 | 303000000 | 32 x 6 mm thick GI tape. | [8 empty] | RM | 80 | 129.765 | 0 | 129.765 | 9.7363 | 0 | 139.5013 | 56.97 | 7.0415 | 0 | 64.0115 | 11160.1014 | 5120.9194 | 16281
1.3 | 303000000 | 25 x 6 mm thick GI tape. | [8 empty] | RM | 300 | 90.73 | 0 | 90.73 | 6.8075 | 0 | 97.5375 | 40.09 | 4.9551 | 0 | 45.0451 | 29261.2416 | 13513.5372 | 42775
1.3 | 303000000 | 25 x 6 mm thick copper tape. | [8 empty] | RM | 25 | 947.39 | 0 | 947.39 | 71.0827 | 0 | 1018.4727 | 37.98 | 4.6943 | 0 | 42.6743 | 25461.8168 | 1066.8582 | 26529
1.4 | 303000000 | 25 x 3 mm thick GI tape. | [8 empty] | RM | 100 | 51.695 | 0 | 51.695 | 3.8787 | 0 | 55.5737 | 31.65 | 3.9119 | 0 | 35.5619 | 5557.3676 | 3556.194 | 9114
1.4 | 303000000 | 15 x 3 mm thick GI tape. | [8 empty] | RM | 650 | 28.485 | 0 | 28.485 | 2.1372 | 0 | 30.6222 | 27.43 | 3.3903 | 0 | 30.8203 | 19904.4492 | 20033.2262 | 39938
1.5 | 303000000 | 8 SWG GI wire | [8 empty] | RM | 300 | 10.55 | 0 | 10.55 | 0.79157 | 0 | 11.3416 | 4.22 | 0.52159 | 0 | 4.7416 | 3402.47 | 1422.4776 | 4825
2 | 303000000 | Providing and laying of 600 x 600 x 3.15 mm thick tined copper plate electrode, with 2 Nos 50 x 6 mm copper strips from earth plate electrode to inspection chamber, 50 mm dia medium class GI pipe, CI funnel with 20 gauge GI wire mesh, masonry chamber 1000 x 500 mm with concrete base C I heavy duty / chequered plate manhole cover with frame painted with bitumastic paint and packing with mixture of charcoal and common salt around plate electrode including digging of pit upto permanent moisture level and as per soil condition but not less than 3 meters and back filling as required. (For ups& DG neutral earthing) | [8 empty] | No. | 6 | 26583.89 | 0 | 26583.89 | 1994.5893 | 0 | 28578.4793 | 3165 | 391.194 | 0 | 3556.194 | 171470.8756 | 21337.164 | 192808
3 | 303000000 | Providing and laying of 600 x 600 x 6.3 mm thick GI plate electrode, with 2 nos. 50 X 6 mm GI strips from earth plate electrode to inspection chamber, 50 mm dia medium class GI pipe, CI funnel with 20 gauge GI wire mesh, masonry chamber 1000 X 500 mm with concrete base CI manhole cover with frame painted with bitumastic paint and packing with mixture of charcoal and common salt around plate electrode including digging of pit upto permanent moisture level but not less than 3 meters and back filling as required. | [8 empty] | No. | 16 | 9573.07 | 0 | 9573.07 | 718.2674 | 0 | 10291.3374 | 2658.6 | 328.603 | 0 | 2987.203 | 164661.3991 | 47795.2474 | 212457
4 | 303000000 | Supply and laying of following 1100 volts grade PVC insulated sheathed copper conductor unarmoured cable including copper thimbles, fixing hardware as required. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4.1 | 303000000 | Single core 35 sq.mm Green colour cable | [8 empty] | RM | 175 | 294.345 | 0 | 294.345 | 22.0847 | 0 | 316.4297 | 25.32 | 3.1296 | 0 | 28.4496 | 55375.1984 | 4978.6716 | 60354
5 | 303000000 | Supply and laying of GI pipe under road / paved area crossing etc. including excavation back filling ramming and making good. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.1 | 303000000 | 50 mm dia pipe. | [8 empty] | RM | 25 | 468.42 | 0 | 468.42 | 35.1456 | 0 | 503.5656 | 94.95 | 11.7358 | 0 | 106.6858 | 12589.1388 | 2667.1455 | 15256
5.2 | 303000000 | 100 mm dia pipe. | [8 empty] | RM | 25 | 1113.025 | 0 | 1113.025 | 83.5103 | 0 | 1196.5353 | 120.27 | 14.8654 | 0 | 135.1354 | 29913.3816 | 3378.3843 | 33292
6 | 303000000 | Supply and installation of 50 x 6 mm Cu busbar mounted on insulators and having 6 nos. holes for terminating single core 35 Sq.mm flexible cable with the entire assembly enclosed in 1.6 mm thick MS enclosure of approved make, design & painted with approved paint shade. (for UPS/low volt earthing and installed in electrical shaft). | [8 empty] | Nos. | 1 | 5207.48 | 0 | 5207.48 | 390.7172 | 0 | 5598.1972 | 633 | 78.2388 | 0 | 711.2388 | 5598.1972 | 711.2388 | 6309
G. | 303000000 | LIGHTING PROTECTION SYSTEM | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | (Based on New Zealand Standards) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 303000000 | Supply and fixing of following Erico LPI or equivalent make enhanced air terminals as per specifications. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.1 | 303000000 | Dynasphere terminal – stainless steel for hostile environment with necessary accessories like FRP mast with base, inlinr coupler, grips, fixing materials etc. complete as per specification. | [8 empty] | sets | 1 | 129997.1 | 0 | 129997.1 | 9753.6824 | 0 | 139750.7824 | 6330 | 782.388 | 0 | 7112.388 | 139750.7824 | 7112.388 | 146863
1.2 | 303000000 | Supply and fixing of 25x3mm bare GI tapes down conductor including all necessary fixing accessories and effecting connections as per specifications. | [8 empty] | Mtrs. | 180 | 51.695 | 0 | 51.695 | 3.8787 | 0 | 55.5737 | 50.64 | 6.2591 | 0 | 56.8991 | 10003.2617 | 10241.8387 | 20245
1.3 | 303000000 | Providing and laying of 600 x 600 x 6.3 mm thick GI electrode, with 2 nos. 50 X 6 mm GI strips from earth electrode to inspection chamber, 50 mm dia medium class GI pipe, CI funnel with 20 gauge GI wire mesh, masonry chamber 1000 X 500 mm with concrete base CI manhole cover with frame painted with bitumastic paint and packing with mixture of charocoal and common salt around plate electrode including digging of pit upto permanent moisture level but not less than 3 meters and back filling as required.. | [8 empty] | Nos. | 2 | 9080.385 | 0 | 9080.385 | 681.3013 | 0 | 9761.6863 | 2532 | 312.9552 | 0 | 2844.9552 | 19523.3726 | 5689.9104 | 25213
1.4 | 303000000 | Supply and laying of medium class GI pipe under road / paved area crossing etc. including excavation back filling ramming and making good (depth of excavation shall be minimum 750 mm). | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.4.1 | 303000000 | 75 mm dia pipe | [8 empty] | RM | 25 | 781.755 | 0 | 781.755 | 58.6551 | 0 | 840.4101 | 113.94 | 14.083 | 0 | 128.023 | 21010.2519 | 3200.5746 | 24211
1.5 | 303000000 | Providing and fixing of lightning event counter MK4 model No-LEC-IV as per specification | [8 empty] | Nos. | 1 | 15850.32 | 0 | 15850.32 | 1189.2495 | 0 | 17039.5695 | 316.5 | 39.1194 | 0 | 355.6194 | 17039.5695 | 355.6194 | 17395
1.6 | 303000000 | Providing and fixing of test link in weather proof 1.6 mm thick MS box of approved make & design | [8 empty] | Nos. | 1 | 2343.155 | 0 | 2343.155 | 175.8069 | 0 | 2518.9619 | 316.5 | 39.1194 | 0 | 355.6194 | 2518.9619 | 355.6194 | 2875
H. | 303000000 | SUPPLY & INSTALLATION OF LIGHTING FIXTURES | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Supply of the following lighting fixtures with all fixing accessories etc. as required. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 303000000 | Fluorescent lighting fixture Philips TCS 669/228 HF or approved equal in quality and design complete with T5 fluorescent lamp. (For office ltg) | [8 empty] | Nos. | 5 | 3511.04 | 0 | 3511.04 | 263.4333 | 0 | 3774.4733 | 0 | 0 | 0 | 0 | 18872.3667 | 0 | 18872
2 | 303000000 | Fluorescent lighting fixture Philips TBS 669/414 D6 HF or approved equal in quality and design complete with T5 fluorescent lamp. (For office ltg) | [8 empty] | Nos. | 130 | 3718.875 | 0 | 3718.875 | 279.0272 | 0 | 3997.9022 | 0 | 0 | 0 | 0 | 519727.2849 | 0 | 519727
3 | 303000000 | Fluorescent lighting fixture Philips TBS 570/414 HF ODF-WH or approved equal in quality and design complete with T5 fluorescent lamp. (For office ltg) | [8 empty] | Nos. | 15 | 4192.57 | 0 | 4192.57 | 314.5685 | 0 | 4507.1385 | 0 | 0 | 0 | 0 | 67607.0779 | 0 | 67607
4 | 303000000 | Fluorescent lighting fixture Philips TBS 520/228 MI HF or approved equal in quality and design complete with T5 fluorescent lamp. (For store areas) | [8 empty] | Nos. | 85 | 1718.595 | 0 | 1718.595 | 128.9462 | 0 | 1847.5412 | 0 | 0 | 0 | 0 | 157041.0005 | 0 | 157041
5 | 303000000 | T5 Fluorescent lighting fixture Philips TMS 122/128 HF or approved equal in quality and design complete with T5 fluorescent lamp. (For plant room, carpark , Electrical room, staircase) | [8 empty] | Nos. | 275 | 932.62 | 0 | 932.62 | 69.9745 | 0 | 1002.5945 | 0 | 0 | 0 | 0 | 275713.4816 | 0 | 275713
6 | 303000000 | T5 Fluorescent lighting fixture Philips TMS 122/228 HF or approved equal in quality and design complete with T5 fluorescent lamp. (For plant room, carpark , Electrical room, staircase) | [8 empty] | Nos. | 225 | 1251.23 | 0 | 1251.23 | 93.8798 | 0 | 1345.1098 | 0 | 0 | 0 | 0 | 302649.7021 | 0 | 302650
7 | 303000000 | Fluorescent lighting fixture Philips TBS 670 2X36 W TL-DEB BOCA or approved equal in quality and design complete with fluorescent lamp. (For Kitchen & Laundry) | [8 empty] | Nos. | 36 | 5674.845 | 0 | 5674.845 | 425.7836 | 0 | 6100.6286 | 0 | 0 | 0 | 0 | 219622.6303 | 0 | 219623
8 | 303000000 | Fluorescent lighting fixture Philips FBS 650 2X36 W PL-EB BOCA HF or approved equal in quality and design complete with PL lamp. (For Kitchen ) | [8 empty] | Nos. | 125 | 5570.4 | 0 | 5570.4 | 417.9471 | 0 | 5988.3471 | 0 | 0 | 0 | 0 | 748543.389 | 0 | 748543
9 | 303000000 | Fluorescent lighting fixture Philips TCW 450 128 W HF or approved equal in quality and design complete with T5 lamp. (For service & terrace floor ) | [8 empty] | Nos. | 30 | 1983.4 | 0 | 1983.4 | 148.8145 | 0 | 2132.2145 | 0 | 0 | 0 | 0 | 63966.4351 | 0 | 63966
10 | 303000000 | Fluorescent lighting fixture Philips TCW 450 228 W HF or approved equal in quality and design complete with T5 lamp. | [8 empty] | Nos. | 5 | 2446.545 | 0 | 2446.545 | 183.5643 | 0 | 2630.1093 | 0 | 0 | 0 | 0 | 13150.5464 | 0 | 13151
11 | 303000000 | Recessed step light fixture Philips DBP 701/2xPLC 18 Watt CFL or approved equal in quality and design (Ramp Lighting) | [8 empty] | Nos. | 15 | 12460.605 | 0 | 12460.605 | 934.9192 | 0 | 13395.5242 | 0 | 0 | 0 | 0 | 200932.8629 | 0 | 200933
12 | 303000000 | Wall mounting luminaire complete with all accessories Philips Cat No. FMS 300 /111 HF with1x PL-S 11 watt or approved equal in quality and design complete with lamp. (Toilet Mirror ltg.) | [8 empty] | Nos. | 10 | 526.445 | 0 | 526.445 | 39.4992 | 0 | 565.9442 | 0 | 0 | 0 | 0 | 5659.4417 | 0 | 5659
13 | 303000000 | Recessed compact fluorescent Philips Cat No. FBH 150 //218 T HF with 2 x PLC-18 watt CFL or approved equal in quality and design. | [8 empty] | Nos. | 345 | 1269.165 | 0 | 1269.165 | 95.2254 | 0 | 1364.3904 | 0 | 0 | 0 | 0 | 470714.7052 | 0 | 470715
14 | 303000000 | Recessed compact fluorescent Philips Cat No. FBH 150 //118 T HF with 1 x PLC-18 watt CFL or approved equal in quality and design. | [8 empty] | Nos. | 45 | 853.495 | 0 | 853.495 | 64.0377 | 0 | 917.5327 | 0 | 0 | 0 | 0 | 41288.9728 | 0 | 41289
16 | 303000000 | Recessed 14.6 watt LED light fixture Philips type no. BBS 175 or approved equal in quality and design. | [8 empty] | Nos. | 220 | 1870.515 | 0 | 1870.515 | 140.3447 | 0 | 2010.8597 | 0 | 0 | 0 | 0 | 442389.1429 | 0 | 442389
| 303000000 | BBS 175 1XDLED-5000 PSU WH PHILIPS MAKE CONSIDERED | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 303000000 | Recessed 7 watt LED light fixture Philips type no. GU10-230V or approved equal in quality and design. | [8 empty] | Nos. | 15 | 1490.715 | 0 | 1490.715 | 111.8483 | 0 | 1602.5633 | 0 | 0 | 0 | 0 | 24038.4502 | 0 | 24038
| 303000000 | QBSO27 1XMAX50 W/12V GU5.3WH WITH 7W GU10CONSIDERD | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 303000000 | Bulk head lighting fixtures Philips make FXC-101 or approved equal in quality and design with 9 watt PL lamps. (Lift Shaft & guest room shaft Ltg.) | [8 empty] | Nos. | 375 | 680.475 | 0 | 680.475 | 51.056 | 0 | 731.531 | 0 | 0 | 0 | 0 | 274324.1397 | 0 | 274324
19 | 303000000 | Self contained single sided exit sign for wall / ceiling / pendant cantilever mounting with 9 W CFL tube for non maintained battery backup emergency lighting for 3 hours duration Thorn EXB3, Prolite make or approved equal in quality and design. | [8 empty] | Nos. | 35 | 4091.29 | 0 | 4091.29 | 306.9695 | 0 | 4398.2595 | 0 | 0 | 0 | 0 | 153939.0821 | 0 | 153939
20 | 303000000 | Self contained double sided exit single for wall / ceiling / pendant cantilever mounting with 9 watt CFL tube, non maintained battery backup 3 hours duration Thorn EXB3, Prolite make or approved equal in quality and design. | [8 empty] | Nos. | 40 | 4791.81 | 0 | 4791.81 | 359.5295 | 0 | 5151.3395 | 0 | 0 | 0 | 0 | 206053.5802 | 0 | 206054
21 | 303000000 | Aviation obstruction light with Light Emitting Diods (LEDs) with photochromatic switch Complete with all accessories as approved. | [8 empty] | Nos. | 1 | 3883.455 | 0 | 3883.455 | 291.3756 | 0 | 4174.8306 | 0 | 0 | 0 | 0 | 4174.8306 | 0 | 4175
| 303000000 | XGP400 1XLED-K2/RD PHILIPD CONSIDERED | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 303000000 | 48" dia sweep ceiling fan with step type fan regulator of approved make complete with all accessories. | [8 empty] | Nos. | 10 | 1947.53 | 0 | 1947.53 | 146.1232 | 0 | 2093.6532 | 0 | 0 | 0 | 0 | 20936.5318 | 0 | 20937
23 | 303000000 | Supply & installation of ON/OFF type occupancy sensors wipro COP 11010 OR equivalent with 360 degree coverage , with built in switch/relay & foot print diameter of 6-8 metres for installation in toilet blocks. | [8 empty] | Nos. | 50 | 3588.055 | 0 | 3588.055 | 269.2118 | 0 | 3857.2668 | 0 | 0 | 0 | 0 | 192863.3383 | 0 | 192863
I. | 303000000 | INSTALLATION OF LIGHTING FIXTURES | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Installation of the following lighting fixtures with all fixing accessories etc. as required. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 303000000 | Fluorescent lighting fixture Philips TCS 669/228 HF or approved equal in quality and design complete with T5 fluorescent lamp. | [8 empty] | Nos. | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 103.39 | 12.779 | 0 | 116.169 | 0 | 1742.5351 | 1743
2 | 303000000 | Fluorescent lighting fixture Philips TBS 669/414 D6 HF or approved equal in quality and design complete with T5 fluorescent lamp. | [8 empty] | Nos. | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 103.39 | 12.779 | 0 | 116.169 | 0 | 5111.4362 | 5111
3 | 303000000 | T5 Fluorescent lighting fixture Philips TMS 122/128 HF or approved equal in quality and design complete with T5 fluorescent lamp. (For cove lighting) | [8 empty] | Nos. | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 103.39 | 12.779 | 0 | 116.169 | 0 | 2904.2251 | 2904
4 | 303000000 | Recessed compact fluorescent Philips Cat No. FBH 150 //218 T HF with 2 x PLC-18 watt CFL or approved equal in quality and design. | [8 empty] | Nos. | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 128.71 | 15.9086 | 0 | 144.6186 | 0 | 2169.2783 | 2169
5 | 303000000 | Recessed compact fluorescent Philips Cat No. FBH 150 //118 T HF with 1 x PLC-18 watt CFL or approved equal in quality and design. | [8 empty] | Nos. | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 128.71 | 15.9086 | 0 | 144.6186 | 0 | 2169.2783 | 2169
6 | 303000000 | Recessed 15 watt LED light fixture Philips type no. BBS 181 or approved equal in quality and design. | [8 empty] | Nos. | 535 | 0 | 0 | 0 | 0 | 0 | 0 | 103.39 | 12.779 | 0 | 116.169 | 0 | 62150.4171 | 62150
7 | 303000000 | 50 watts 12 volts halogen down lighter with 220 /12 volts transformer and lamp Philips Cat No. DN-652 or approved equal in quality and design (Tentative) | [8 empty] | Nos. | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 194.12 | 23.9932 | 0 | 218.1132 | 0 | 10905.6616 | 10906
8 | 303000000 | Recessed mounted metal Halide Philips Cat No. MBS 050 / 70 or approved equal in quality and design with CDM-TP 70W/ 1x MHN- TD 70W (Tentative) | [8 empty] | Nos. | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 194.12 | 23.9932 | 0 | 218.1132 | 0 | 3271.6985 | 3272
9 | 303000000 | 1 meter low voltage track length for use with 12 V output Philips make or approved equal in quality and design | [8 empty] | Nos. | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 322.83 | 39.9018 | 0 | 362.7318 | 0 | 3627.3179 | 3627
10 | 303000000 | LV track adaptor for connecting LV spots to the track unit Philips make or approved equal in quality and design | [8 empty] | Nos. | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 258.475 | 31.9475 | 0 | 290.4225 | 0 | 8712.6753 | 8713
11 | 303000000 | 150 VA electronic transformer for LV track unit Philips make or approved equal in quality and design | [8 empty] | Nos. | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 258.475 | 31.9475 | 0 | 290.4225 | 0 | 2904.2251 | 2904
12 | 303000000 | Current supply end assembly for LV track unit Philips make or approved equal in quality and design | [8 empty] | Nos. | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 258.475 | 31.9475 | 0 | 290.4225 | 0 | 2904.2251 | 2904
13 | 303000000 | Chandelier of approved quality and design | [8 empty] | Nos. | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 645.66 | 79.8036 | 0 | 725.4636 | 0 | 6529.1722 | 6529
14 | 303000000 | LED strip light for cove lighting | [8 empty] | RM. | 748 | 0 | 0 | 0 | 0 | 0 | 0 | 103.39 | 12.779 | 0 | 116.169 | 0 | 86894.415 | 86894
| 303000000 | (Guest Room Ltg Fixture) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | 303000000 | Recessed 10 W LED downlight (L1) | [8 empty] | No. | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 103.39 | 12.779 | 0 | 116.169 | 0 | 46467.6016 | 46468
16 | 303000000 | Recessed 5W adjustable down light (L2) | [8 empty] | No. | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 103.39 | 12.779 | 0 | 116.169 | 0 | 46467.6016 | 46468
17 | 303000000 | Recessed 5W LED downlight (L3) | [8 empty] | No. | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 103.39 | 12.779 | 0 | 116.169 | 0 | 69701.4024 | 69701
18 | 303000000 | Recessed 7W Low Voltage dimmable down light (L4) | [8 empty] | No. | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 103.39 | 12.779 | 0 | 116.169 | 0 | 46467.6016 | 46468
19 | 303000000 | Recessed 7W Low Voltage down light (L5 steam proof) | [8 empty] | No. | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 103.39 | 12.779 | 0 | 116.169 | 0 | 23233.8008 | 23234
20 | 303000000 | Fluorescent T5 light fixture (L6 & L10) | [8 empty] | No. | 800 | 0 | 0 | 0 | 0 | 0 | 0 | 103.39 | 12.779 | 0 | 116.169 | 0 | 92935.2032 | 92935
21 | 303000000 | Under counter LED night light (L7) | [8 empty] | No. | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 103.39 | 12.779 | 0 | 116.169 | 0 | 46467.6016 | 46468
22 | 303000000 | Fluorescent T5 light fixture (L8) | [8 empty] | No. | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 103.39 | 12.779 | 0 | 116.169 | 0 | 23233.8008 | 23234
23 | 303000000 | Decorative bed side light fixture (L9) | [8 empty] | No. | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 103.39 | 12.779 | 0 | 116.169 | 0 | 46467.6016 | 46468
24 | 303000000 | Bed Head Wall light fixture (L11) | [8 empty] | No. | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 103.39 | 12.779 | 0 | 116.169 | 0 | 46467.6016 | 46468
25 | 303000000 | Recessed 3W LED down light (L13) | [8 empty] | No. | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 103.39 | 12.779 | 0 | 116.169 | 0 | 23233.8008 | 23234
26 | 303000000 | Low Voltage Desk light fixture (L14) | [8 empty] | No. | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 103.39 | 12.779 | 0 | 116.169 | 0 | 23233.8008 | 23234
27 | 303000000 | LED strip light 12w /mtr (L15) | [8 empty] | Mtr | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 103.39 | 12.779 | 0 | 116.169 | 0 | 69701.4024 | 69701
J. | 303000000 | INVERTER | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 303000000 | Inverter | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Supply & installation of 20 KVA inverter input 3 phase (415 V + 10%) output 3 phase (415 V + 10%) with sealed maintenance free batteries suitable for 15 minutes backup including providing suitable size of 14 gauge MS battery rack suitably painted.. | [8 empty] | Set | 1 | 370257.525 | 0 | 370257.525 | 27780.4221 | 0 | 398037.9471 | 6330 | 782.388 | 0 | 7112.388 | 398037.9471 | 7112.388 | 405150
K. | 303000000 | HV INSTALLATION | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
I | 303000000 | SUPPLY AND INSTALLATION OF SUB-STATION EQUIPMENT | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 303000000 | Supply, installation, testing and commissioning of 11 KV SF6 insulated compact HT panel consisting of 1 Nos. incoming isolator switch and 2 nos. outgoing 630 Amps 25 KA for 1 sec. motorized Vacuum circuit breaker as per feeder details given in the specification and single line diagram. | [8 empty] | Set | 1 | 948967.225 | 0 | 948967.225 | 71201.0109 | 0 | 1020168.2359 | 45576 | 5633.1936 | 0 | 51209.1936 | 1020168.2359 | 51209.1936 | 1071377
2 | 303000000 | Supply, installation, testing and commissioning of 1000 KVA capacity 11/ 0.433 KV, Z= 5 % step down oil cooled transformers with ON load tap changer(OLTC) on HV side, and with surge Arrestor and surge counter on HV side as per specification. | [8 empty] | No. | 2 | 1387025.38 | 0 | 1387025.38 | 104068.5143 | 0 | 1491093.8943 | 37980 | 4694.328 | 0 | 42674.328 | 2982187.7885 | 85348.656 | 3067536
3 | 303000000 | Supply, installation, testing and commissioning of 200 AH capacity 24 volts DC hermetically sealed maintenance free lead acid batteries duly charged. | [8 empty] | Set | 1 | 31181.58 | 0 | 31181.58 | 2339.5539 | 0 | 33521.1339 | 633 | 78.2388 | 0 | 711.2388 | 33521.1339 | 711.2388 | 34232
4 | 303000000 | Supply, installation, testing and commissioning of battery charger unit with provisions of Boost Charing, and Float charging. Suitable for 240 V single phase + 10% AC, 50 Hz power supply as per specifications. | [8 empty] | Set | 1 | 51987.235 | 0 | 51987.235 | 3900.6022 | 0 | 55887.8372 | 1899 | 234.7164 | 0 | 2133.7164 | 55887.8372 | 2133.7164 | 58022
5 | 303000000 | Supply and fixing in position the approved “Shock Treatment Charts” written in English and Local Language. These charts shall be framed in teak wood frame and covered with glass. | [8 empty] | No. | 1 | 974.82 | 0 | 974.82 | 73.1407 | 0 | 1047.9607 | 63.3 | 7.8239 | 0 | 71.1239 | 1047.9607 | 71.1239 | 1119
6 | 303000000 | Supply and fixing in position the fire extinguishers carbon-di-odide type 2.5 Kgs capacity. | [8 empty] | No. | 2 | 3248.345 | 0 | 3248.345 | 243.7233 | 0 | 3492.0683 | 63.3 | 7.8239 | 0 | 71.1239 | 6984.1367 | 142.2478 | 7126
7 | 303000000 | Supply and fixing in position the best quality Danger Boards of approved shape and size as specified by Local Electricity Authorities written in English & Local Languages. | [8 empty] | No. | 2 | 325.995 | 0 | 325.995 | 24.4594 | 0 | 350.4544 | 63.3 | 7.8239 | 0 | 71.1239 | 700.9088 | 142.2478 | 843
8 | 303000000 | Supply and fixing in position 1000 mm wide rubber matting of 11 KV grade as per electricity rules. | [8 empty] | RM | 10 | 1948.585 | 0 | 1948.585 | 146.2023 | 0 | 2094.7873 | 63.3 | 7.8239 | 0 | 71.1239 | 20947.8733 | 711.2388 | 21659
9 | 303000000 | Supply of fire buckets 5 nos. in each set duly filled with fine sand and fixed on an angle iron frame as per requirement of local authorities. Fire buckets shall be painted red from outside and white from inside with additional handle at the bottom. | [8 empty] | Sets | 1 | 6499.855 | 0 | 6499.855 | 487.6841 | 0 | 6987.5391 | 316.5 | 39.1194 | 0 | 355.6194 | 6987.5391 | 355.6194 | 7343
10 | 303000000 | Supply and fixing in position the approved single line diagram framed in 1000 x 800 mm size glass frame in the sub station. | [8 empty] | No. | 2 | 1948.585 | 0 | 1948.585 | 146.2023 | 0 | 2094.7873 | 63.3 | 7.8239 | 0 | 71.1239 | 4189.5747 | 142.2478 | 4332
11 | 303000000 | Supply of first aid box of approved make as per specification. | [8 empty] | No. | 1 | 1948.585 | 0 | 1948.585 | 146.2023 | 0 | 2094.7873 | 63.3 | 7.8239 | 0 | 71.1239 | 2094.7873 | 71.1239 | 2166
12 | 303000000 | Supply of tool kit with 1 pair 12 KV rubber hand gloves of approved make. | [8 empty] | No. | 2 | 974.82 | 0 | 974.82 | 73.1407 | 0 | 1047.9607 | 63.3 | 7.8239 | 0 | 71.1239 | 2095.9215 | 142.2478 | 2238
| 303000000 | TOTAL CARRIED TO SUMMARY | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
II | 303000000 | HT CABLES & LT CONTROL CABLES | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 303000000 | Supplying and laying following size 11 KV grade XLPE (E) aluminium conductor armoured cables laid over MS supports in existing trenches. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.1 | 303000000 | 3 C x 240 sq.mm 11 KV XLPE cable (between metering panel room to HT panel and HT panel to transformers). | [8 empty] | RM | 100 | 1116.19 | 0 | 1116.19 | 83.7477 | 0 | 1199.9377 | 126.6 | 15.6478 | 0 | 142.2478 | 119993.7736 | 14224.776 | 134219
2 | 303000000 | Supplying and making cable end terminations for the following size of 11 KV grade, XLPE aluminium conductor armoured cable including termination kit complete heat shrinkable sleeve etc. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.1 | 303000000 | 3 C x 240 sq.mm 11 KV XLPE cable (indoor) | [8 empty] | Nos. | 4 | 5041.845 | 0 | 5041.845 | 378.2896 | 0 | 5420.1346 | 2532 | 312.9552 | 0 | 2844.9552 | 21680.5385 | 11379.8208 | 33060
2.2 | 303000000 | 3 C x 240 sq.mm 11 KV XLPE cable (outdoor) | [8 empty] | Nos. | 2 | 7827.045 | 0 | 7827.045 | 587.2632 | 0 | 8414.3082 | 2785.2 | 344.2507 | 0 | 3129.4507 | 16828.6164 | 6258.9014 | 23088
3 | 303000000 | Supplying, laying GI sleeves of following sizes: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.1 | 303000000 | 150 mm dia | [8 empty] | RM | 0 | 1749.19 | 0 | 1749.19 | 131.2417 | 0 | 1880.4317 | 151.92 | 18.7773 | 0 | 170.6973 | 0 | 0 | 0
3.2 | 303000000 | 200 mm dia | [8 empty] | RM | 15 | 2216.555 | 0 | 2216.555 | 166.3081 | 0 | 2382.8631 | 189.9 | 23.4716 | 0 | 213.3716 | 35742.9468 | 3200.5746 | 38944
4 | 303000000 | Supplying and laying of following 1100 volts grade PVC insulated sheathed copper conductor armoured control cables in existing trenches cables trays, clamped on wall with suitable saddles, fixing bolts, including testing and commissioning. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4.1 | 303000000 | 12 Core 2.5 sq mm PVC insulated copper conductor armoured control cables | [8 empty] | RM | 50 | 281.685 | 0 | 281.685 | 21.1348 | 0 | 302.8198 | 31.65 | 3.9119 | 0 | 35.5619 | 15140.9913 | 1778.097 | 16919
5 | 303000000 | Cable end termination of the following PVC insulated sheathed aluminium conductor armoured cables of 1100 volt grade including supplying and fixing of crimping lugs. Double compression glands with earthing provision and cable sockets | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.1 | 303000000 | 12 Core 2.5 sq.mm Control cable | [8 empty] | Nos. | 4 | 294.345 | 0 | 294.345 | 22.0847 | 0 | 316.4297 | 189.9 | 23.4716 | 0 | 213.3716 | 1265.7188 | 853.4866 | 2119
III | 303000000 | EARTHING FOR SUB-STATION EQUIPMENT | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 303000000 | Supplying and fixing of following bare copper / GI tapes including all necessary fixing accessories and effecting connections. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.1 | 303000000 | 50 x 8 mm thick GI tape. (For Transformer body earthing & LT breaker panel on Ground floor) | [8 empty] | RM | 250 | 251.09 | 0 | 251.09 | 18.8393 | 0 | 269.9293 | 88.62 | 10.9534 | 0 | 99.5734 | 67482.3207 | 24893.358 | 92376
1.2 | 303000000 | 50 x 6 mm thick copper tape. (For Neutral earthing of Transformer & DG) | [8 empty] | RM | 300 | 1895.835 | 0 | 1895.835 | 142.2445 | 0 | 2038.0795 | 82.29 | 10.171 | 0 | 92.461 | 611423.85 | 27738.3132 | 639162
1.3 | 303000000 | 25 mm x 6 mm thick copper tape. | [8 empty] | RM | 25 | 948.445 | 0 | 948.445 | 71.1618 | 0 | 1019.6068 | 50.64 | 6.2591 | 0 | 56.8991 | 25490.1707 | 1422.4776 | 26913
2 | 303000000 | Providing earthing stations at locations as called for including providing and laying 600 x 600 x 3.15 mm thick tinned copper electrode with 2 Nos 50 x 6 mm thick copper strip, from earth electrode to inspection chamber,50 mm dia medium class G I pipe CI / chequered plate funnel with 20 gauge G I wire mesh, masonry chamber 1000 x 500 mm with concrete base, CI chequered plate manhole cover with frame and bitumastic paint and packing of mixture of charcoal and common salt around plate electrode complete with digging of pit upto permanent misture level but not less than 3 metres and back filling as required. (For transformer Neutral Earthing) | [8 empty] | Nos. | 4 | 26583.89 | 0 | 26583.89 | 1994.5893 | 0 | 28578.4793 | 3165 | 391.194 | 0 | 3556.194 | 114313.9171 | 14224.776 | 128539
3 | 303000000 | Providing earthing stations at locations as called for including providing and laying 600 x 600 x 6.3 mm GI electrode with 2 Nos. 50 x 6 mm thick GI stripe, from earth electrode to inspection chamber,50 mm dia medium class G I pipe CI / chequered plate funnel with 20 gauge G I wire mesh, masonry chamber 1000 x 500 mm with concrete base, CI chequered plate manhole cover with frame and bitumastic paint and packing of mixture of charcoal and common salt around plate electrode complete with digging of pit upto permanent misture level but not less than 3 metres and back filling as required. (For HT panel client & supply company, Transformer body earthing) | [8 empty] | No. | 8 | 9573.07 | 0 | 9573.07 | 718.2674 | 0 | 10291.3374 | 2658.6 | 328.603 | 0 | 2987.203 | 82330.6995 | 23897.6237 | 106228
4 | 303000000 | Supply and laying medium class GI pipe under road/paved areas/wall crossing etc. including earth excavations refilling, ramming and making good as approved. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4.1 | 303000000 | 150 mm dia GI pipe | [8 empty] | RM | 25 | 1750.245 | 0 | 1750.245 | 131.3209 | 0 | 1881.5659 | 189.9 | 23.4716 | 0 | 213.3716 | 47039.1471 | 5334.291 | 52373
L. | 303000000 | CABLING AND INSTALLATION OF LIGHTING FIXTURE FOR EXTERNAL / LANDSCAPE LIGHTING | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 303000000 | Receiving, storing handling, installing, testing and commissioning of the following lighting fixtures and poles including excavation and back filling, foundation of pole, base plate as required. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.1 | 303000000 | Recessed uplight fixture | [8 empty] | No. | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 194.12 | 23.9932 | 0 | 218.1132 | 0 | 5452.8308 | 5453
1.2 | 303000000 | Recessed underwater light | [8 empty] | No. | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 194.12 | 23.9932 | 0 | 218.1132 | 0 | 2181.1323 | 2181
1.3 | 303000000 | Bollard | [8 empty] | No. | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 103.39 | 12.779 | 0 | 116.169 | 0 | 580.845 | 581
1.4 | 303000000 | Post top lantern | [9 empty] | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 103.39 | 12.779 | 0 | 116.169 | 0 | 697.014 | 697
1.5 | 303000000 | 1 x 50 W in ground low voltage tree uplight | [8 empty] | No. | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 103.39 | 12.779 | 0 | 116.169 | 0 | 1742.5351 | 1743
1.6 | 303000000 | 70 W wallmounted up down light fixtures | [8 empty] | No. | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 103.39 | 12.779 | 0 | 116.169 | 0 | 580.845 | 581
1.7 | 303000000 | 150 / 250 W compact general purpose flood light with high pressure lamp | [8 empty] | No. | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 194.12 | 23.9932 | 0 | 218.1132 | 0 | 1090.5662 | 1091
2 | 303000000 | Supply, laying, testing and commissioning of following size PVC insulated sheathed copper conductor 1100 V grade armoured cable as per specification including excavation of earth, 300 mm thick and all around the cable, brick protection refilling, watering and ramming or providing to earth etc. complete. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.1 | 303000000 | 3 x 4 sq.mm (Red, Black & Green) | [8 empty] | RM | 350 | 141.37 | 0 | 141.37 | 10.607 | 0 | 151.977 | 75.96 | 9.3887 | 0 | 85.3487 | 53191.9469 | 29872.0296 | 83064
2.2 | 303000000 | 3 x 4 sq.mm (Yellow, Black & Green) | [8 empty] | RM | 350 | 141.37 | 0 | 141.37 | 10.607 | 0 | 151.977 | 75.96 | 9.3887 | 0 | 85.3487 | 53191.9469 | 29872.0296 | 83064
2.3 | 303000000 | 3 x 4 sq.mm (Blue, Black & Green) | [8 empty] | RM | 350 | 141.37 | 0 | 141.37 | 10.607 | 0 | 151.977 | 75.96 | 9.3887 | 0 | 85.3487 | 53191.9469 | 29872.0296 | 83064
3 | 303000000 | Making end termination of following size PVC insulated sheathed copper conductor 1100 V grade armoured cable including cost of crimping lugs, sockets, double compression glands with earthing facility etc. complete. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.1 | 303000000 | 3C x 4 Sq. mm. | [8 empty] | No. | 10 | 281.685 | 0 | 281.685 | 21.1348 | 0 | 302.8198 | 94.95 | 11.7358 | 0 | 106.6858 | 3028.1983 | 1066.8582 | 4095
4 | 303000000 | Providing and fixing of following PVC insulated copper conductor 1100 volts grade stranded flexible wire in GI conduit including providing and fixing of conduit concealed or surface mounted as indicated PVC insulated green colour copper stranded flexible wire for earthing and making connection complete. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4.1 | 303000000 | 3 x 2.5 sq.mm wire in 25 mm dia 16 gauge conduit. | [8 empty] | RM | 175 | 202.56 | 0 | 202.56 | 15.1981 | 0 | 217.7581 | 37.98 | 4.6943 | 0 | 42.6743 | 38107.6634 | 7468.0074 | 45576
5 | 303000000 | Supply and installation of following hume pipe (NP-2 class) under paved areas, including providing 75 mm thick cement concrete cover all around pipe 1:3:6 (1 cement, 3 coarse sand and 6 crushed stone aggregate). | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.1 | 303000000 | 50 mm dia ID | [8 empty] | RM | 15 | 132.93 | 0 | 132.93 | 9.9737 | 0 | 142.9037 | 158.25 | 19.5597 | 0 | 177.8097 | 2143.5561 | 2667.1455 | 4811
5.2 | 303000000 | 100 mm dia ID | [8 empty] | RM | 25 | 231.045 | 0 | 231.045 | 17.3353 | 0 | 248.3803 | 189.9 | 23.4716 | 0 | 213.3716 | 6209.5077 | 5334.291 | 11544
6 | 303000000 | Providing, installation, testing and commissining of 200 x 150 x 125 mm polycarbonate weather proof (IP-55) junction box recessed in wall or surface mounted as required for housing of 1 no. 10 amps SPN MCBs suitable size of terminal blocks complete. Suitable length of GI pipe upto junction box shall also be provided for laying of cables. | [8 empty] | Nos. | 5 | 1055 | 0 | 1055 | 79.1566 | 0 | 1134.1566 | 126.6 | 15.6478 | 0 | 142.2478 | 5670.7832 | 711.2388 | 6382
7 | 303000000 | Supply, installation, testing and commissioning of following polycarbonate weather proof (IP-55) junction box suitable for pole mounting / underground complete as rerequired. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7.1 | 303000000 | One way | [8 empty] | Nos. | 5 | 781.755 | 0 | 781.755 | 58.6551 | 0 | 840.4101 | 126.6 | 15.6478 | 0 | 142.2478 | 4202.0504 | 711.2388 | 4913
7.2 | 303000000 | Two way | [8 empty] | Nos. | 5 | 781.755 | 0 | 781.755 | 58.6551 | 0 | 840.4101 | 126.6 | 15.6478 | 0 | 142.2478 | 4202.0504 | 711.2388 | 4913
7.3 | 303000000 | Three Way | [8 empty] | Nos. | 61 | 911.52 | 0 | 911.52 | 68.3913 | 0 | 979.9113 | 126.6 | 15.6478 | 0 | 142.2478 | 59774.5921 | 8677.1134 | 68452
8 | 303000000 | Installation, testing & commissioning of 4.0 M high poles GI decorative poles (3.0 M above & 1 M below ground). | [8 empty] | Nos. | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 2582.64 | 319.2143 | 0 | 2901.8543 | 0 | 14509.2715 | 14509
9 | 303000000 | Making end termination of following size PVC insulated sheathed copper conductor 1100 V grade armoured cable including cost of crimping lugs, sockets, PVC glands etc. complete ( for polycarbonate boxes only). | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.1 | 303000000 | 3C x 4 Sq. mm. | [8 empty] | No. | 142 | 281.685 | 0 | 281.685 | 21.1348 | 0 | 302.8198 | 94.95 | 11.7358 | 0 | 106.6858 | 43000.4152 | 15149.3864 | 58150
M. | 303000000 | CONDUITING AND CABLING FOR TELEPHONE SYSTEM | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 303000000 | Supply, installation, testing and commissioning of Krone make Protector panel with swivel input stub and splice chamber as required, for the incoming P & T lines. The panel shall have provision for both top and bottom cable feeding. The conductors in the swivel stub and splice chamber shall have 24 AWG conductors and satisfy the fuse link requirement. 5 Nos. test cards shall also be provided. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.1 | 303000000 | 150 pair protector panel | [8 empty] | Nos. | 1 | 16959.125 | 0 | 16959.125 | 1272.4431 | 0 | 18231.5681 | 3798 | 469.4328 | 0 | 4267.4328 | 18231.5681 | 4267.4328 | 22499
2 | 303000000 | Supply, installation, testing and commissioning of Category 5 Riser cable consisting of multiple core or solid copper conductors of 24 AWG size insulated with expanded polyethylene covered by a PVC skin and inner shielding for grounding. The core shall be covered by a layer of plastic tape and overlaid with a corrugated PVC plastic. The cable shall be as per the specifications laid down in the tender | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.1 | 303000000 | 25 pair unarmoured riser cable | [8 empty] | RM | 3000 | 162.47 | 0 | 162.47 | 12.1901 | 0 | 174.6601 | 14.77 | 1.8256 | 0 | 16.5956 | 523980.3723 | 49786.716 | 573767
3 | 303000000 | Supply, installation, testing and commissioning of following Category 6, IDC patch panel prepackaged with wiring block with legs with legs insert labels, label holders, jumper troughs, metal back panel, duct assembly, screws, washers and an instruction sheet for termination of incoming pairs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.1 | 303000000 | 24 port jack panel | [8 empty] | Nos. | 60 | 6251.93 | 0 | 6251.93 | 469.0823 | 0 | 6721.0123 | 886.2 | 109.5343 | 0 | 995.7343 | 403260.7385 | 59744.0592 | 463005
4 | 303000000 | Supply, installation, testing and commissioning of 4 pair Category 6 UTP cable consisting of 23 AWG solid copper conductors and as per the specification. The cable should have flexible jacket and ripcord for easy stripability. | [8 empty] | RM | 26500 | 23.21 | 0 | 23.21 | 1.7414 | 0 | 24.9514 | 5.275 | 0.65199 | 0 | 5.927 | 661213.327 | 157065.235 | 818279
5 | 303000000 | Providing and fixing in position the following 2mm thick embeded , concealed and or surface mounted, heavy duty FRLS PVC conduit as called for including all acessories i.e. bends, junction boxes, outlet boxes with cover plates of approved make and design. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.1 | 303000000 | 25 mm dia conduit | [8 empty] | RM | 10000 | 28.485 | 0 | 28.485 | 2.1372 | 0 | 30.6222 | 25.32 | 3.1296 | 0 | 28.4496 | 306222.2955 | 284495.52 | 590718
6 | 303000000 | Supply, installation, testing and commissioning of Category 6 IDC patch panle prepackaged with wiring block with legs, insert labels, label holders, jumper troughs, metal back panel duct assembly, screws washers and an instruction sheet for termination of incoming pairs. Rate shall include suitable size of lockable 1.6mm thick CRCA sheet steel enclosure duly powder coated. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6.1 | 303000000 | 300 pair wiring block | [8 empty] | Nos. | 4 | 13309.88 | 0 | 13309.88 | 998.6403 | 0 | 14308.5203 | 3162 | 390.8232 | 0 | 3552.8232 | 57234.0812 | 14211.2928 | 71445
6.2 | 303000000 | 100 pair wiring block | [8 empty] | Nos. | 2 | 4440.495 | 0 | 4440.495 | 333.1703 | 0 | 4773.6653 | 1266 | 156.4776 | 0 | 1422.4776 | 9547.3307 | 2844.9552 | 12392
7 | 303000000 | Supply and installation, testing and commissioning following size KRONE make telephone tag block in lockable 16 gauge sheet steel enclosure complete as required. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7.1 | 303000000 | 20 pair Krone type tag block | [8 empty] | No. | 210 | 627.725 | 0 | 627.725 | 47.0982 | 0 | 674.8232 | 253.2 | 31.2955 | 0 | 284.4955 | 141712.8734 | 59744.0592 | 201457
8 | 303000000 | Supply and installation of flush mounted Category 6 T 568 A or B outlet. The plastic shall be high impact, flame-retardant UL rated thermoplastic. Dust cover / Blank shall be provided to protect unused face plate openings. Termination cap and plastic cover shall be provided to protect jack wiring. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8.1 | 303000000 | Single outlet face plate with RJ-11 jack | [8 empty] | Nos. | 600 | 163.525 | 0 | 163.525 | 12.2693 | 0 | 175.7943 | 50.64 | 6.2591 | 0 | 56.8991 | 105476.5685 | 34139.4624 | 139616
8.2 | 303000000 | Double outlet face plate with RJ-11 jack | [8 empty] | Nos. | 15 | 231.045 | 0 | 231.045 | 17.3353 | 0 | 248.3803 | 50.64 | 6.2591 | 0 | 56.8991 | 3725.7046 | 853.4866 | 4579
9 | 303000000 | Supply and fixing perforated GI cable tray with Cover of the following size including fixing hardware supports etc as required (From communication room to LV shaft and vertical in LV shaft: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.1 | 303000000 | a. 450mm x 40 x 40 x 2 mm thick | [8 empty] | RM | 100 | 1499.155 | 0 | 1499.155 | 112.4816 | 0 | 1611.6366 | 202.56 | 25.0364 | 0 | 227.5964 | 161163.66 | 22759.6416 | 183923
10 | 303000000 | Providing and laying the following HDPE pipe of 6 Kg/ Cm2 working pressure laid in ground including cost of digging, 150 mm sand all around the pipe, brick protection and back filling including all accessories i.e. bends, reducers, flanges of approved make and design complete as required. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10.1 | 303000000 | a. 50 mm OD with 2.9 mm wall thickness | [8 empty] | RM | 15 | 79.125 | 0 | 79.125 | 5.9367 | 0 | 85.0617 | 63.3 | 7.8239 | 0 | 71.1239 | 1275.9262 | 1066.8582 | 2343
11 | 303000000 | Supply, installation, testing and commisioning of the following incoming telephone cables. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11.1 | 303000000 | a. 150 pair 0.61 mm dia tinned copper armoured cable | [8 empty] | RM | 100 | 1637.36 | 0 | 1637.36 | 122.8511 | 0 | 1760.2111 | 50.64 | 6.2591 | 0 | 56.8991 | 176021.1121 | 5689.9104 | 181711
12 | 303000000 | Supply and installation of single pair 110 - 110 voice patch cord of 1meters length. | [8 empty] | Nos. | 450 | 169.855 | 0 | 169.855 | 12.7442 | 0 | 182.5992 | 25.32 | 3.1296 | 0 | 28.4496 | 82169.6493 | 12802.2984 | 94972
13 | 303000000 | Supply and installation of following Enhanced Category 6 patch cord for item no 6 above. It shall have male RJ 45 connector on one end and male RJ45 connector at the other end. It shall be a 8 conductor. 4 pair cord with each conductor of 24 AWG stranded wire. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13.1 | 303000000 | 1 m long | [8 empty] | Nos. | 450 | 240.54 | 0 | 240.54 | 18.0477 | 0 | 258.5877 | 37.98 | 4.6943 | 0 | 42.6743 | 116364.4723 | 19203.4476 | 135568
N. | 303000000 | CONDUITING AND CABLING FOR DATA SYSTEM | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 303000000 | Supply and installation of following 19 inch rack for ethernet switches with A.C. distribution box, wire manager, fan tray, lockable front tinted glass door and two pair angle to support the switch installed in the rack. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.1 | 303000000 | 42 U Rack | [8 empty] | Nos. | 7 | 23407.285 | 0 | 23407.285 | 1756.2486 | 0 | 25163.5336 | 1519.2 | 187.7731 | 0 | 1706.9731 | 176144.7352 | 11948.8118 | 188094
2 | 303000000 | Supply, installation, testing and commissioning of following Category 6, IDC patch panel prepackaged with wiring block with legs with legs insert labels, label holders, jumper troughs, metal back panel, duct assembly, screws, washers and an instruction sheet for termination of incoming pairs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.1 | 303000000 | 24 port jack panel | [8 empty] | Nos. | 40 | 5861.58 | 0 | 5861.58 | 439.7943 | 0 | 6301.3743 | 886.2 | 109.5343 | 0 | 995.7343 | 252054.9739 | 39829.3728 | 291884
3 | 303000000 | Supply and installatlion of wire manager suitable for mounted on 19 inch rack. | [8 empty] | Nos. | 40 | 524.335 | 0 | 524.335 | 39.3409 | 0 | 563.6759 | 253.2 | 31.2955 | 0 | 284.4955 | 22547.0342 | 11379.8208 | 33927
4 | 303000000 | Supply, installation, testing and commissioning of 4 pair Category 6 LAN cable consisting of 24 AWG solid copper conductors and as per the specification. The cable shall have flexible jacket and ripcord for easy Stripability | [8 empty] | RM | 26000 | 23.21 | 0 | 23.21 | 1.7414 | 0 | 24.9514 | 5.275 | 0.65199 | 0 | 5.927 | 648737.6038 | 154101.74 | 802839
5 | 303000000 | Supply and installation of flush mounted Enhanced Category 6 T 568 A or B) outlet. The plastic shall be high impact, flame-retardant, UL rate thermoplastic. Dust cover / blank shall be provided to protect unused faceplate openings. Termination caps and plastic cover shall be provided to protect jack wiring. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.1 | 303000000 | Single outlet faceplate with RJ-45 jack with information outlet | [8 empty] | Nos. | 600 | 422 | 0 | 422 | 31.6627 | 0 | 453.6627 | 50.64 | 6.2591 | 0 | 56.8991 | 272197.596 | 34139.4624 | 306337
5.2 | 303000000 | Duplex outlet faceplate with 2 Nos. RJ-45 with information outlets | [8 empty] | Nos. | 15 | 762.765 | 0 | 762.765 | 57.2303 | 0 | 819.9953 | 50.64 | 6.2591 | 0 | 56.8991 | 12299.9289 | 853.4866 | 13153
6 | 303000000 | Supply and installation of following Enhanced Category 6 mounting cord for connecting the outlets to the data station (computer/printer etc). It shall have male RJ 45 connector on one end and male RJ45 connector or open ended wire or a connector suitable for data outlet at the other end. It shall be a 8 conductor. 4 pair cord with each conductor of 24 AWG stranded wire. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6.1 | 303000000 | 1 m long (For patchong of jack panel & switch) | [8 empty] | Nos. | 600 | 168.8 | 0 | 168.8 | 12.6651 | 0 | 181.4651 | 12.66 | 1.5648 | 0 | 14.2248 | 108879.0384 | 8534.8656 | 117414
6.2 | 303000000 | 2 m long (For outlet) | [8 empty] | Nos. | 600 | 259.53 | 0 | 259.53 | 19.4725 | 0 | 279.0025 | 12.66 | 1.5648 | 0 | 14.2248 | 167401.5215 | 8534.8656 | 175936
7 | 303000000 | Supply and fixing in position the following 2mm thick embeded heavy duty FRLS PVC conduit and or surface mounted 16 gauge GI conduits concealed or exposed as called for including cost of junction boxes, bends, elbows, sockets, tees etc. laying in slab cutting chasis and making good or surface mounted including all fixing hardware. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7.1 | 303000000 | 25 mm dia | [8 empty] | RM | 8500 | 39.035 | 0 | 39.035 | 2.9288 | 0 | 41.9638 | 25.32 | 3.1296 | 0 | 28.4496 | 356692.2664 | 241821.192 | 598513
8 | 303000000 | Supply and fixing perforated GI cable tray with Cover of the following size including fixing hardware supports etc as required (From communication room to LV shaft and vertical in LV shaft): | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8.1 | 303000000 | a. 450mm x 40 x 40 x 2 mm thick | [8 empty] | RM | 100 | 1499.155 | 0 | 1499.155 | 112.4816 | 0 | 1611.6366 | 202.56 | 25.0364 | 0 | 227.5964 | 161163.66 | 22759.6416 | 183923
9 | 303000000 | Providing and laying the following HDPE pipe of 6 Kg/ Cm2 working pressure laid in ground including cost of digging, 150 mm sand all around the pipe, brick protection and back filling including all accessories i.e. bends, reducers, flanges of approved make and design complete as required. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.1 | 303000000 | a. 50 mm OD with 2.9 mm wall thickness | [8 empty] | RM | 15 | 325.995 | 0 | 325.995 | 24.4594 | 0 | 350.4544 | 63.3 | 7.8239 | 0 | 71.1239 | 5256.8161 | 1066.8582 | 6324
10 | 303000000 | Supply, installation and testing of 50/125 microm OM3 - 6 core multimode Fiber optics as per specification. | [8 empty] | RM | 50 | 182.515 | 0 | 182.515 | 13.6941 | 0 | 196.2091 | 23.21 | 2.8688 | 0 | 26.0788 | 9810.455 | 1303.9378 | 11114
11 | 303000000 | Supply, installation and testing of 50/125 microm OM3 - 12 core multimode Fiber optics as per specification. | [8 empty] | RM | 1625 | 207.835 | 0 | 207.835 | 15.5939 | 0 | 223.4289 | 25.32 | 3.1296 | 0 | 28.4496 | 363071.8976 | 46230.522 | 409302
12 | 303000000 | Supply , installation and testing of 12 port rack mount LIU | [8 empty] | Nos | 1 | 10397.025 | 0 | 10397.025 | 780.0888 | 0 | 11177.1138 | 379.8 | 46.9433 | 0 | 426.7433 | 11177.1138 | 426.7433 | 11604
13 | 303000000 | Supply , installation and testing of 24 port rack mount LIU | [8 empty] | Nos | 5 | 18196.64 | 0 | 18196.64 | 1365.2939 | 0 | 19561.9339 | 759.6 | 93.8866 | 0 | 853.4866 | 97809.6695 | 4267.4328 | 102077
14 | 303000000 | Termination of both sides of 6 core fiber optics cables in the LIU which includes adapter panel, adapter , SC type pigtail | [8 empty] | Nos | 4 | 1570.895 | 0 | 1570.895 | 117.8643 | 0 | 1688.7593 | 633 | 78.2388 | 0 | 711.2388 | 6755.037 | 2844.9552 | 9600
15 | 303000000 | Termination of both sides of 12 core fiber optics cables in the LIU which includes adapter panel, adapter , SC type pigtail | [8 empty] | Nos | 20 | 3926.71 | 0 | 3926.71 | 294.6211 | 0 | 4221.3311 | 1519.2 | 187.7731 | 0 | 1706.9731 | 84426.621 | 34139.4624 | 118566
O. | 303000000 | CONDUTING & CABLING FOR TV SYSTEM | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 303000000 | Providing and fixing in position the following 2mm thick conduits concealed, embeded or exposed as called for including all accessories i.e. bends, junction boxes, outlet boxes with cover plates of approved make and design | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.1 | 303000000 | 25 mm dia conduit | [8 empty] | RM | 3350 | 39.035 | 0 | 39.035 | 2.9288 | 0 | 41.9638 | 25.32 | 3.1296 | 0 | 28.4496 | 140578.7168 | 95305.9992 | 235885
1.2 | 303000000 | 32 mm dia conduit | [8 empty] | RM | 1350 | 63.3 | 0 | 63.3 | 4.7494 | 0 | 68.0494 | 31.65 | 3.9119 | 0 | 35.5619 | 91866.6886 | 48008.619 | 139875
1.2.1 | 303000000 | (For RG-11 Co-axial cable) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 303000000 | Supply and fixing following signal outlets with grid plate in 2 mm thick GI box complete including cutting, chases, fixing of GI boxes and making good. (Cover plate shall match the colour, size and make of wiring accessories to be used in the project.) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.1 | 303000000 | TV Signals outlet | [8 empty] | Nos. | 295 | 162.47 | 0 | 162.47 | 12.1901 | 0 | 174.6601 | 50.64 | 6.2591 | 0 | 56.8991 | 51524.7366 | 16785.2357 | 68310
3 | 303000000 | Supply, erection, testing and commissioning of following tap off with IP 55 boxes for CATV system. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.1 | 303000000 | One way (T-1) | [8 empty] | Nos. | 75 | 390.35 | 0 | 390.35 | 29.288 | 0 | 419.638 | 63.3 | 7.8239 | 0 | 71.1239 | 31472.847 | 5334.291 | 36807
3.2 | 303000000 | Two way (T-2) | [8 empty] | Nos. | 102 | 455.76 | 0 | 455.76 | 34.1957 | 0 | 489.9557 | 75.96 | 9.3887 | 0 | 85.3487 | 49975.4786 | 8705.5629 | 58681
3.3 | 303000000 | Four way (T-4) | [8 empty] | Nos. | 4 | 521.17 | 0 | 521.17 | 39.1034 | 0 | 560.2734 | 75.96 | 9.3887 | 0 | 85.3487 | 2241.0935 | 341.3946 | 2582
4 | 303000000 | Supply, erection, testing and commissioning of spliter with IP 55 boxes. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4.1 | 303000000 | Two way (S 2) | [8 empty] | Nos. | 5 | 522.225 | 0 | 522.225 | 39.1825 | 0 | 561.4075 | 101.28 | 12.5182 | 0 | 113.7982 | 2807.0377 | 568.991 | 3376
4.2 | 303000000 | Four way (S 4) | [8 empty] | Nos. | 5 | 650.935 | 0 | 650.935 | 48.8397 | 0 | 699.7747 | 101.28 | 12.5182 | 0 | 113.7982 | 3498.8733 | 568.991 | 4068
5 | 303000000 | Supply, laying, connecting and commissioning of RG-11 co-axial cable of MATV as per specification in existing PVC conduit | [8 empty] | RM | 1350 | 36.925 | 0 | 36.925 | 2.7705 | 0 | 39.6955 | 5.275 | 0.65199 | 0 | 5.927 | 53588.9017 | 8001.4365 | 61590
6 | 303000000 | Supply, laying, connecting and commissioning of RG-6 co-axial cable of MATV as per specification in existing PVC conduit. | [8 empty] | RM | 3500 | 18.99 | 0 | 18.99 | 1.4248 | 0 | 20.4148 | 5.275 | 0.65199 | 0 | 5.927 | 71451.8689 | 20744.465 | 92196
7 | 303000000 | Supply and fixing of Line extender amplifier 110 DB as per specification housed in suitable size of 16 gauge CRCA sheet enclosed. | [8 empty] | Nos | 3 | 3901.39 | 0 | 3901.39 | 292.7213 | 0 | 4194.1113 | 253.2 | 31.2955 | 0 | 284.4955 | 12582.3339 | 853.4866 | 13436
8 | 303000000 | Supply, laying and connecting of single pair PVC insulated twisted copper conductor cable of 32/0.2 mm dia in conealed/surface mounted 2mm thick heavy duty FRLS pvc conduit including all fixing accessories as required. | [8 empty] | RM | 250 | 50.64 | 0 | 50.64 | 3.7995 | 0 | 54.4395 | 31.65 | 3.9119 | 0 | 35.5619 | 13609.8798 | 8890.485 | 22500

## Certification
Scenario 3
Local Supply + Installation |  |  | COP-R001 | [21 empty] | 63424804 |  |  | 5118098.6605 | 0 | 5118098.6605 | 384010.9425 | 0 | 5502109.603 | 747928.233 | 92443.9296 | 0 | 840372.1626 | 6342481.7656
|  | UNIQUE IDENTIFIERS | [8 empty] | UOM | QTY | RATE (can be entered directly or summed up for totals)
Sr. No. | Item Range Code | Description | Area | Make | Model No./ Product Code | Tag/ Item No. | ITC HS Code | Country of Origin | Port of Loading | User defined column |  |  | Local supply rate | [5 empty] | Installation Rate |  |  |  | Amount |  |  | LOCAL SUPPLY CERTIFICATION | [7 empty] | INSTALLATION CERTIFICATION |  |  |  | CERTIFICATION TOTAL
[13 empty] | Basic Rate | Excise | Subtotal = Basic + Excise | VAT/CST on Subtotal | Others | Supply Rate Total (sum or direct entry) | Basic Rate | Service Tax | Other | Installation Rate Total (sum or direct entry) | LOCAL SUPPLY AMOUNT | INSTALLATION AMOUNT | TOTAL AMOUNT | COP Percentage | COP Quantity | COP Supply Basic | COP Excise | COP Sub Total | COP VAT / CST | COP SupplyOthers | COP Supply Total | COP Installation Basic | COP Service TAX | COP Others | COP Installation Total | TOTAL COP AMOUNT
A. | 303000000 | CIRCUIT CUM POINT WIRING | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
I | 303000000 | Public & BOH Areas | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 303000000 | Wiring of following light points with 2.5 sq.mm PVC insulated copper conductor 1100 volts grade stranded flexible FRLS wires surface mounted and or embeded in 25mm dia. heavy duty FRLS PVC conduit as per IS 9537 part-3 including providing and fixing of 6 amps single pole rocker operated flush mounted switches of approved quality colour make and design in 1.6 mm thick GI box and earthing of fixture and the outlet box with 2.5 Sq.mm PVC insulated copper conductor stranded flexible FRLS wire. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.1 | 303000000 | MCB controlled Primary point (from DB to switch board - cost of switch & board NOT included) | [8 empty] | Pt | 130 | 1779.785 | 0 | 1779.785 | 133.5373 | 0 | 1913.3223 | 472.64 | 58.4183 | 0 | 531.0583 | 248731.8949 | 69037.5795 | 317769 | 10 | 130 | 23137.205 | 0 | 23137.205 | 1735.9845 | 0 | 24873.1895 | 6144.32 | 759.438 | 0 | 6903.758 | 31776.9474
1.2 | 303000000 | Secondary point with switch ( from switch board to first point - cost of switch & board included) | [8 empty] | Pt | 215 | 629.835 | 0 | 629.835 | 47.2565 | 0 | 677.0915 | 125.545 | 15.5174 | 0 | 141.0624 | 145574.6768 | 30328.4078 | 175903 | 10 | 215 | 13541.4525 | 0 | 13541.4525 | 1016.0152 | 0 | 14557.4677 | 2699.2175 | 333.6233 | 0 | 3032.8408 | 17590.3085
1.3 | 303000000 | Secondary point without switch ( from light point to light point - cost of switch & board NOT included) | [8 empty] | Pt | 320 | 475.805 | 0 | 475.805 | 35.6996 | 0 | 511.5046 | 176.185 | 21.7765 | 0 | 197.9615 | 163681.4877 | 63347.6691 | 227029 | 10 | 320 | 15225.76 | 0 | 15225.76 | 1142.3888 | 0 | 16368.1488 | 5637.92 | 696.8469 | 0 | 6334.7669 | 22702.9157
1.4 | 303000000 | Primary point without switch (from switch board to switch board looping- cost of switch & board NOT included) | [8 empty] | Pt | 40 | 1423.195 | 0 | 1423.195 | 106.7823 | 0 | 1529.9773 | 377.69 | 46.6825 | 0 | 424.3725 | 61199.0928 | 16974.8994 | 78174 | 10 | 40 | 5692.78 | 0 | 5692.78 | 427.1293 | 0 | 6119.9093 | 1510.76 | 186.7299 | 0 | 1697.4899 | 7817.3992
2 | 303000000 | Wiring for the twin control light points with 2.5 sq.mm PVC insulated copper conductor 1100 volts grade stranded flexible FRLS wires surface mounted and or embeded in 25mm dia. heavy duty FRLS PVC conduit as per IS 9537 part-3 including providing and fixing 2 Nos.6 amps 2 way rocker operated flush mounted switches of approved quality colour make and design in 1.6 mm thick GI box and earthing of fixture and the outlet box with 2.5 Sq.mm PVC insulated copper conductor stranded flexible FRLS wire. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.1 | 303000000 | MCB controlled Primary point (from DB to switch board - cost of switch & board NOT included) | [8 empty] | Pt | 5 | 2372.695 | 0 | 2372.695 | 178.0233 | 0 | 2550.7183 | 629.835 | 77.8476 | 0 | 707.6826 | 12753.5915 | 3538.413 | 16292 | 10 | 5 | 1186.3475 | 0 | 1186.3475 | 89.0117 | 0 | 1275.3592 | 314.9175 | 38.9238 | 0 | 353.8413 | 1629.2005
2.2 | 303000000 | six point controlled by 2 Nos. two way switches. | [8 empty] | set | 5 | 4207.34 | 0 | 4207.34 | 315.6767 | 0 | 4523.0167 | 1065.55 | 131.702 | 0 | 1197.252 | 22615.0836 | 5986.2599 | 28601 | 10 | 5 | 2103.67 | 0 | 2103.67 | 157.8384 | 0 | 2261.5084 | 532.775 | 65.851 | 0 | 598.626 | 2860.1344
2.3 | 303000000 | Eight points controlled by 2 Nos two way switches. | [8 empty] | set | 5 | 4907.86 | 0 | 4907.86 | 368.2367 | 0 | 5276.0967 | 1232.24 | 152.3049 | 0 | 1384.5449 | 26380.4837 | 6922.7243 | 33303 | 10 | 5 | 2453.93 | 0 | 2453.93 | 184.1184 | 0 | 2638.0484 | 616.12 | 76.1524 | 0 | 692.2724 | 3330.3208
3 | 303000000 | Wiring for following 250 volt single phase and neutral 6 amps switch socket outlet with 2.5 sq.mm PVC insulated copper conductor 1100 volts grade stranded flexible FRLS wires in surface mounted and or embeded in 25mm dia. heavy duty FRLS PVC conduit as per IS 9537 part-3, including providing and fixing of 6 amps switch and 6A 3 pin socket of approved make colour and design in 1.6 mm thick GI box with grid plate and earthing of third pin of the socket outlet and the GI box with 2.5 Sq.mm PVC insulated copper conductor stranded flexible FRLS wire. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.1 | 303000000 | 2 nos. switched socket outlet connected on one circuit. | [8 empty] | set | 5 | 1900 | 0 | 1900 | 142.557 | 0 | 2042.557 | 554.93 | 68.5893 | 0 | 623.5193 | 10212.785 | 3117.5967 | 13330 | 10 | 5 | 950 | 0 | 950 | 71.2785 | 0 | 1021.2785 | 277.465 | 34.2947 | 0 | 311.7597 | 1333.0382
3.2 | 303000000 | 4 nos. switched socket outlet connected on one circuit. | [8 empty] | set | 5 | 1900 | 0 | 1900 | 142.557 | 0 | 2042.557 | 567.59 | 70.1541 | 0 | 637.7441 | 10212.785 | 3188.7206 | 13402 | 10 | 5 | 950 | 0 | 950 | 71.2785 | 0 | 1021.2785 | 283.795 | 35.0771 | 0 | 318.8721 | 1340.1506
4 | 303000000 | Wiring for 250 volts single phase and neutral 6/16 amps switch and socket outlet with 4 sq.mm PVC insulated copper conductor 1100 volts grade stranded flexible FRLS wires in surface mounted or embeded in 25mm dia. heavy duty FRLS PVC conduit as per IS 9537 part-3 , including providing and fixing of 16 amps switch and 5 pin socket of approved make and design in 1.6 mm thick GI boxes with grid plates and earthing the third pin of socket outlet with 4 Sq. mm PVC insulated copper conductor stranded flexible FRLS wire. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4.1 | 303000000 | 1 nos. switched socket outlet connected on one circuit. | [8 empty] | Pts. | 12 | 1068.715 | 0 | 1068.715 | 80.1857 | 0 | 1148.9007 | 334.435 | 41.3362 | 0 | 375.7712 | 13786.8082 | 4509.254 | 18296 | 10 | 12 | 1282.458 | 0 | 1282.458 | 96.2228 | 0 | 1378.6808 | 401.322 | 49.6034 | 0 | 450.9254 | 1829.6062
4.2 | 303000000 | 2 nos. switched socket outlet connected on one circuit. | [8 empty] | sets | 115 | 1306.09 | 0 | 1306.09 | 97.9959 | 0 | 1404.0859 | 396.68 | 49.0296 | 0 | 445.7096 | 161469.8823 | 51256.6095 | 212726 | 10 | 115 | 15020.035 | 0 | 15020.035 | 1126.9532 | 0 | 16146.9882 | 4561.82 | 563.841 | 0 | 5125.661 | 21272.6492
4.3 | 303000000 | 3 nos. switched socket outlet connected on one circuit. | [8 empty] | sets | 55 | 1661.625 | 0 | 1661.625 | 124.6717 | 0 | 1786.2967 | 491.63 | 60.7655 | 0 | 552.3955 | 98246.3198 | 30381.7507 | 128628 | 10 | 55 | 9138.9375 | 0 | 9138.9375 | 685.6945 | 0 | 9824.632 | 2703.965 | 334.2101 | 0 | 3038.1751 | 12862.8071
4.4 | 303000000 | 4 nos. switched socket outlet connected on one circuit. | [8 empty] | sets | 8 | 2217.61 | 0 | 2217.61 | 166.3873 | 0 | 2383.9973 | 680.475 | 84.1067 | 0 | 764.5817 | 19071.9782 | 6116.6537 | 25189 | 10 | 8 | 1774.088 | 0 | 1774.088 | 133.1098 | 0 | 1907.1978 | 544.38 | 67.2854 | 0 | 611.6654 | 2518.8632
5 | 303000000 | Wiring for following 250 volt single phase and neutral with 2 nos 6/16 amps 5 pin socket outlet controlled by 1 nos 16 Amps switch for work stations with 4 sq.mm PVC insulated copper conductor 1100 volts grade stranded flexible FRLS wires in surface mounted or embeded 25mm dia. heavy duty FRLS PVC conduit as per IS 9537 part-3, including providing and fixing of 2 nos. 6/16A 5 pin sockets and one 16 amps switch of approved make colour and design in 1.6 mm thick GI box with grid plate and earthing of third pin of the socket outlet and the GI box with 4 Sq.mm PVC insulated copper conductor stranded flexible FRLS wire. (Max of 4 sets of item as described shall be connected on one circuit.) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.1 | 303000000 | Primary point. | [8 empty] | Sets | 115 | 1306.09 | 0 | 1306.09 | 97.9959 | 0 | 1404.0859 | 396.68 | 49.0296 | 0 | 445.7096 | 161469.8823 | 51256.6095 | 212726 | 10 | 115 | 15020.035 | 0 | 15020.035 | 1126.9532 | 0 | 16146.9882 | 4561.82 | 563.841 | 0 | 5125.661 | 21272.6492
5.2 | 303000000 | Same as Item No. 5 above but secondary point. | [8 empty] | Sets | 130 | 475.805 | 0 | 475.805 | 35.6996 | 0 | 511.5046 | 176.185 | 21.7765 | 0 | 197.9615 | 66495.6044 | 25734.9906 | 92231 | 10 | 130 | 6185.465 | 0 | 6185.465 | 464.0954 | 0 | 6649.5604 | 2290.405 | 283.0941 | 0 | 2573.4991 | 9223.0595
6 | 303000000 | Wiring for following dimmer/MCB controlled point with 2.5 sq.mm PVC insulated copper conductor 1100 volts grade stranded flexible FRLS wires in surface mounted and or embeded in 25mm dia. heavy duty FRLS PVC conduit as per IS 9537 part-3 s, including fixing electronic dimmer of approved mak in 1.6 mm thick GI box and earthing of outlet box and lighting fixture with 2.5 sq. mm. PVC insulated copper conductor stranded flexible FRLS wire (Dimmer/MCB not included). | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6.1 | 303000000 | MCB controlled Primary point (from MCB to first light point) | [8 empty] | Pt | 450 | 1899 | 0 | 1899 | 142.482 | 0 | 2041.482 | 504.29 | 62.3302 | 0 | 566.6202 | 918666.8865 | 254979.1098 | 1173646 | 10 | 450 | 85455 | 0 | 85455 | 6411.6887 | 0 | 91866.6886 | 22693.05 | 2804.861 | 0 | 25497.911 | 117364.5996
6.2 | 303000000 | MCB controlled Secondary point (from point to point of same circuit) | [8 empty] | Pt | 1595 | 474.75 | 0 | 474.75 | 35.6205 | 0 | 510.3705 | 125.545 | 15.5174 | 0 | 141.0624 | 814040.9355 | 224994.4674 | 1039035 | 10 | 1595 | 75722.625 | 0 | 75722.625 | 5681.4686 | 0 | 81404.0936 | 20024.4275 | 2475.0192 | 0 | 22499.4467 | 103903.5403
7 | 303000000 | Wiring for 250 volts single phase and neutral 16 amps polycarbonate splash proof (IP-65) 3 pin industrial socket outlet with 16 amps interlocked rotary switch in polycarbonate enclosure of approved size and design with 4 sq.mm PVC insulated copper conductor 1100 volts grade stranded flexible FRLS wires in surface mounted or embeded 25mm dia. heavy duty FRLS PVC conduit as per IS 9537 part-3 s, including providing and fixing of 3 pin industrial socket and earthing of third pin of the socket outlet with 4 Sq. mm PVC insulated copper conductor stranded flexible FRLS wire. | [8 empty] | Pts. | 245 | 4703.19 | 0 | 4703.19 | 352.8803 | 0 | 5056.0703 | 354.48 | 43.8137 | 0 | 398.2937 | 1238737.2347 | 97581.9634 | 1336319 | 10 | 245 | 115228.155 | 0 | 115228.155 | 8645.5685 | 0 | 123873.7235 | 8684.76 | 1073.4363 | 0 | 9758.1963 | 133631.9198
8 | 303000000 | Wiring for 250 volts single phase and neutral 32 amps polycarbonate splash proof (IP-65) 3 pin industrial socket outlet with 32 amps interlocked rotary switch in polycarbonate enclosure of approved size and design with 6 sq. mm PVC insulated copper conductor 1100 volts grade stranded flexible FRLS wires in embeded or surface mounted 25 mm dia heavy duty FRLS PVC conduit, including providing and fixing of 3 pin industrial socket and earthing of third pin of the socket and outlet with 6 sq. mm PVC insulated copper conductor stranded flexible FRLS wire. | [8 empty] | Pts. | 5 | 7094.875 | 0 | 7094.875 | 532.3285 | 0 | 7627.2035 | 428.33 | 52.9416 | 0 | 481.2716 | 38136.0174 | 2406.3579 | 40542 | 10 | 5 | 3547.4375 | 0 | 3547.4375 | 266.1642 | 0 | 3813.6017 | 214.165 | 26.4708 | 0 | 240.6358 | 4054.2375
9 | 303000000 | Wiring for 415 volts three phase and neutral 16 amps polycarbonate splash proof (IP-65) industrial socket outlet with 16 amps interlocked rotary switch in polycarbonate enclosure of approved size and design with 4 x 4 sq.mm PVC insulated copper conductor 1100 volts grade stranded flexible FRLS wires in 25mm dia. 2mm thick embeded or surface mounted PVC conduit including providing and fixing of 5 pin industrial socket and earthing of earth pin of the socket outlet with 4 Sq. mm PVC insulated copper conductor stranded flexible FRLS wire. | [8 empty] | Pts. | 50 | 6517.79 | 0 | 6517.79 | 489.0298 | 0 | 7006.8198 | 404.065 | 49.9424 | 0 | 454.0074 | 350340.9892 | 22700.3717 | 373041 | 10 | 50 | 32588.95 | 0 | 32588.95 | 2445.1489 | 0 | 35034.0989 | 2020.325 | 249.7122 | 0 | 2270.0372 | 37304.1361
10 | 303000000 | Wiring for 415 volts three phase and neutral 32 amps polycarbonate splash proof (IP-65/66) industrial socket outlet with 32 amps interlocked rotary switch in polycarbonate enclosure of approved size and design with 4 x 6 sq.mm PVC insulated copper conductor 1100 volts grade stranded flexible FRLS wires in 25mm dia. 2mm thick embeded or surface mounted PVC conduit, including earthing of earth pin of the socket with 6 sq mm PVC insulated copper conductor stranded flexible FRLS wires. | [8 empty] | Pts. | 15 | 8811.36 | 0 | 8811.36 | 661.1163 | 0 | 9472.4763 | 559.15 | 69.1109 | 0 | 628.2609 | 142087.1451 | 9423.9141 | 151511 | 10 | 15 | 13217.04 | 0 | 13217.04 | 991.6745 | 0 | 14208.7145 | 838.725 | 103.6664 | 0 | 942.3914 | 15151.1059
11 | 303000000 | Wiring for Exhaust fan point with 2.5 sq. mm. Insulated copper conductor 1100 volts grade stranded flexible FRLS wires of approved make in 25mm dia. 2mm thick embeded or surface mounted PVC conduit including providing and fixing of 6 amps flush mounted switch at the normal switch level in 2 mm thick GI box and 6 amps 3 pin flush mounted socket outlet near exhaust fan and earthing of exhaust fan through the third pin of the socket outlet and GI box with 2.5 sq. mm. PVC insulated copper conductor strande flexible FRLS wire. (As per HVAC boq) | [8 empty] | Pts. | 15 | 1410.535 | 0 | 1410.535 | 105.8324 | 0 | 1516.3674 | 385.075 | 47.5953 | 0 | 432.6703 | 22745.5116 | 6490.054 | 29236 | 10 | 15 | 2115.8025 | 0 | 2115.8025 | 158.7487 | 0 | 2274.5512 | 577.6125 | 71.3929 | 0 | 649.0054 | 2923.5566
12 | 303000000 | Wiring for fan coil unit with 2.5 sq. mm. PVC insulated Copper conductor 1100 volts grade stranded flexible FRLS wires of approved make in embeded or surface mounted 25mm dia. heavy duty FRLS PVC conduit as per IS 9537 part-3 and terminating the wire into the HVAC control box (control box and wiring shall be in scope of HVAC contractor) including conduiting (length of conduit approx. 3 – 5 metre) from fan coil unit to thermostat including 2 mm thick GI box, providing and fixing of 6A switch socket, earthing of GI box with 2.5 sq. mm. PVC insulated copper conductor stranded flexible FRLS wires. | [8 empty] | Pts. | 38 | 1195.315 | 0 | 1195.315 | 89.6845 | 0 | 1284.9995 | 302.785 | 37.4242 | 0 | 340.2092 | 48829.9804 | 12927.9506 | 61758 | 10 | 38 | 4542.197 | 0 | 4542.197 | 340.801 | 0 | 4882.998 | 1150.583 | 142.2121 | 0 | 1292.7951 | 6175.7931
13 | 303000000 | Wiring for DB controlled Chandelier point with 4 sq. mm. PVC insulated copper conductor 1100 volts grade stranded flexible FRLS wires of approved make in embeded or surface mounted 25mm dia. heavy duty FRLS PVC conduit as per IS 9537 part-3 including providing of fixing hook for down rod etc. and earthing with 4 sq. mm. PVC insulated copper conductor stranded flexible FRLS wire. | [8 empty] | Nos. | 15 | 9055.065 | 0 | 9055.065 | 679.4015 | 0 | 9734.4665 | 953.72 | 117.8798 | 0 | 1071.5998 | 146016.9979 | 16073.9969 | 162091 | 10 | 15 | 13582.5975 | 0 | 13582.5975 | 1019.1023 | 0 | 14601.6998 | 1430.58 | 176.8197 | 0 | 1607.3997 | 16209.0995
14 | 303000000 | Supply, installation, testing and commissioning of 415 volts 3 phase and neutral 16 amps polycarbonate splash proof (IP-55) industrial socket outlets with 16 amps interlocked rotary switch in weather proof polycarbonate enclosure of approved size and design. (Near swimming pool) | [8 empty] | Pts. | 2 | 5068.22 | 0 | 5068.22 | 380.2685 | 0 | 5448.4885 | 126.6 | 15.6478 | 0 | 142.2478 | 10896.9771 | 284.4955 | 11181 | 10 | 2 | 1013.644 | 0 | 1013.644 | 76.0537 | 0 | 1089.6977 | 25.32 | 3.1296 | 0 | 28.4496 | 1118.1473
15 | 303000000 | Wiring for 250 volts single phase and neutral 16 amps recessed in floor polycarbonate socket outlet wiring with 4 sq.mm PVC insulated copper conductor 1100 volts grade stranded flexible FRLS wire in embeded or surface mounted 25mm dia. heavy duty FRLS PVC conduit as per IS 9537 part-3, including providing and fixing of 16 amps 3 Pin socket of approved make and design polycarbonate water tight box (IP-65) for kitchen area including providing and fixing socket and earthing of third pin of the socket outlet with 4 sq.mm PVC insulated copper conductor stranded flexible FRLS wire. | [8 empty] | Pts. | 5 | 5803.555 | 0 | 5803.555 | 435.4407 | 0 | 6238.9957 | 777.535 | 96.1033 | 0 | 873.6383 | 31194.9787 | 4368.1916 | 35563 | 10 | 5 | 2901.7775 | 0 | 2901.7775 | 217.7204 | 0 | 3119.4979 | 388.7675 | 48.0517 | 0 | 436.8192 | 3556.317
16 | 303000000 | Wiring for guest room shafts lighting with 2.5 sq.mm PVC insulated copper conductor 1100 volts grade stranded flexible FRLS wire in 25 mm dia 2 mm thich heavy duty FRLS PVC conduit embeded or surface mounted as asked for controlled by 1 no. 6 amps switch located in the each shaft. | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16.1 | 303000000 | 12 points on one circuit | [8 empty] | Set | 13 | 5852.085 | 0 | 5852.085 | 439.0819 | 0 | 6291.1669 | 1562.455 | 193.1194 | 0 | 1755.5744 | 81785.1702 | 22822.4677 | 104608 | 10 | 13 | 7607.7105 | 0 | 7607.7105 | 570.8065 | 0 | 8178.517 | 2031.1915 | 251.0553 | 0 | 2282.2468 | 10460.7638
II | 303000000 | LIFT SHAFTS | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 303000000 | Wiring for 250 volts single phase and neutral 16 amps switched socket outlet for lift shafts ONE AT EACH FLOOR LEVEL with 4 sq.mm PVC insulated copper conductor 1100 volts grade stranded flexible FRLS wires in surface mounted 25 mm dia 16 gauge GI conduit including providing and fixing of 16 amps 3 pin switched socket of approved make and design in 2 mm thick GI boxes with grid plates and earthing of third pin of socket outlet and GI box with 4 sq.mm PVC insulated copper conductor stranded flexible FRLS wire. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.1 | 303000000 | 9 points on one circuit | [8 empty] | Set | 4 | 9156.345 | 0 | 9156.345 | 687.0006 | 0 | 9843.3456 | 1789.28 | 221.155 | 0 | 2010.435 | 39373.3823 | 8041.74 | 47415 | 10 | 4 | 3662.538 | 0 | 3662.538 | 274.8002 | 0 | 3937.3382 | 715.712 | 88.462 | 0 | 804.174 | 4741.5122
1.2 | 303000000 | 8 points on one circuit | [8 empty] | Set | 4 | 8223.725 | 0 | 8223.725 | 617.0261 | 0 | 8840.7511 | 1608.875 | 198.8569 | 0 | 1807.7319 | 35363.0043 | 7230.9278 | 42594 | 10 | 4 | 3289.49 | 0 | 3289.49 | 246.8104 | 0 | 3536.3004 | 643.55 | 79.5428 | 0 | 723.0928 | 4259.3932
1.3 | 303000000 | 5 points on one circuit | [8 empty] | Set | 2 | 5421.645 | 0 | 5421.645 | 406.786 | 0 | 5828.431 | 1066.605 | 131.8324 | 0 | 1198.4374 | 11656.862 | 2396.8748 | 14054 | 10 | 2 | 1084.329 | 0 | 1084.329 | 81.3572 | 0 | 1165.6862 | 213.321 | 26.3665 | 0 | 239.6875 | 1405.3737
2 | 303000000 | Installation & wiring of 230 V bulk head lamp with on/off switch for Lift shafts ONE AT EACH FLOOR LEVEL with 2.5 sq.mm PVC insulated copper conductor 1100V grade stranded flexible FRLS wires in 25 mm dia 16 guage GI surface mounted conduits including providing and fixing of 6A switch AT EACH FLOOR LEVEL with 2.5 sq.mm. PVC insulated copper conductor stranded flexible earth wire. (Supply of fixture considered elsewere in the Boq) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.1 | 303000000 | 9 points on one circuit | [8 empty] | Set | 4 | 7259.455 | 0 | 7259.455 | 544.6769 | 0 | 7804.1319 | 2643.83 | 326.7774 | 0 | 2970.6074 | 31216.5276 | 11882.4296 | 43099 | 10 | 4 | 2903.782 | 0 | 2903.782 | 217.8708 | 0 | 3121.6528 | 1057.532 | 130.711 | 0 | 1188.243 | 4309.8957
2.2 | 303000000 | 8 points on one circuit | [8 empty] | Set | 4 | 6531.505 | 0 | 6531.505 | 490.0588 | 0 | 7021.5638 | 2368.475 | 292.7435 | 0 | 2661.2185 | 28086.2553 | 10644.874 | 38731 | 10 | 4 | 2612.602 | 0 | 2612.602 | 196.0235 | 0 | 2808.6255 | 947.39 | 117.0974 | 0 | 1064.4874 | 3873.1129
2.3 | 303000000 | 5 points on one circuit | [8 empty] | Set | 2 | 4348.71 | 0 | 4348.71 | 326.2837 | 0 | 4674.9937 | 1541.355 | 190.5115 | 0 | 1731.8665 | 9349.9874 | 3463.733 | 12814 | 10 | 2 | 869.742 | 0 | 869.742 | 65.2567 | 0 | 934.9987 | 308.271 | 38.1023 | 0 | 346.3733 | 1281.372
A II | 303000000 | Guest Rooms | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | CIRCUIT CUM POINT WIRING (WITH HARD WIRED LIGHTING CONTROL) Note: switch and socket shall be client supplied item except for item no A.II. 5 | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 303000000 | Wiring for the following light points including wiring from energy saver to switch board, with 1.5 sq.mm PVC insulated copper conductor 1100 volts grade stranded flexible FRLS wires of approved make in embeded or surface mounted 25mm dia. heavy duty FRLS PVC conduit as per IS 9537 part-3 including fixing of 6 amps single pole rocker operted flush mounted switch of approved quality, colour, make & design in 1.6 mm thick GI box and earthing of fixtures and the outlet box with 1.5 sq.mm PVC insulated copper conductor stranded flexible FRLS wire. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.1 | 303000000 | Two point (Down light at vanity) , 1 nos JB for Magnifier glass & 1 nos JB for Heater Pad controlled by one 6 amps switch | [8 empty] | set | 200 | 400.9 | 0 | 400.9 | 30.0795 | 0 | 430.9795 | 176.185 | 21.7765 | 0 | 197.9615 | 86195.9054 | 39592.2932 | 125788 | 10 | 200 | 8018 | 0 | 8018 | 601.5905 | 0 | 8619.5905 | 3523.7 | 435.5293 | 0 | 3959.2293 | 12578.8199
1.2 | 303000000 | Two points (Down light in toilet), 2 nos JB for FTL lights controlled by one 6 amps switch | [8 empty] | set | 200 | 400.9 | 0 | 400.9 | 30.0795 | 0 | 430.9795 | 176.185 | 21.7765 | 0 | 197.9615 | 86195.9054 | 39592.2932 | 125788 | 10 | 200 | 8018 | 0 | 8018 | 601.5905 | 0 | 8619.5905 | 3523.7 | 435.5293 | 0 | 3959.2293 | 12578.8199
1.3 | 303000000 | One no reading light controlled by Electronic Dimmer switch suitable for 5 W led Adjustable down light. | [8 empty] | Pts | 400 | 500.07 | 0 | 500.07 | 37.5203 | 0 | 537.5903 | 207.835 | 25.6884 | 0 | 233.5234 | 215036.1008 | 93409.3624 | 308445 | 10 | 400 | 20002.8 | 0 | 20002.8 | 1500.8101 | 0 | 21503.6101 | 8313.4 | 1027.5362 | 0 | 9340.9362 | 30844.5463
1.4 | 303000000 | one points controlled by one 6 amps switch (Bed side light) | [8 empty] | Pts | 400 | 400.9 | 0 | 400.9 | 30.0795 | 0 | 430.9795 | 176.185 | 21.7765 | 0 | 197.9615 | 172391.8108 | 79184.5864 | 251576 | 10 | 400 | 16036 | 0 | 16036 | 1203.1811 | 0 | 17239.1811 | 7047.4 | 871.0586 | 0 | 7918.4586 | 25157.6397
2 | 303000000 | Wiring for the twin control light points with 1.5 sq.mm PVC insulated copper conductor 1100 volts grade stranded flexible FRLS wires in embeded or surface mounted 25mm dia. heavy duty FRLS PVC conduit as per IS 9537 part-3 . Light point shall be controlled by 2 nos. 6 amps 2 way rocker operated flush mounted switch of approved quality, colour, make & design in 1.6 mm thick GI box and earthing of fixture and the outlet box with 1.5 Sq.mm PVC insulated copper conductor stranded flexible FRLS wire. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.1 | 303000000 | Five point controlled by 2 Nos. 6 amp switch | [8 empty] | set. | 200 | 1041.285 | 0 | 1041.285 | 78.1276 | 0 | 1119.4126 | 351.315 | 43.4225 | 0 | 394.7375 | 223882.5227 | 78947.5068 | 302830 | 10 | 200 | 20825.7 | 0 | 20825.7 | 1562.5523 | 0 | 22388.2523 | 7026.3 | 868.4507 | 0 | 7894.7507 | 30283.003
2.2 | 303000000 | Six point controlled by 2 Nos. 6 amp switch | [8 empty] | set. | 0 | 2255.59 | 0 | 2255.59 | 169.2369 | 0 | 2424.8269 | 648.825 | 80.1948 | 0 | 729.0198 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.3 | 303000000 | Three point controlled by 2 nos. 6 amp switch | [8 empty] | set. | 200 | 899.915 | 0 | 899.915 | 67.5206 | 0 | 967.4356 | 334.435 | 41.3362 | 0 | 375.7712 | 193487.1245 | 75154.2332 | 268641 | 10 | 200 | 17998.3 | 0 | 17998.3 | 1350.4124 | 0 | 19348.7124 | 6688.7 | 826.7233 | 0 | 7515.4233 | 26864.1358
3 | 303000000 | Wiring for 250 volt single phase and neutral 6 amps switch socket outlet with 1.5 sq.mm PVC insulated copper conductor 1100 volts grade stranded flexible FRLS wires in surface mounted and or embeded 25mm dia. heavy duty FRLS PVC conduit as per IS 9537 part-3, including fixing of approved make and design in 1.6 mm thick GI box and fixing of 6 amps switch socket outlet with cover plate and earthing of third pin of the socket outlet and the GI box with 1.5 Sq.mm PVC insulated copper conductor stranded flexible FRLS wire. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.1 | 303000000 | 1 nos switch socket outlet | [8 empty] | Nos | 200 | 500.07 | 0 | 500.07 | 37.5203 | 0 | 537.5903 | 207.835 | 25.6884 | 0 | 233.5234 | 107518.0504 | 46704.6812 | 154223 | 10 | 200 | 10001.4 | 0 | 10001.4 | 750.405 | 0 | 10751.805 | 4156.7 | 513.7681 | 0 | 4670.4681 | 15422.2732
3.2 | 303000000 | 2 nos switch socket outlet | [8 empty] | Set | 400 | 699.465 | 0 | 699.465 | 52.4809 | 0 | 751.9459 | 271.135 | 33.5123 | 0 | 304.6473 | 300778.3436 | 121858.9144 | 422637 | 10 | 400 | 27978.6 | 0 | 27978.6 | 2099.2344 | 0 | 30077.8344 | 10845.4 | 1340.4914 | 0 | 12185.8914 | 42263.7258
3.3 | 303000000 | 3 nos switch socket outlet | [8 empty] | Set | 200 | 899.915 | 0 | 899.915 | 67.5206 | 0 | 967.4356 | 334.435 | 41.3362 | 0 | 375.7712 | 193487.1245 | 75154.2332 | 268641 | 10 | 200 | 17998.3 | 0 | 17998.3 | 1350.4124 | 0 | 19348.7124 | 6688.7 | 826.7233 | 0 | 7515.4233 | 26864.1358
3.4 | 303000000 | 4 nos switch socket outlet | [8 empty] | Set | 0 | 1397.875 | 0 | 1397.875 | 104.8826 | 0 | 1502.7576 | 491.63 | 60.7655 | 0 | 552.3955 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 303000000 | Wiring for 250 volts single phase and neutral 6/16 amps switched socket outlet with 4 sq.mm PVC insulated copper conductor 1100 volts grade stranded flexible FRLS wires in surface mounted and or embeded 25mm dia. heavy duty FRLS PVC conduit as per IS 9537 part-3, including fixing in 1.6 mm thick GI boxes nd earthing the third pin of socket outlet with 4 Sq. mm PVC insulated copper conductor standard flexible FRLS wire | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4.1 | 303000000 | 1 nos switch socket outlet | [8 empty] | Nos | 200 | 877.76 | 0 | 877.76 | 65.8583 | 0 | 943.6183 | 227.88 | 28.166 | 0 | 256.046 | 188723.6666 | 51209.1936 | 239933 | 10 | 200 | 17555.2 | 0 | 17555.2 | 1317.1667 | 0 | 18872.3667 | 4557.6 | 563.3194 | 0 | 5120.9194 | 23993.286
4.2 | 303000000 | 2 nos switch socket outlet | [8 empty] | Set | 400 | 1002.25 | 0 | 1002.25 | 75.1988 | 0 | 1077.4488 | 260.585 | 32.2083 | 0 | 292.7933 | 430979.527 | 117117.3224 | 548097 | 10 | 400 | 40090 | 0 | 40090 | 3007.9527 | 0 | 43097.9527 | 10423.4 | 1288.3322 | 0 | 11711.7322 | 54809.6849
5 | 303000000 | Wiring for fan coil unit including providing & fixing of 2 nos 250 volts single phase and neutral 6 amps switched socket outlet with 1.5 sq. mm. PVC insulated Copper conductor 1100 volts grade stranded flexible FRLS wires of approved make in 25mm dia. 2mm thick embeded and or surface mounted heavy duty FRLS PVC conduit and terminating the wire into the HVAC control box, (box to be provided by HVAC contractor free of cost) including the control wiring with 10 nos 1 sqmm PVC insulated Copper conductor 1100 volts grade stranded flexible FRLS wires from thermostat to FCU control box and wiring from Keytag holder to Energy saver unit above vestibult. | [8 empty] | set | 200 | 299.62 | 0 | 299.62 | 22.4805 | 0 | 322.1005 | 94.95 | 11.7358 | 0 | 106.6858 | 64420.0977 | 21337.164 | 85757 | 10 | 200 | 5992.4 | 0 | 5992.4 | 449.6098 | 0 | 6442.0098 | 1899 | 234.7164 | 0 | 2133.7164 | 8575.7262
6 | 303000000 | Wiring for light point for the ward robe with 1.5 sq.mm PVC insulated copper conductor 1100 volts grade stranded flexible FRLS Wires of approved make in embeded and or surface mounted 25mm dia. heavy duty FRLS PVC conduit as per IS 9537 part-3 including providing and fixing of 6 amps SP Micro switch | [8 empty] | Pts | 200 | 299.62 | 0 | 299.62 | 22.4805 | 0 | 322.1005 | 94.95 | 11.7358 | 0 | 106.6858 | 64420.0977 | 21337.164 | 85757 | 10 | 200 | 5992.4 | 0 | 5992.4 | 449.6098 | 0 | 6442.0098 | 1899 | 234.7164 | 0 | 2133.7164 | 8575.7262
7 | 303000000 | Receiving, storing, handling, fixing and connecting of energy saving unit for each Guest Room including embeded 25mm dia. heavy duty FRLS PVC conduit as per IS 9537 part-3 and wiring from energy saving unit to Key tag and earthing of box with 4 sq.mm PVC insulated copper conductor standed flexible FRLS wire. ( Unit will be supplied by the owner free of cost) | [8 empty] | Nos. | 200 | 450.485 | 0 | 450.485 | 33.7999 | 0 | 484.2849 | 147.7 | 18.2557 | 0 | 165.9557 | 96856.9779 | 33191.144 | 130048 | 10 | 200 | 9009.7 | 0 | 9009.7 | 675.9978 | 0 | 9685.6978 | 2954 | 365.1144 | 0 | 3319.1144 | 13004.8122
8 | 303000000 | Wiring for shaver unit with 2.5 sq. mm. PVC insulated copper conductor 1100 volts grade stranded flexible FRLS Wire of approved make in embeded 25mm dia. heavy duty FRLS PVC conduit as per IS 9537 part-3 including fixing of 1.6 MM thick GI box and fixing of shaver socket outlet with grid plate. Outlet box shall be earthed by 2.5 sq. mm. PVC insulated copper conductor stranded flexible FRLS wire. | [8 empty] | Nos. | 200 | 356.59 | 0 | 356.59 | 26.7549 | 0 | 383.3449 | 145.59 | 17.9949 | 0 | 163.5849 | 76668.9895 | 32716.9848 | 109386 | 10 | 200 | 7131.8 | 0 | 7131.8 | 535.099 | 0 | 7666.899 | 2911.8 | 359.8985 | 0 | 3271.6985 | 10938.5974
9 | 303000000 | Wiring for bell points with 1.5 sq. mm. PVC insulated copper conductor 1100 volts grade stranded flexible FRLS Wires in embeded and or surface mounted 25mm dia. heavy duty FRLS PVC conduit as per IS 9537 part-3 including fixing of electronic call bell and earthing of GI box with 1.5 sq mm PVC insulated copper conductor stranded flexible FRLS Wire. including receiving, storing, handling, installation, testing and commissioning of call bell | [8 empty] | Pts | 200 | 400.9 | 0 | 400.9 | 30.0795 | 0 | 430.9795 | 176.185 | 21.7765 | 0 | 197.9615 | 86195.9054 | 39592.2932 | 125788 | 10 | 200 | 8018 | 0 | 8018 | 601.5905 | 0 | 8619.5905 | 3523.7 | 435.5293 | 0 | 3959.2293 | 12578.8199
10 | 303000000 | Wiring for 250 volts single phase and neutral 16 amps switched socket outlet for hair dryer with 4 sq.mm PVC insulated copper conductor 1100 volts grade stranded flexible FRLS wires in surface mounted and or embeded 25mm dia. heavy duty FRLS PVC conduit as per IS 9537 part-3 including fixing of 1.6 mm thick GI box and fixing of 16 amps switch socket outlet with grid plate and earthing the third pin of socket outlet and GI box with 4 sq.mm PVC insulated copper conductor stranded flexible FRLS wire. | [8 empty] | Pts. | 200 | 450.485 | 0 | 450.485 | 33.7999 | 0 | 484.2849 | 147.7 | 18.2557 | 0 | 165.9557 | 96856.9779 | 33191.144 | 130048 | 10 | 200 | 9009.7 | 0 | 9009.7 | 675.9978 | 0 | 9685.6978 | 2954 | 365.1144 | 0 | 3319.1144 | 13004.8122
11 | 303000000 | Wiring for Do not disturb cum bell points with 1.5 sqmm PVC insulated copper conductor 1100 volts grade stranded flexible FRLS wires in surface mounted and or embeded 25mm dia. heavy duty FRLS PVC conduit as per IS 9537 part-3 and fixing of electronic call bell, bell will not operate when the DND switch is ON, neon indicating lamps on the plate of bell push button, two way switch with LED indicator on the suitable location and earthing of GI box with 1.5 sqmm PVC insulated copper conductor stranded flexible FRLS wire. | [8 empty] | Pts. | 200 | 600.295 | 0 | 600.295 | 45.0401 | 0 | 645.3351 | 239.485 | 29.6003 | 0 | 269.0853 | 129067.0268 | 53817.0692 | 182884 | 10 | 200 | 12005.9 | 0 | 12005.9 | 900.8027 | 0 | 12906.7027 | 4789.7 | 592.0069 | 0 | 5381.7069 | 18288.4096
12 | 303000000 | Wiring for forward and Reverse operation of Motorised Curtain point & centre off switch for forward and reverse operation of motor with 1.5 sq.mm PVC insulated copper conductor 1100 volts grade stranded flexible FRLS wire in 25mm dia. 2mm thick embeded or surface mounted PVC conduit in 1.6 mm thick GI box and earthing of GI box with 1.5 Sqmm PVC insulated copper conductor stranded flexible ZHFR wire. | [8 empty] | Pts. | 200 | 798.635 | 0 | 798.635 | 59.9216 | 0 | 858.5566 | 302.785 | 37.4242 | 0 | 340.2092 | 171711.3168 | 68041.8452 | 239753 | 10 | 200 | 15972.7 | 0 | 15972.7 | 1198.4317 | 0 | 17171.1317 | 6055.7 | 748.4845 | 0 | 6804.1845 | 23975.3162
13 | 303000000 | Supply and fixing of surface mounted/embeded FRLS heavy duty PVC conduit in following sizes including cost of junction boxes, bends, elbows, sockets, tees etc. laying in slab cutting chasis and making good including all fixing hardware ( Ceiling conduits in corridor) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13.1 | 303000000 | a 25 mm dia | [8 empty] | RM | 2500 | 40.09 | 0 | 40.09 | 3.008 | 0 | 43.098 | 25.32 | 3.1296 | 0 | 28.4496 | 107744.8818 | 71123.88 | 178869 | 10 | 2500 | 10022.5 | 0 | 10022.5 | 751.9882 | 0 | 10774.4882 | 6330 | 782.388 | 0 | 7112.388 | 17886.8762
13.2 | 303000000 | b 32 mm dia | [8 empty] | RM | 350 | 65.41 | 0 | 65.41 | 4.9077 | 0 | 70.3177 | 31.65 | 3.9119 | 0 | 35.5619 | 24611.1993 | 12446.679 | 37058 | 10 | 350 | 2289.35 | 0 | 2289.35 | 171.7699 | 0 | 2461.1199 | 1107.75 | 136.9179 | 0 | 1244.6679 | 3705.7878
14 | 303000000 | Providing and laying of PVC insulated copper conductor 1100 volt grade stranded flexible FRLS Wire in already laid conduit (Wiring from Floor Panel to Room DB, for Kitchen equipment) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14.1 | 303000000 | 3 nos - 4 sq.mm PVC insulated stranded flexible copper wires in conduit | [8 empty] | RM | 5000 | 93.895 | 0 | 93.895 | 7.0449 | 0 | 100.9399 | 32.705 | 4.0423 | 0 | 36.7473 | 504699.7092 | 183736.69 | 688436 | 10 | 5000 | 46947.5 | 0 | 46947.5 | 3522.4709 | 0 | 50469.9709 | 16352.5 | 2021.169 | 0 | 18373.669 | 68843.6399
14.2 | 303000000 | 3 nos - 6 sq.mm PVC insulated stranded flexible copper wires in conduit | [8 empty] | RM | 400 | 174.075 | 0 | 174.075 | 13.0608 | 0 | 187.1358 | 39.035 | 4.8247 | 0 | 43.8597 | 74854.3389 | 17543.8904 | 92398 | 10 | 400 | 6963 | 0 | 6963 | 522.4339 | 0 | 7485.4339 | 1561.4 | 192.989 | 0 | 1754.389 | 9239.8229
14.3 | 303000000 | 3 nos - 10 sq.mm PVC insulated stranded flexible copper wires in conduit | [8 empty] | RM | 150 | 323.885 | 0 | 323.885 | 24.3011 | 0 | 348.1861 | 50.64 | 6.2591 | 0 | 56.8991 | 52227.9137 | 8534.8656 | 60763 | 10 | 150 | 4858.275 | 0 | 4858.275 | 364.5164 | 0 | 5222.7914 | 759.6 | 93.8866 | 0 | 853.4866 | 6076.2779
A | 303000000 | CARPARK | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 303000000 | Wiring for following MCB controlled point for car park area with 2.5 sq.mm PVC insulated copper conductor 1100 volts grade stranded flexible FRLS wires in surface mounted 25mm dia heavy duty FRLS PVC conduit, including earthing of lighting fixture with 2.5 sq. mm. PVC insulated copper conductor stranded flexible FRLS wire (MCB not included). | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.1 | 303000000 | MCB controlled Primary point (from MCB to first light point) | [8 empty] | Pt | 28 | 4187.295 | 0 | 4187.295 | 314.1727 | 0 | 4501.4677 | 945 | 116.802 | 0 | 1061.802 | 126041.0968 | 29730.456 | 155772 | 10 | 28 | 11724.426 | 0 | 11724.426 | 879.6837 | 0 | 12604.1097 | 2646 | 327.0456 | 0 | 2973.0456 | 15577.1553
1.2 | 303000000 | MCB controlled Secondary point ( from point to point of same circuit) | [8 empty] | Pt | 90 | 976.93 | 0 | 976.93 | 73.2991 | 0 | 1050.2291 | 220 | 27.192 | 0 | 247.192 | 94520.6152 | 22247.28 | 116768 | 10 | 90 | 8792.37 | 0 | 8792.37 | 659.6915 | 0 | 9452.0615 | 1980 | 244.728 | 0 | 2224.728 | 11676.7895
B | 303000000 | RACEWAY & JUNCTION BOXES | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 303000000 | GI Raceway & Junction boxes | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.1 | 303000000 | Providing and fixing of overhead race way made from 1.6 mm thick pregalvenised steel sheet, factory fabricated, with internal partition of the following sizes including providing removable double folded cover of 1.6mm thick, knock out holes at regular interval, junction boxes and fixing accessories, earthing stud for terminating 8 SWG copper earth wire complete as required including supports, bends etc as per site requirement. The pregalvenised sheet shall be as per IS 277 or BS 2989 having tensile strength of minimum 500 N/sq.m. and minimum zinc coating of 275 GSM. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
a | 303000000 | 100 mm wide x 40 mm deep single compartment raceway | [8 empty] | RM | 730 | 339.71 | 0 | 339.71 | 25.4884 | 0 | 365.1984 | 164.58 | 20.3421 | 0 | 184.9221 | 266594.8621 | 134993.1242 | 401588 | 10 | 730 | 24798.83 | 0 | 24798.83 | 1860.6562 | 0 | 26659.4862 | 12014.34 | 1484.9724 | 0 | 13499.3124 | 40158.7986
b | 303000000 | 200 mm wide x 40 mm deep single compartment raceway | [8 empty] | RM | 50 | 610.845 | 0 | 610.845 | 45.8317 | 0 | 656.6767 | 177.24 | 21.9069 | 0 | 199.1469 | 32833.835 | 9957.3432 | 42791 | 10 | 50 | 3054.225 | 0 | 3054.225 | 229.1585 | 0 | 3283.3835 | 886.2 | 109.5343 | 0 | 995.7343 | 4279.1178
2 | 303000000 | Providing and fixing of 2 mm thick pregavanised sheet outlet junction box including providing cover with provision to adjust overall height, knock outs on four sides to accept raceways of specified sizes and cutouts to fix required outlets for following size of race ways. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
a | 303000000 | 150 mm wide x 40 mm deep single compatment raceway | [8 empty] | Nos | 12 | 490.575 | 0 | 490.575 | 36.8078 | 0 | 527.3828 | 164.58 | 20.3421 | 0 | 184.9221 | 6328.5941 | 2219.0651 | 8548 | 10 | 12 | 588.69 | 0 | 588.69 | 44.1694 | 0 | 632.8594 | 197.496 | 24.4105 | 0 | 221.9065 | 854.7659
b | 303000000 | 100 mm wide x 40 mm deep single compartment raceway | [8 empty] | Nos | 2 | 385.075 | 0 | 385.075 | 28.8922 | 0 | 413.9672 | 126.6 | 15.6478 | 0 | 142.2478 | 827.9344 | 284.4955 | 1112 | 10 | 2 | 77.015 | 0 | 77.015 | 5.7784 | 0 | 82.7934 | 25.32 | 3.1296 | 0 | 28.4496 | 111.243
C. | 303000000 | CABLES, MAINS, SUB MAINS AND CABLE TRAYS | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 303000000 | Supplying & laying of following 1100 volt grade XLPE insulated PVC inner sheathed and FRLS PVC outer sheathed aluminium conductor armoured cables as per specification in existing trenches, buried in soft soil, cable trays, ducts, clamped to wall with suitable clamps including, saddles fixing bolts, connecting testing and commissioning. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.1 | 303000000 | 3.1/2 core 300 sq. mm | [8 empty] | RM | 2400 | 1029.68 | 0 | 1029.68 | 77.2569 | 0 | 1106.9369 | 82.29 | 10.171 | 0 | 92.461 | 2656648.537 | 221906.5056 | 2878555 | 10 | 2400 | 247123.2 | 0 | 247123.2 | 18541.6537 | 0 | 265664.8537 | 19749.6 | 2441.0506 | 0 | 22190.6506 | 287855.5043
1.2 | 303000000 | 3.1/2 core 240 sq. mm. | [8 empty] | RM | 2350 | 845.055 | 0 | 845.055 | 63.4045 | 0 | 908.4595 | 75.96 | 9.3887 | 0 | 85.3487 | 2134879.7701 | 200569.3416 | 2335449 | 10 | 2350 | 198587.925 | 0 | 198587.925 | 14900.052 | 0 | 213487.977 | 17850.6 | 2206.3342 | 0 | 20056.9342 | 233544.9112
1.3 | 303000000 | 3.1/2 core 185 sq. mm. | [8 empty] | RM | 350 | 667.815 | 0 | 667.815 | 50.1062 | 0 | 717.9212 | 75.96 | 9.3887 | 0 | 85.3487 | 251272.4058 | 29872.0296 | 281144 | 10 | 350 | 23373.525 | 0 | 23373.525 | 1753.7156 | 0 | 25127.2406 | 2658.6 | 328.603 | 0 | 2987.203 | 28114.4435
1.4 | 303000000 | 3.1/2 core 120 sq.mm | [8 empty] | RM | 300 | 463.145 | 0 | 463.145 | 34.7498 | 0 | 497.8948 | 69.63 | 8.6063 | 0 | 78.2363 | 149368.4308 | 23470.8804 | 172839 | 10 | 300 | 13894.35 | 0 | 13894.35 | 1042.4931 | 0 | 14936.8431 | 2088.9 | 258.188 | 0 | 2347.088 | 17283.9311
1.5 | 303000000 | 3.1/2 core 50 sq. mm | [8 empty] | RM | 650 | 218.385 | 0 | 218.385 | 16.3854 | 0 | 234.7704 | 56.97 | 7.0415 | 0 | 64.0115 | 152600.7773 | 41607.4698 | 194208 | 10 | 650 | 14195.025 | 0 | 14195.025 | 1065.0527 | 0 | 15260.0777 | 3703.05 | 457.697 | 0 | 4160.747 | 19420.8247
1.6 | 303000000 | 4 core 35 sq. mm | [8 empty] | RM | 100 | 192.01 | 0 | 192.01 | 14.4065 | 0 | 206.4165 | 44.31 | 5.4767 | 0 | 49.7867 | 20641.651 | 4978.6716 | 25620 | 10 | 100 | 1920.1 | 0 | 1920.1 | 144.0651 | 0 | 2064.1651 | 443.1 | 54.7672 | 0 | 497.8672 | 2562.0323
1.7 | 303000000 | 4 core 25 sq. mm | [8 empty] | RM | 4750 | 151.92 | 0 | 151.92 | 11.3986 | 0 | 163.3186 | 25.32 | 3.1296 | 0 | 28.4496 | 775763.1486 | 135135.372 | 910899 | 10 | 4750 | 72162 | 0 | 72162 | 5414.3149 | 0 | 77576.3149 | 12027 | 1486.5372 | 0 | 13513.5372 | 91089.8521
2 | 303000000 | Supplying & laying of following 1100 volt grade XLPE insulated FRLS PVC outer sheathed copper conductor armoured cable as per specification in existing trenches, cable trays ducts , clamped to wall with suitable clamps, including fixing bolts, connecting testing and commissioning. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.1 | 303000000 | 4 core 16 sq.mm | [8 empty] | RM | 50 | 597.13 | 0 | 597.13 | 44.8027 | 0 | 641.9327 | 27.43 | 3.3903 | 0 | 30.8203 | 32096.6332 | 1541.0174 | 33638 | 10 | 50 | 2985.65 | 0 | 2985.65 | 224.0133 | 0 | 3209.6633 | 137.15 | 16.9517 | 0 | 154.1017 | 3363.7651
2.2 | 303000000 | 4 core 10 sq.mm | [8 empty] | RM | 100 | 405.12 | 0 | 405.12 | 30.3962 | 0 | 435.5162 | 23.21 | 2.8688 | 0 | 26.0788 | 43551.6154 | 2607.8756 | 46159 | 10 | 100 | 4051.2 | 0 | 4051.2 | 303.9615 | 0 | 4355.1615 | 232.1 | 28.6876 | 0 | 260.7876 | 4615.9491
2.3 | 303000000 | 4 core 4 sq.mm | [8 empty] | RM | 1950 | 188.845 | 0 | 188.845 | 14.169 | 0 | 203.014 | 14.77 | 1.8256 | 0 | 16.5956 | 395877.3787 | 32361.3654 | 428239 | 10 | 1950 | 36824.775 | 0 | 36824.775 | 2762.9629 | 0 | 39587.7379 | 2880.15 | 355.9865 | 0 | 3236.1365 | 42823.8744
2.4 | 303000000 | 3 core 4 sq.mm | [8 empty] | RM | 1450 | 149.81 | 0 | 149.81 | 11.2402 | 0 | 161.0502 | 14.77 | 1.8256 | 0 | 16.5956 | 233522.8542 | 24063.5794 | 257586 | 10 | 1450 | 21722.45 | 0 | 21722.45 | 1629.8354 | 0 | 23352.2854 | 2141.65 | 264.7079 | 0 | 2406.3579 | 25758.6434
2.5 | 303000000 | 4 core 2.5 sq.mm control cable | [8 empty] | RM | 25 | 129.765 | 0 | 129.765 | 9.7363 | 0 | 139.5013 | 14.77 | 1.8256 | 0 | 16.5956 | 3487.5317 | 414.8893 | 3902 | 10 | 25 | 324.4125 | 0 | 324.4125 | 24.3407 | 0 | 348.7532 | 36.925 | 4.5639 | 0 | 41.4889 | 390.2421
2.6 | 303000000 | 7 core 2.5 sq.mm control cable | [8 empty] | RM | 50 | 216.275 | 0 | 216.275 | 16.2271 | 0 | 232.5021 | 23.21 | 2.8688 | 0 | 26.0788 | 11625.1057 | 1303.9378 | 12929 | 10 | 50 | 1081.375 | 0 | 1081.375 | 81.1356 | 0 | 1162.5106 | 116.05 | 14.3438 | 0 | 130.3938 | 1292.9043
2.7 | 303000000 | 12 core 2.5 sq.mm control cable | [8 empty] | RM | 150 | 301.73 | 0 | 301.73 | 22.6388 | 0 | 324.3688 | 25.32 | 3.1296 | 0 | 28.4496 | 48655.3203 | 4267.4328 | 52923 | 10 | 150 | 4525.95 | 0 | 4525.95 | 339.582 | 0 | 4865.532 | 379.8 | 46.9433 | 0 | 426.7433 | 5292.2753
2.8 | 303000000 | 3 core 2.5 sq.mm (Flexible copper cable for swimming pool ltg) | [8 empty] | RM | 100 | 70.685 | 0 | 70.685 | 5.3035 | 0 | 75.9885 | 14.77 | 1.8256 | 0 | 16.5956 | 7598.8496 | 1659.5572 | 9258 | 10 | 100 | 706.85 | 0 | 706.85 | 53.035 | 0 | 759.885 | 147.7 | 18.2557 | 0 | 165.9557 | 925.8407
3 | 303000000 | Cable end termination of the following XLPE insulated FRLS PVC outer sheathed aluminium/copper conductor armoured cables of 1100 volt grade including supplying and fixing of bimettalic crimping lugs, double compression glands with earthing. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.1 | 303000000 | 3.1/2 core 300 sq. mm.Aluminium Cable | [8 empty] | Nos. | 100 | 2137.43 | 0 | 2137.43 | 160.3714 | 0 | 2297.8014 | 506.4 | 62.591 | 0 | 568.991 | 229780.1373 | 56899.104 | 286679 | 10 | 100 | 21374.3 | 0 | 21374.3 | 1603.7137 | 0 | 22978.0137 | 5064 | 625.9104 | 0 | 5689.9104 | 28667.9241
3.2 | 303000000 | 3.1/2 core 240 sq. mm. Aluminium Cable | [8 empty] | Nos. | 100 | 1826.205 | 0 | 1826.205 | 137.0202 | 0 | 1963.2252 | 443.1 | 54.7672 | 0 | 497.8672 | 196322.5161 | 49786.716 | 246109 | 10 | 100 | 18262.05 | 0 | 18262.05 | 1370.2016 | 0 | 19632.2516 | 4431 | 547.6716 | 0 | 4978.6716 | 24610.9232
3.3 | 303000000 | 3.1/2 core 185 sq. mm. Aluminium Cable | [8 empty] | Nos. | 14 | 1795.61 | 0 | 1795.61 | 134.7246 | 0 | 1930.3346 | 379.8 | 46.9433 | 0 | 426.7433 | 27024.6847 | 5974.4059 | 32999 | 10 | 14 | 2513.854 | 0 | 2513.854 | 188.6145 | 0 | 2702.4685 | 531.72 | 65.7206 | 0 | 597.4406 | 3299.9091
3.4 | 303000000 | 3.1/2 core 120 sq. mm. Aluminium Cable | [8 empty] | Nos. | 10 | 1113.025 | 0 | 1113.025 | 83.5103 | 0 | 1196.5353 | 284.85 | 35.2075 | 0 | 320.0575 | 11965.3527 | 3200.5746 | 15166 | 10 | 10 | 1113.025 | 0 | 1113.025 | 83.5103 | 0 | 1196.5353 | 284.85 | 35.2075 | 0 | 320.0575 | 1516.5927
3.5 | 303000000 | 3.1/2 core 50 sq. mm. Aluminium Cable | [8 empty] | Nos. | 56 | 651.99 | 0 | 651.99 | 48.9188 | 0 | 700.9088 | 189.9 | 23.4716 | 0 | 213.3716 | 39250.8933 | 11948.8118 | 51200 | 10 | 56 | 3651.144 | 0 | 3651.144 | 273.9453 | 0 | 3925.0893 | 1063.44 | 131.4412 | 0 | 1194.8812 | 5119.9705
3.6 | 303000000 | 4 core 35 sq. mm Aluminium Cable | [8 empty] | Nos. | 10 | 445.21 | 0 | 445.21 | 33.4041 | 0 | 478.6141 | 158.25 | 19.5597 | 0 | 177.8097 | 4786.1411 | 1778.097 | 6564 | 10 | 10 | 445.21 | 0 | 445.21 | 33.4041 | 0 | 478.6141 | 158.25 | 19.5597 | 0 | 177.8097 | 656.4238
3.7 | 303000000 | 4 core 25 sq. mm Aluminium Cable | [8 empty] | Nos. | 266 | 432.55 | 0 | 432.55 | 32.4542 | 0 | 465.0042 | 158.25 | 19.5597 | 0 | 177.8097 | 123691.1242 | 47297.3802 | 170989 | 10 | 266 | 11505.83 | 0 | 11505.83 | 863.2824 | 0 | 12369.1124 | 4209.45 | 520.288 | 0 | 4729.738 | 17098.8504
3.8 | 303000000 | 4 core 16 sq. mm copper cable | [8 empty] | Nos. | 4 | 418.835 | 0 | 418.835 | 31.4252 | 0 | 450.2602 | 126.6 | 15.6478 | 0 | 142.2478 | 1801.0408 | 568.991 | 2370 | 10 | 4 | 167.534 | 0 | 167.534 | 12.5701 | 0 | 180.1041 | 50.64 | 6.2591 | 0 | 56.8991 | 237.0032
3.9 | 303000000 | 4 core 10 sq. mm copper cable | [8 empty] | Nos. | 8 | 291.18 | 0 | 291.18 | 21.8472 | 0 | 313.0272 | 126.6 | 15.6478 | 0 | 142.2478 | 2504.2179 | 1137.9821 | 3642 | 10 | 8 | 232.944 | 0 | 232.944 | 17.4778 | 0 | 250.4218 | 101.28 | 12.5182 | 0 | 113.7982 | 364.22
3.1 | 303000000 | 4 core 4 sq. mm copper cable | [8 empty] | Nos. | 112 | 290.125 | 0 | 290.125 | 21.7681 | 0 | 311.8931 | 94.95 | 11.7358 | 0 | 106.6858 | 34932.0248 | 11948.8118 | 46881 | 10 | 112 | 3249.4 | 0 | 3249.4 | 243.8025 | 0 | 3493.2025 | 1063.44 | 131.4412 | 0 | 1194.8812 | 4688.0837
3.11 | 303000000 | 3 core 4 sq.mm copper cable | [8 empty] | Nos. | 66 | 285.905 | 0 | 285.905 | 21.4515 | 0 | 307.3565 | 94.95 | 11.7358 | 0 | 106.6858 | 20285.5258 | 7041.2641 | 27327 | 10 | 66 | 1886.973 | 0 | 1886.973 | 141.5796 | 0 | 2028.5526 | 626.67 | 77.4564 | 0 | 704.1264 | 2732.679
3.12 | 303000000 | 4 core 2.5 sq.mm copper cable | [8 empty] | Nos. | 8 | 285.905 | 0 | 285.905 | 21.4515 | 0 | 307.3565 | 94.95 | 11.7358 | 0 | 106.6858 | 2458.8516 | 853.4866 | 3312 | 10 | 8 | 228.724 | 0 | 228.724 | 17.1612 | 0 | 245.8852 | 75.96 | 9.3887 | 0 | 85.3487 | 331.2338
3.13 | 303000000 | 7 core 2.5 sq.mm copper cable | [8 empty] | Nos. | 8 | 286.96 | 0 | 286.96 | 21.5306 | 0 | 308.4906 | 94.95 | 11.7358 | 0 | 106.6858 | 2467.9249 | 853.4866 | 3321 | 10 | 8 | 229.568 | 0 | 229.568 | 17.2245 | 0 | 246.7925 | 75.96 | 9.3887 | 0 | 85.3487 | 332.1411
3.14 | 303000000 | 12 core 2.5 sq.mm copper cable | [8 empty] | Nos. | 4 | 291.18 | 0 | 291.18 | 21.8472 | 0 | 313.0272 | 158.25 | 19.5597 | 0 | 177.8097 | 1252.1089 | 711.2388 | 1963 | 10 | 4 | 116.472 | 0 | 116.472 | 8.7389 | 0 | 125.2109 | 63.3 | 7.8239 | 0 | 71.1239 | 196.3348
4 | 303000000 | Supply and installation of following RCC (NP-2 class) Hume pipe under paved areas, including providing 75 mm thick cement concrete all around pipe 1:3:6 (1 cement, 3 coarse sand and 6 crushed stone aggregate). | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4.1 | 303000000 | 100 mm dia ID | [8 empty] | RM | 25 | 327.05 | 0 | 327.05 | 24.5386 | 0 | 351.5886 | 126.6 | 15.6478 | 0 | 142.2478 | 8789.714 | 3556.194 | 12346 | 10 | 25 | 817.625 | 0 | 817.625 | 61.3464 | 0 | 878.9714 | 316.5 | 39.1194 | 0 | 355.6194 | 1234.5908
4.2 | 303000000 | 150 mm dia ID | [8 empty] | RM | 25 | 392.46 | 0 | 392.46 | 29.4463 | 0 | 421.9063 | 139.26 | 17.2125 | 0 | 156.4725 | 10547.6568 | 3911.8134 | 14459 | 10 | 25 | 981.15 | 0 | 981.15 | 73.6157 | 0 | 1054.7657 | 348.15 | 43.0313 | 0 | 391.1813 | 1445.947
5 | 303000000 | Providing and fixing of the following size medium class PVC pipe sleeves. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.1 | 303000000 | 100 mm. dia. | [8 empty] | RM | 25 | 327.05 | 0 | 327.05 | 24.5386 | 0 | 351.5886 | 126.6 | 15.6478 | 0 | 142.2478 | 8789.714 | 3556.194 | 12346 | 10 | 25 | 817.625 | 0 | 817.625 | 61.3464 | 0 | 878.9714 | 316.5 | 39.1194 | 0 | 355.6194 | 1234.5908
6 | 303000000 | Supply and fixing of factory fabricated Pregalvanized ( 120 GSM) GI ladder type cable trays, with radial bends, suspenders and supports as per specification and of the following sizes. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6.1 | 303000000 | 1200 mm wide | [8 empty] | RM | 200 | 1796.665 | 0 | 1796.665 | 134.8038 | 0 | 1931.4688 | 227.88 | 28.166 | 0 | 256.046 | 386293.755 | 51209.1936 | 437503 | 10 | 200 | 35933.3 | 0 | 35933.3 | 2696.0755 | 0 | 38629.3755 | 4557.6 | 563.3194 | 0 | 5120.9194 | 43750.2949
6.2 | 303000000 | 1000 mm wide | [8 empty] | RM | 325 | 1674.285 | 0 | 1674.285 | 125.6216 | 0 | 1799.9066 | 221.55 | 27.3836 | 0 | 248.9336 | 584969.6462 | 80903.4135 | 665873 | 10 | 325 | 54414.2625 | 0 | 54414.2625 | 4082.7021 | 0 | 58496.9646 | 7200.375 | 889.9663 | 0 | 8090.3413 | 66587.306
6.3 | 303000000 | 750 mm wide | [8 empty] | RM | 25 | 1136.235 | 0 | 1136.235 | 85.2517 | 0 | 1221.4867 | 202.56 | 25.0364 | 0 | 227.5964 | 30537.1678 | 5689.9104 | 36227 | 10 | 25 | 2840.5875 | 0 | 2840.5875 | 213.1293 | 0 | 3053.7168 | 506.4 | 62.591 | 0 | 568.991 | 3622.7078
6.4 | 303000000 | 600 mm wide | [8 empty] | RM | 75 | 1081.375 | 0 | 1081.375 | 81.1356 | 0 | 1162.5106 | 189.9 | 23.4716 | 0 | 213.3716 | 87188.2925 | 16002.873 | 103191 | 10 | 75 | 8110.3125 | 0 | 8110.3125 | 608.5167 | 0 | 8718.8292 | 1424.25 | 176.0373 | 0 | 1600.2873 | 10319.1165
6.5 | 303000000 | 450 mm wide | [8 empty] | RM | 285 | 783.865 | 0 | 783.865 | 58.8134 | 0 | 842.6784 | 170.91 | 21.1245 | 0 | 192.0345 | 240163.3414 | 54729.8257 | 294893 | 10 | 285 | 22340.1525 | 0 | 22340.1525 | 1676.1816 | 0 | 24016.3341 | 4870.935 | 602.0476 | 0 | 5472.9826 | 29489.3167
7 | 303000000 | Supply and fixing of perforated type factory fabricatedPregalvanized(120 GSM) GI cable trays of the following sizes including providing GI suspenders and supports as per specifications.. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7.1 | 303000000 | 300 mm wide | [8 empty] | RM | 400 | 643.55 | 0 | 643.55 | 48.2856 | 0 | 691.8356 | 151.92 | 18.7773 | 0 | 170.6973 | 276734.2226 | 68278.9248 | 345013 | 10 | 400 | 25742 | 0 | 25742 | 1931.4223 | 0 | 27673.4223 | 6076.8 | 751.0925 | 0 | 6827.8925 | 34501.3147
7.2 | 303000000 | 150 mm wide | [8 empty] | RM | 650 | 434.66 | 0 | 434.66 | 32.6125 | 0 | 467.2725 | 113.94 | 14.083 | 0 | 128.023 | 303727.1509 | 83214.9396 | 386942 | 10 | 650 | 28252.9 | 0 | 28252.9 | 2119.8151 | 0 | 30372.7151 | 7406.1 | 915.394 | 0 | 8321.494 | 38694.209
D. | 303000000 | DISTRIBUTION BOARDS / RISING MAINS | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
a | 303000000 | Design, fabrication, assembling, supply, installation, testing and commissioning of Main LT panel, Main Distribution Panels, Sub Distribution panels and Final Distribution panels suitable for 415 V, 3 phase, 50 Hz, 4 wire power supply system.Panels shall be fabricated out of 2 mm thick CRCA sheet steel in cubical formation, compartmentalized in Form 3b Construction, floor mounted, free standing and shall be dust and vermin proof. 3 mm thick cable gland plate, shall be provided both at the top and the bottom of the panel.Final distribution panels shall be fabricated out of 1.2mm & 1.6 mm thick CRCA sheet steel for SPN & TPN db respectively and shall be wall mounted. All large panels shall be provided with lifting hooks. Distribution panels shall be fabricated in accordance with the specifications. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 303000000 | Main LT Panel | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.1 | 303000000 | Section – I | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
A. | 303000000 | Incoming Air Circuit Breaker A For DG supply | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 303000000 | 1600 amps 4P manually operated fully drawout type air circuit breaker with built in microprocessor based release unit for protection and measurment as per specification and with following accessories : | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | Phase indicating light protected by 2 amps MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | Breaker ON / OFF / TRIP indicating lights with control MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | Under voltage release (only provision required) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iv. | 303000000 | 24 V DC Shunt trip coil | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
v. | 303000000 | 3 Nos. 96 x 96 mm sq. 0- 1600/ 5 amps CTR digital ammeter with 3 nos. 1600/ 5 amps 15 VA CL : 1 CTs | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
vi. | 303000000 | 96 x 96 mm sq. 0-500 Volt digital voltmeter with selector switch protected by 2 amp TP MCBs | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
vii. | 303000000 | Load Manager with RS 485 port | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
viii. | 303000000 | Breaker control switch | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
B. | 303000000 | Incoming Air Circuit Breaker B For Transformer supply | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 303000000 | 1600 amps 4 pole electrically operated fully drawout type air circuit breaker with built in microprocessor based release unit for protection and measurment as per specification and with following accessories : | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | Phase indicating light protected by 2 amps MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | Breaker ON / OFF / TRIP indicating lights with control MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | Under voltage release | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iv. | 303000000 | 24 V DC Shunt trip coil | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
v | 303000000 | Under voltage relay with timer (27) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
vi. | 303000000 | Over voltage relay with timer (59) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
vii. | 303000000 | Load Manager with RS 485 port | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
viii | 303000000 | Breaker control switch | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ix. | 303000000 | 3 Nos. 96 x 96 sq.mm 0- 1600 / 5 amps CTR digital ammeter with 3 nos 1600 / 5 amps, 15 VA Class I CTs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
x. | 303000000 | 96 x 96 mm sq. 0-500 Volt digital voltmeter with selector switch protected by 2 amp TP MCBs | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
xi. | 303000000 | Class – B surge arrestor (Lines to Neutral) & (Neutral to Earth) suitable for 3 phases. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 1600 Amps rating Auto Transfer Switch with overlapping neutral , In phase open transition, without Bypass and with required WCR suitable for main lt panel application with 25 KA as per specification. ASCO 7000 series or equivalent. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | DELETED on 06.05.13 | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Bus Bars | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 1600 amps 4 pole (25 KA) copper bus bars with colour coded heat shrinkable insulating sleeves | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
C. | 303000000 | Outgoing | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | 800 amps 4 pole manually operated fully drawout type air circuit breaker with ON/OFF/TRIP indicating lamps with MCBs and microprocessor based release for protection & indication as per specification. (for HVAC panel) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | 630 amps 4 pole MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | 400 amps 4 pole MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iv. | 303000000 | 250 amps 4 pole MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 303000000 | Spare MCCBs for the following : | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | 250 amps 4 pole MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | 400 amps 4 pole MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
D. | 303000000 | Bus Coupler : Breaker C | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 303000000 | 1600 amps 4 pole manually Electrically operated fully drawout type air circuit breaker with ON / OFF / TRIP indicating lamps with control MCBs, shunt trip, breaker control switch etc. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.1 | 303000000 | Changed on 06.05.13 | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E. | 303000000 | Incoming Air Circuit Breaker D For transformer supply | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 303000000 | 1600 amps 4P electrically operated fully drawout type air circuit breaker with built in microprocessor based release unit for protection & measurment as per specification and with following accessories : | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | Phase indicating light protected by 2 amps MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | Breaker ON / OFF / TRIP indicating lights with control MCBs | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | Under voltage release | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iv. | 303000000 | 24 V DC Shunt trip coil. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
v | 303000000 | Under voltage relay with timer (27) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
vi. | 303000000 | Over voltage relay with timer (59) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
vii. | 303000000 | Load Manager with RS 485 port | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
viii. | 303000000 | Breaker control switch | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ix. | 303000000 | 3 Nos. 96 x 96 sq.mm 0- 1600 / 5 amps CTR digital ammeter with 3 nos 1600 / 5 amps, 15 VA Class I CTs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
x. | 303000000 | 96 x 96 mm sq. 0-500 Volt digital voltmeter with selector switch protected by 2 amp TP MCBs | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
xi. | 303000000 | Class – B surge arrestor (Lines to Neutral) & (Neutral to Earth) suitable for 3 phases. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 1600 Amps rating Auto Transfer Switch with overlapping neutral , In phase open transition, without Bypass and with required WCR suitable for main lt panel application with 25 KA as per specification. ASCO 7000 series or equivalent. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Deleted on 06.05.13 | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
F. | 303000000 | Incoming Air Circuit Breaker E (For DG Supply) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 303000000 | 1600 amps 4P manually Electrically operated fully drawout type air circuit breaker with built in microprocessor based release unit for protection and measurment as per specification and with following accessories : | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.1 | 303000000 | changed on 06.05.13 | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | Phase indicating light protected by 2 amps MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | Breaker ON / OFF / TRIP indicating lights with control MCBs | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | Under voltage release (only provision required) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iv. | 303000000 | 24 V DC Shunt trip coil | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
v | 303000000 | 3 Nos. 96 x 96 mm sq. 0-1600/ 5 amps CTR digital ammeter with 3 Nos. 1600/ 5 amps 15 VA CL:1 CTs | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
vi. | 303000000 | 96 x 96 mm sq 0-500 Volt digital voltmeter with selector switch PTs shall be protected by 2 amp TP MCBs | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
vii. | 303000000 | Load Manager with RS 485 port | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
viii. | 303000000 | Breaker control switch | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Bus Bars | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 1600 amps 4 pole manually operated fully drawout type air circuit breaker with ON / OFF / TRIP indicating lamps with control MCBs, shunt trip, breaker control switch etc. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
G. | 303000000 | Outgoing | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | 1000 amps 4 pole manually operated fully drawout type air circuit breaker with ON/OFF/TRIP indicating lamps with MCBs and microprocessor based release for protection & indication as per specification. (for fire emergency panel) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | 800 amps 4 pole manually operated fully drawout type air circuit breaker with ON/OFF/TRIP indicating lamps with MCBs and microprocessor based release for protection & indication as per specification. (for HVAC panel ) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | 630 amps 4 pole MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iv. | 303000000 | 400 amps 4 pole MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
v. | 303000000 | 250 amps 4 pole MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Spare MCCBs for the following : | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | 250 amps 4 pole MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | 400 amps 4 pole MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Notes : | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | All outgoing feeders shall have suitable range of followings (except capacitor feeders) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | a. Digital electronic KWH meter with RS 485 port including spare. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | b. Digital electronic ammeter with selector switch and 3 Nos. CTs including spare. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | c. Three phase indicating lamps protected by 2 amps SP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | d. Nos. 630 / 5, 15 VA CTs shall be provided for APFCR | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | All breakers shall be electrically/ mechanically interlocked as per schematic diagram. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | All MCCBs shall be suitable for 25 KA (ICS) breaking capacity. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iv. | 303000000 | All ACBs shall be suitable for 25 kA( Icu=Ics=Icw for 1 sec.) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
v. | 303000000 | 415 / 110 V suitable rating control transformer shall be provided for aux. Control supply | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
vi. | 303000000 | Wiring with space heater, thermostat and control MCBs shall be provided all vertical sections of main LT panel. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
vii. | 303000000 | All outgoing MCCBs feeders shall be provided with built-in microprocessor release unit with earth fault protection and time delay. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
viii. | 303000000 | All incoming as well as outgoing feeders shall have pad locking facility. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ix. | 303000000 | suitable danger board shall be provided. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
x. | 303000000 | All bus bar section / backside panels shall have pad locking facility and hinged type door. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Main LT Panel as described above. | [8 empty] | Set | 1 | 6631568.585 | 0 | 6631568.585 | 497566.5909 | 0 | 7129135.1759 | 101280 | 12518.208 | 0 | 113798.208 | 7129135.1759 | 113798.208 | 7242933 | 10 | 1 | 663156.8585 | 0 | 663156.8585 | 49756.6591 | 0 | 712913.5176 | 10128 | 1251.8208 | 0 | 11379.8208 | 724293.3384
2 | 303000000 | FIRE EMERGENCY PANEL | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 303000000 | Incoming | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.1 | 303000000 | 2 Nos. 1000 amps 4P manually operated drawout type ACB electromechanically and castle key interlocked. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.2 | 303000000 | i) 0-500 volts digital volt meter with selector switch be protected by 2 amps TP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.3 | 303000000 | ii) 0-1000. digital ammeter with selector switch and digital type KWH meter with 1000 / 5 amps 15 VA, CL 1 epoxy cast resin CTs | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.4 | 303000000 | iii) .Phase indicating light protected by 2 amps SP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.5 | 303000000 | Bus Bars | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.6 | 303000000 | 1000 amps TPN (25 KA for 1 Sec.) copper bus bars with Heat Shrinkable insulated sleeves | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 303000000 | Outgoings | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.1 | 303000000 | 400 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.2 | 303000000 | 250 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.3 | 303000000 | 160 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.4 | 303000000 | 100 amps TPN MCCBs | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.5 | 303000000 | Spare MCCBs of the following : | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.6 | 303000000 | 100 amps TPN MCCBs | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.7 | 303000000 | All outgoing MCCBs shall be of 25 KA breaking capacity | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.8 | 303000000 | FIRE EMERGENCY PANEL as described above | [8 empty] | No. | 1 | 969119.835 | 0 | 969119.835 | 72713.0612 | 0 | 1041832.8962 | 18990 | 2347.164 | 0 | 21337.164 | 1041832.8962 | 21337.164 | 1063170 | 10 | 1 | 96911.9835 | 0 | 96911.9835 | 7271.3061 | 0 | 104183.2896 | 1899 | 234.7164 | 0 | 2133.7164 | 106317.006
3 | 303000000 | MDB PUBLIC & COMMON AREA LIGHTING | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 303000000 | Incoming | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | 400 Amps rating power Manual Change over switch suitable for 25 kA system fault level as per specification. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | 400 amps TPN MCCB with following accessories: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | 0-500 volts digital volt meter with selector switch be protected by 2 amps TP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iv. | 303000000 | 0- 400 Amps digital electronic ammeter with selector switch and 400 /5 amps 15 VA, CL 1 CTs . | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
v. | 303000000 | Phase indicating light protected by 2 amps SP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Bus Bars | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 400 amps TPN aluminium bus bars with coloured heat shrinkable insulated sleeve. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 303000000 | Outgoing | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 250 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 100 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Spare MCCBs of the following : | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 100 amps TPN MCCBs | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | All MCCBs shall be of 25 KA (Ics) breaking capacity. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | MDB LIGHTING described as above | [8 empty] | Set | 1 | 198234.5 | 0 | 198234.5 | 14873.5345 | 0 | 213108.0345 | 10128 | 1251.8208 | 0 | 11379.8208 | 213108.0345 | 11379.8208 | 224488 | 10 | 1 | 19823.45 | 0 | 19823.45 | 1487.3535 | 0 | 21310.8035 | 1012.8 | 125.1821 | 0 | 1137.9821 | 22448.7855
4 | 303000000 | MDB POWER -1 | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Incoming | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 630 amps TPN MCCB with following accessories: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | 0-500 volts digital volt meter with selector switch be protected by 2 amps TP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | 0- 630 Amps digital electronic ammeter with selector switch and 630 /5 amps 15 VA, CL 1 CTs . | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | Phase indicating light protected by 2 amps SP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Bus Bars | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 630 amps (25 KA) TPN aluminium bus bars with heat shrinkable insulation sleeve. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Outgoing | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 200 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 160 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Spare MCCBs of the following: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 160 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | All MCCBs shall be of 25KA( Ics) breaking capacity. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | MD POWER- 1 described as above | [8 empty] | No. | 1 | 221686.095 | 0 | 221686.095 | 16633.1077 | 0 | 238319.2027 | 10128 | 1251.8208 | 0 | 11379.8208 | 238319.2027 | 11379.8208 | 249699 | 10 | 1 | 22168.6095 | 0 | 22168.6095 | 1663.3108 | 0 | 23831.9203 | 1012.8 | 125.1821 | 0 | 1137.9821 | 24969.9024
5 | 303000000 | MDB POWER -2 | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Incoming | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 250 amps TPN MCCB (25 KA) with following accessories: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | 0-500 volts digital volt meter with selector switch be protected by 2 amps TP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | 0- 250 Amps digital electronic ammeter with selector switch and 3 nos 250/5 amps 15 VA, CL 1 CTs . | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | Phase indicating light protected by 2 amps SP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Bus Bars | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 250 amps TPN aluminium bus bars with heat shrinkable insulation sleeve. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Outgoing | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 100 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 amps TPN MCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Spare MCCBs of the following: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 100 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 amps TPN MCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | All MCCBs shall be of 25KA(Ics) breaking capacity. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | MD POWER -2 described as above | [8 empty] | No. | 1 | 96645.385 | 0 | 96645.385 | 7251.3032 | 0 | 103896.6882 | 10128 | 1251.8208 | 0 | 11379.8208 | 103896.6882 | 11379.8208 | 115277 | 10 | 1 | 9664.5385 | 0 | 9664.5385 | 725.1303 | 0 | 10389.6688 | 1012.8 | 125.1821 | 0 | 1137.9821 | 11527.6509
6 | 303000000 | MDB POWER -3 | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Incoming | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 250 amps TPN MCCB (25 KA) with following accessories: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | 0-500 volts digital volt meter with selector switch be protected by 2 amps TP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | 0- 250 Amps digital electronic ammeter with selector switch and 3 nos 250/5 amps 5 VA, CL 1 CTs . | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | Phase indicating light protected by 2 amps SP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Bus Bars | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 250 amps TPN aluminium bus bars with heat shrinkable insulation sleeve. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Outgoing | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 100 amps TPN MCCB (FOR UPS BYPASS) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 amps TPN MCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Spare MCCBs of the following: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 amps TPN MCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | All MCCBs shall be of 25 KA(Ics) breaking capacity. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | MD POWER -3 described as above | [8 empty] | No. | 1 | 94850.83 | 0 | 94850.83 | 7116.6578 | 0 | 101967.4878 | 10128 | 1251.8208 | 0 | 11379.8208 | 101967.4878 | 11379.8208 | 113347 | 10 | 1 | 9485.083 | 0 | 9485.083 | 711.6658 | 0 | 10196.7488 | 1012.8 | 125.1821 | 0 | 1137.9821 | 11334.7309
7 | 303000000 | MDB AHU & VENTILATION | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Incoming | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 400 amps TPN MCCB (25KA) with following accessories: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | 0-500 volts digital volt meter with selector switch be protected by 2 amps TP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | 0- 400 Amps digital electronic ammeter with selector switch and 3 nos 400/5 amps 5 VA, CL 1 CTs . | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | Phase indicating light protected by 2 amps SP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Bus Bars | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 400 amps (25 KA) TPN aluminium bus bars with heat shrinkable insulation sleeve. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Outgoing | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 160 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 100 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Spare MCCBs of the following: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 100 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | All MCCBs shall be of 25 KA(Ics) breaking capacity. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | MDB AHU & VENTILATION described as above | [8 empty] | No. | 1 | 146089.015 | 0 | 146089.015 | 10961.0588 | 0 | 157050.0738 | 11394 | 1408.2984 | 0 | 12802.2984 | 157050.0738 | 12802.2984 | 169852 | 10 | 1 | 14608.9015 | 0 | 14608.9015 | 1096.1059 | 0 | 15705.0074 | 1139.4 | 140.8298 | 0 | 1280.2298 | 16985.2372
8 | 303000000 | MDB KITCHEN | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Incoming | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 630 amps TPN MCCB (25KA) with following accessories: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | 0-500 volts digital volt meter with selector switch be protected by 2 amps TP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | 0- 630 Amps digital electronic ammeter with selector switch and 3 nos 630/5 amps 15 VA, CL 1 CTs . | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | Phase indicating light protected by 2 amps SP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Bus Bars | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 630 amps (25 KA) TPN aluminium bus bars with heat shrinkable insulation sleeve. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Outgoing | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 315 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 250 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 200 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Spare MCCBs of the following: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 160 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 100 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | All MCCBs shall be of 25 KA(Ics) breaking capacity. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | MDB KITCHEN described as above | [8 empty] | No. | 1 | 218191.935 | 0 | 218191.935 | 16370.9409 | 0 | 234562.8759 | 8862 | 1095.3432 | 0 | 9957.3432 | 234562.8759 | 9957.3432 | 244520 | 10 | 1 | 21819.1935 | 0 | 21819.1935 | 1637.0941 | 0 | 23456.2876 | 886.2 | 109.5343 | 0 | 995.7343 | 24452.0219
9 | 303000000 | FIRE VENTILATION DB. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Incoming | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 400 amps TPN MCCB (25KA) with following accessories: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | 0-500 volts digital volt meter with selector switch be protected by 2 amps TP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | 0- 400 Amps digital electronic ammeter with selector switch and 3 nos 400/5 amps 15 VA, CL 1 CTs . | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | Phase indicating light protected by 2 amps SP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Bus Bars | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 400 amps (25 KA) TPN aluminium bus bars with heat shrinkable insulation sleeve. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Outgoing | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 100 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 80 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 25 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Spare MCCBs of the following: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | All MCCBs shall be of 25 KA(Ics) breaking capacity. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | FIRE VENTILATION DB described as above | [8 empty] | No. | 1 | 143765.905 | 0 | 143765.905 | 10786.7559 | 0 | 154552.6609 | 8862 | 1095.3432 | 0 | 9957.3432 | 154552.6609 | 9957.3432 | 164510 | 10 | 1 | 14376.5905 | 0 | 14376.5905 | 1078.6756 | 0 | 15455.2661 | 886.2 | 109.5343 | 0 | 995.7343 | 16451.0004
10 | 303000000 | MDB ELEVATOR. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Incoming | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 250 amps TPN MCCB (25KA) with following accessories: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | 0-500 volts digital volt meter with selector switch be protected by 2 amps TP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | 0- 250 Amps digital electronic ammeter with selector switch and 3 nos 250/5 amps 15 VA, CL 1 CTs . | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | Digital electronic KWH meter with RS 485 port . | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iv. | 303000000 | Phase indicating light protected by 2 amps SP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Bus Bars | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 250 amps (25 KA) TPN aluminium bus bars with heat shrinkable insulation sleeve. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Outgoing | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 40 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Spare MCCBs of the following: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Note: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | a. All MCCBs shall be of 25 KA(Ics) breaking capacity. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | b. Digital electronic ammeter with selector switch and 3 Nos. CTs | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | MDB ELEVATOR described as above | [8 empty] | No. | 1 | 161166.02 | 0 | 161166.02 | 12092.2865 | 0 | 173258.3065 | 11394 | 1408.2984 | 0 | 12802.2984 | 173258.3065 | 12802.2984 | 186061 | 10 | 1 | 16116.602 | 0 | 16116.602 | 1209.2286 | 0 | 17325.8306 | 1139.4 | 140.8298 | 0 | 1280.2298 | 18606.0605
11 | 303000000 | SDB FIRE EMERGENCY TERRACE. (IP 55) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Incoming | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 160 amps TPN MCCB (25KA) with following accessories: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | 0-500 volts digital volt meter with selector switch be protected by 2 amps TP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | 0- 160 Amps digital electronic ammeter with selector switch and 3 nos 160/5 amps 15 VA, CL 1 CTs . | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | Phase indicating light protected by 2 amps SP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Bus Bars | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 160 amps (25 KA) TPN aluminium bus bars with heat shrinkable insulation sleeve. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Outgoing | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 25 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 32 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Spare MCCBs of the following: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 40 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | All MCCBs shall be of 25 KA(Ics) breaking capacity. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | SDB FIRE EMERGENCY TERRACE described as above | [8 empty] | No. | 1 | 184020.485 | 0 | 184020.485 | 13807.057 | 0 | 197827.542 | 11394 | 1408.2984 | 0 | 12802.2984 | 197827.542 | 12802.2984 | 210630 | 10 | 1 | 18402.0485 | 0 | 18402.0485 | 1380.7057 | 0 | 19782.7542 | 1139.4 | 140.8298 | 0 | 1280.2298 | 21062.984
12 | 303000000 | SDB EMRGENCY LTG GUEST FLOOR | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Incoming | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 amps TPN MCCB (25KA) with following accessories: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | 0-500 volts digital volt meter with selector switch be protected by 2 amps TP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | 0- 63 Amps digital electronic ammeter with selector switch and 3 nos 63/5 amps 15 VA, CL 1 CTs . | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | Phase indicating light protected by 2 amps SP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Bus Bars | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 amps 4 pole aluminium bus bars with heat shrinkable insulation sleeve. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Outgoing | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 25 Amps DP MCBs | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Spare MCCBs of the following: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 25 Amps DP MCBs | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | SDB EMRGENCY LTG GUEST FLOOR described as above | [8 empty] | No. | 1 | 49518.535 | 0 | 49518.535 | 3715.3757 | 0 | 53233.9107 | 5064 | 625.9104 | 0 | 5689.9104 | 53233.9107 | 5689.9104 | 58924 | 10 | 1 | 4951.8535 | 0 | 4951.8535 | 371.5376 | 0 | 5323.3911 | 506.4 | 62.591 | 0 | 568.991 | 5892.3821
13 | 303000000 | SDB LTG-1 PUBLIC AREA | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Incoming | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 250 amps TPN MCCB (25KA) (Thermal magnetic release) with following accessories: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | 0-500 volts digital volt meter with selector switch be protected by 2 amps TP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | 0- 250 Amps digital electronic ammeter with selector switch and 3 nos 250/5 amps 15 VA, CL 1 CTs . | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | [9 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | Phase indicating light protected by 2 amps SP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | [9 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iv | 303000000 | Class – C surge arrestor (Lines to Neutral) & (Neutral to Earth) suitable for 3 phases with backup MCB protection of suitable rating. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Bus Bars | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 250 amps TPN aluminium bus bars with heat shrinkable insulation sleeve. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Outgoing | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 40 Amps 4P MCB and 40 Amps DP RCCB of 30 mA | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 40 amps TPN MCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Spare MCCBs of the following: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 40 amps TPN MCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 40 Amps 4P MCB and 40 Amps DP RCCB of 30 mA | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | SDB LTG PUBLIC AREA described as above | [8 empty] | No. | 1 | 139696.77 | 0 | 139696.77 | 10481.4487 | 0 | 150178.2187 | 8862 | 1095.3432 | 0 | 9957.3432 | 150178.2187 | 9957.3432 | 160136 | 10 | 1 | 13969.677 | 0 | 13969.677 | 1048.1449 | 0 | 15017.8219 | 886.2 | 109.5343 | 0 | 995.7343 | 16013.5562
14 | 303000000 | SDB LTG-2 BOH AREA | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Incoming | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 100 amps TPN MCCB (25KA) with following accessories: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | 0-500 volts digital volt meter with selector switch be protected by 2 amps TP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | 0- 100 Amps digital electronic ammeter with selector switch and 3 nos 100/5 amps 5 VA, CL 1 CTs . | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | Phase indicating light protected by 2 amps SP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iv | 303000000 | Class – C surge arrestor (Lines to Neutral) & (Neutral to Earth) suitable for 3 phases with backup MCB protection of suitable rating. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Bus Bars | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 100 amps TPN aluminium bus bars with heat shrinkable insulation sleeve. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Outgoing | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 40 amps TPN MCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Spare MCCBs of the following: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 40 amps TPN MCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | SDB LTG-2 BOH AREA described as above | [8 empty] | No. | 1 | 76348.24 | 0 | 76348.24 | 5728.4084 | 0 | 82076.6484 | 6330 | 782.388 | 0 | 7112.388 | 82076.6484 | 7112.388 | 89189 | 10 | 1 | 7634.824 | 0 | 7634.824 | 572.8408 | 0 | 8207.6648 | 633 | 78.2388 | 0 | 711.2388 | 8918.9036
15 | 303000000 | SDB LAUNDRY | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Incoming | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 160 amps TPN MCCB (25KA) with following accessories: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | 0-500 volts digital volt meter with selector switch be protected by 2 amps TP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | 0- 160 Amps digital electronic ammeter with selector switch and 3 nos 160/5 amps 5 VA, CL 1 CTs . | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | Phase indicating light protected by 2 amps SP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iv | 303000000 | Class – C surge arrestor (Lines to Neutral) & (Neutral to Earth) suitable for 3 phases with backup MCB protection of suitable rating. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Bus Bars | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 160 amps TPN aluminium bus bars with heat shrinkable insulation sleeve. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Outgoing | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 amps TPN MCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Spare MCCBs of the following: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 amps TPN MCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | SDB LAUNDRY described as above | [8 empty] | No. | 1 | 64980.615 | 0 | 64980.615 | 4875.4955 | 0 | 69856.1105 | 6330 | 782.388 | 0 | 7112.388 | 69856.1105 | 7112.388 | 76968 | 10 | 1 | 6498.0615 | 0 | 6498.0615 | 487.5496 | 0 | 6985.6111 | 633 | 78.2388 | 0 | 711.2388 | 7696.8499
16 | 303000000 | MDB UPS. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Incoming | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 100 amps TPN MCCB ISOLATOR with following accessories: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | 0-500 volts digital volt meter with selector switch be protected by 2 amps TP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | 0- 1000 Amps digital electronic ammeter with selector switch and 3 nos 100/5 amps 15 VA, CL 1 CTs . | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | Digital electronic KWH meter with RS 485 port . | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iv. | 303000000 | Phase indicating light protected by 2 amps SP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Bus Bars | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 160 amps (10 KA) TPN aluminium bus bars with heat shrinkable insulation sleeve. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Outgoing | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 amps TPN MCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Spare MCBs of the following: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | MDB UPS described as above | [8 empty] | No. | 1 | 73500.795 | 0 | 73500.795 | 5514.7646 | 0 | 79015.5596 | 7596 | 938.8656 | 0 | 8534.8656 | 79015.5596 | 8534.8656 | 87550 | 10 | 1 | 7350.0795 | 0 | 7350.0795 | 551.4765 | 0 | 7901.556 | 759.6 | 93.8866 | 0 | 853.4866 | 8755.0425
17 | 303000000 | SDB AHU & VENTILATION BASEMENT-2. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Incoming | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 100 amps TPN MCCB (25KA) with following accessories: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | 0-500 volts digital volt meter with selector switch be protected by 2 amps TP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | 0- 100 Amps digital electronic ammeter with selector switch and 3 nos 100/5 amps 15 VA, CL 1 CTs . | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | Phase indicating light protected by 2 amps SP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Bus Bars | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 100 amps TPN aluminium bus bars with heat shrinkable insulation sleeve. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Outgoing | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 25 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Spare MCCBs of the following: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 25 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | All MCCBs shall be of 25 KA(Ics) breaking capacity. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | SDB AHU & VENTILATION BASEMENT-2 described as above | [8 empty] | No. | 1 | 136226.875 | 0 | 136226.875 | 10221.1024 | 0 | 146447.9774 | 8862 | 1095.3432 | 0 | 9957.3432 | 146447.9774 | 9957.3432 | 156405 | 10 | 1 | 13622.6875 | 0 | 13622.6875 | 1022.1102 | 0 | 14644.7977 | 886.2 | 109.5343 | 0 | 995.7343 | 15640.5321
18 | 303000000 | SDB AHU & VENTILATION BASEMENT-1. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Incoming | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 100 amps TPN MCCB (25KA) with following accessories: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | 0-500 volts digital volt meter with selector switch be protected by 2 amps TP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | 0- 100 Amps digital electronic ammeter with selector switch and 3 nos 100/5 amps 15 VA, CL 1 CTs . | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | Phase indicating light protected by 2 amps SP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Bus Bars | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 100 amps TPN aluminium bus bars with heat shrinkable insulation sleeve. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Outgoing | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 25 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Spare MCCBs of the following: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 25 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | All MCCBs shall be of 25 KA(Ics) breaking capacity. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | SDB AHU & VENTILATION BASEMENT-1 described as above | [8 empty] | No. | 1 | 148090.35 | 0 | 148090.35 | 11111.219 | 0 | 159201.569 | 8862 | 1095.3432 | 0 | 9957.3432 | 159201.569 | 9957.3432 | 169159 | 10 | 1 | 14809.035 | 0 | 14809.035 | 1111.1219 | 0 | 15920.1569 | 886.2 | 109.5343 | 0 | 995.7343 | 16915.8912
19 | 303000000 | SDB AHU & VENTILATION GROUND. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Incoming | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 100 amps TPN MCCB (25KA) with following accessories: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | 0-500 volts digital volt meter with selector switch be protected by 2 amps TP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | 0- 100 Amps digital electronic ammeter with selector switch and 3 nos 100/5 amps 15 VA, CL 1 CTs . | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | Phase indicating light protected by 2 amps SP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Bus Bars | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 100 amps TPN aluminium bus bars with heat shrinkable insulation sleeve. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Outgoing | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 25 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Spare MCCBs of the following: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 25 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | All MCCBs shall be of 25 KA(Ics) breaking capacity. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | SDB AHU & VENTILATION GROUND described as above | [8 empty] | No. | 1 | 125936.405 | 0 | 125936.405 | 9449.0085 | 0 | 135385.4135 | 8862 | 1095.3432 | 0 | 9957.3432 | 135385.4135 | 9957.3432 | 145343 | 10 | 1 | 12593.6405 | 0 | 12593.6405 | 944.9008 | 0 | 13538.5413 | 886.2 | 109.5343 | 0 | 995.7343 | 14534.2757
20 | 303000000 | SDB AHU & VENTILATION TRANSFER FLOOR-01. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Incoming | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 160 amps TPN MCCB (25KA) with following accessories: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | 0-500 volts digital volt meter with selector switch be protected by 2 amps TP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | 0- 160 Amps digital electronic ammeter with selector switch and 3 nos 160/5 amps 15 VA, CL 1 CTs . | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | Phase indicating light protected by 2 amps SP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Bus Bars | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 160 amps TPN aluminium bus bars with heat shrinkable insulation sleeve. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Outgoing | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 32 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 25 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Spare MCCBs of the following: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 25 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | All MCCBs shall be of 25 KA(Ics) breaking capacity. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | SDB AHU & VENTILATION TRANSFER FLOOR-01described as above | [8 empty] | No. | 1 | 219891.54 | 0 | 219891.54 | 16498.4622 | 0 | 236390.0022 | 10128 | 1251.8208 | 0 | 11379.8208 | 236390.0022 | 11379.8208 | 247770 | 10 | 1 | 21989.154 | 0 | 21989.154 | 1649.8462 | 0 | 23639.0002 | 1012.8 | 125.1821 | 0 | 1137.9821 | 24776.9823
21 | 303000000 | SDB AHU & VENTILATION TRANSFER FLOOR-02. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Incoming | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 160 amps TPN MCCB (25KA) with following accessories: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | 0-500 volts digital volt meter with selector switch be protected by 2 amps TP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | 0- 160 Amps digital electronic ammeter with selector switch and 3 nos 160/5 amps 15 VA, CL 1 CTs . | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | Phase indicating light protected by 2 amps SP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Bus Bars | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 160 amps TPN aluminium bus bars with heat shrinkable insulation sleeve. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Outgoing | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 40 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 32 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 25 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Spare MCCBs of the following: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 25 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | All MCCBs shall be of 25 KA(Ics) breaking capacity. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | SDB AHU & VENTILATION TRANSFER FLOOR-02 described as above | [8 empty] | No. | 1 | 218934.655 | 0 | 218934.655 | 16426.6672 | 0 | 235361.3222 | 10128 | 1251.8208 | 0 | 11379.8208 | 235361.3222 | 11379.8208 | 246741 | 10 | 1 | 21893.4655 | 0 | 21893.4655 | 1642.6667 | 0 | 23536.1322 | 1012.8 | 125.1821 | 0 | 1137.9821 | 24674.1143
22 | 303000000 | SDB COMMISSIONARY KITCHEN-01 | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Incoming | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 200 amps TPN MCCB (25KA ) with following accessories: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | 0-500 volts digital volt meter with selector switch be protected by 2 amps TP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | 0- 200Amps digital electronic ammeter with selector switch and 200/5 amps 15 VA, CL 1 CTs . | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | Phase indicating light protected by 2 amps SP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Bus Bars | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 200 amps TPN Aluminium bus bars with heat shrinkable insulation sleeve. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Outgoing | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 25 Amps 4P RCBO of 30 mA | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 40 Amps 4P RCBO of 30 mA | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 Amps 4P RCBO of 30 mA ( BA-31) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 amps TPN MCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Spare MCCBs of the following: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 amps TPN MCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 25 Amps 4P RCBO of 30 mA | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | SDB COMMISSIONARY KITCHEN-01 described as above | [8 empty] | No. | 1 | 143644.58 | 0 | 143644.58 | 10777.6528 | 0 | 154422.2328 | 8862 | 1095.3432 | 0 | 9957.3432 | 154422.2328 | 9957.3432 | 164380 | 10 | 1 | 14364.458 | 0 | 14364.458 | 1077.7653 | 0 | 15442.2233 | 886.2 | 109.5343 | 0 | 995.7343 | 16437.9576
23 | 303000000 | SDB COMMISSIONARY KITCHEN-02 | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Incoming | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 200 amps TPN MCCB (25KA) with following accessories: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | 0-500 volts digital volt meter with selector switch be protected by 2 amps TP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | 0- 200Amps digital electronic ammeter with selector switch and 200/5 amps 5 VA, CL 1 CTs . | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | Phase indicating light protected by 2 amps SP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Bus Bars | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 200 amps TPN Aluminium bus bars with heat shrinkable insulation sleeve. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Outgoing | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 25 Amps 4P RCBO of 30 mA | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 40 Amps 4P RCBO of 30 mA | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 Amps 4P RCBO of 30 mA (BA-30) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 amps TPN MCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Spare MCCBs of the following: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 amps TPN MCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 25 Amps 4P RCBO of 30 mA | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | SDB COMMISSIONARY KITCHEN-02 described as above | [8 empty] | No. | 1 | 145440.19 | 0 | 145440.19 | 10912.3775 | 0 | 156352.5675 | 8862 | 1095.3432 | 0 | 9957.3432 | 156352.5675 | 9957.3432 | 166310 | 10 | 1 | 14544.019 | 0 | 14544.019 | 1091.2377 | 0 | 15635.2567 | 886.2 | 109.5343 | 0 | 995.7343 | 16630.9911
24 | 303000000 | SDB GROUND KITCHEN-03 | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Incoming | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 250 amps TPN MCCB (25KA) with following accessories (TMD): | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | 0-500 volts digital volt meter with selector switch be protected by 2 amps TP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | 0- 250Amps digital electronic ammeter with selector switch and 250/5 amps 15 VA, CL 1 CTs . | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | Phase indicating light protected by 2 amps SP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Bus Bars | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 250 amps TPN Aluminium bus bars with heat shrinkable insulation sleeve. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Outgoing | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 amps TPN MCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 40 Amps 4P RCBO of 30 mA | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 Amps 4P RCBO of 30 mA | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Spare MCCBs of the following: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 amps TPN MCCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | SDB GROUND KITCHEN-03 described as above | [8 empty] | No. | 1 | 131200.855 | 0 | 131200.855 | 9844.0002 | 0 | 141044.8552 | 8862 | 1095.3432 | 0 | 9957.3432 | 141044.8552 | 9957.3432 | 151002 | 10 | 1 | 13120.0855 | 0 | 13120.0855 | 984.4 | 0 | 14104.4855 | 886.2 | 109.5343 | 0 | 995.7343 | 15100.2198
25 | 303000000 | SDB FIRST FLOOR KITCHEN-04 | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Incoming | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 315 amps TPN MCCB (25KA) with following accessories: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | 0-500 volts digital volt meter with selector switch be protected by 2 amps TP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | 0- 315 Amps digital electronic ammeter with selector switch and 315/5 amps 15 VA, CL 1 CTs . | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | Phase indicating light protected by 2 amps SP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Bus Bars | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 315 amps TPN Aluminium bus bars with heat shrinkable insulation sleeve. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Outgoing | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 amps TPN MCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 100 Amps 4P RCBO of 30 mA | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 40 Amps 4P RCBO of 30 mA | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Spare MCCBs of the following: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 amps TPN MCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | SDB FIRST FLOOR KITCHEN-04 described as above | [8 empty] | No. | 1 | 105593.895 | 0 | 105593.895 | 7922.7099 | 0 | 113516.6049 | 8862 | 1095.3432 | 0 | 9957.3432 | 113516.6049 | 9957.3432 | 123474 | 10 | 1 | 10559.3895 | 0 | 10559.3895 | 792.271 | 0 | 11351.6605 | 886.2 | 109.5343 | 0 | 995.7343 | 12347.3948
26 | 303000000 | SDB GUEST ROOM 3RD TO 12TH FLOOR | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Incoming | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 100 amps TPN MCCB (25KA) with following accessories: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | 0-500 volts digital volt meter with selector switch be protected by 2 amps TP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | 0- 100 Amps digital electronic ammeter with selector switch and 3 nos 100/5 amps 15 VA, CL 1 CTs . | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | Phase indicating light protected by 2 amps SP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iv | 303000000 | Class – C surge arrestor (Lines to Neutral) & (Neutral to Earth) suitable for 3 phases with backup MCB protection of suitable rating. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Bus Bars | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 100 amps TPN aluminium bus bars with heat shrinkable insulation sleeve. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Outgoing | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 32 Amps DP RCBO of 30 mA | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 25 Amps DP RCBO of 30 mA | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 40 amps TPN MCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Spare MCCBs of the following: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 25 Amps DP RCBO of 30 mA | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | SDB GUEST ROOM 3RD TO 12TH FLOOR guest floor described as above | [8 empty] | No. | 10 | 122106.755 | 0 | 122106.755 | 9161.6698 | 0 | 131268.4248 | 8862 | 1095.3432 | 0 | 9957.3432 | 1312684.2483 | 99573.432 | 1412258 | 10 | 10 | 122106.755 | 0 | 122106.755 | 9161.6698 | 0 | 131268.4248 | 8862 | 1095.3432 | 0 | 9957.3432 | 141225.768
27 | 303000000 | SDB GUEST ROOM 2ND FLOOR | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Incoming | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 amps TPN MCCB (25KA) with following accessories: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | 0-500 volts digital volt meter with selector switch be protected by 2 amps TP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | 0- 63 Amps digital electronic ammeter with selector switch and 3 nos 63/5 amps 15 VA, CL 1 CTs . | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | Phase indicating light protected by 2 amps SP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iv | 303000000 | Class – C surge arrestor (Lines to Neutral) & (Neutral to Earth) suitable for 3 phases with backup MCB protection of suitable rating. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Bus Bars | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 amps TPN aluminium bus bars with heat shrinkable insulation sleeve. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Outgoing | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 25 Amps DP RCBO of 30 mA | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 40 amps TPN MCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Spare MCCBs of the following: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 25 Amps DP RCBO of 30 mA | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 40 amps TPN MCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | SDB GUEST ROOM 2ND FLOOR described as above | [8 empty] | No. | 1 | 78647.085 | 0 | 78647.085 | 5900.8908 | 0 | 84547.9758 | 7596 | 938.8656 | 0 | 8534.8656 | 84547.9758 | 8534.8656 | 93083 | 10 | 1 | 7864.7085 | 0 | 7864.7085 | 590.0891 | 0 | 8454.7976 | 759.6 | 93.8866 | 0 | 853.4866 | 9308.2841
28 | 303000000 | SDB GUEST ROOM DB PENTH HOUSE FLOOR | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Incoming | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 100 amps TPN MCCB (25KA) with following accessories: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | 0-500 volts digital volt meter with selector switch be protected by 2 amps TP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | 0- 100 Amps digital electronic ammeter with selector switch and 3 nos 100/5 amps 15 VA, CL 1 CTs . | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | Phase indicating light protected by 2 amps SP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iv | 303000000 | Class – C surge arrestor (Lines to Neutral) & (Neutral to Earth) suitable for 3 phases with backup MCB protection of suitable rating. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Bus Bars | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 100 amps TPN aluminium bus bars with heat shrinkable insulation sleeve. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Outgoing | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 40 Amps DP RCBO of 100 mA | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 25 Amps DP RCBO of 30 mA | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 40 amps TPN MCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Spare MCCBs of the following: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 40 Amps DP RCBO of 100 mA | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 25 Amps DP RCBO of 30 mA | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 40 amps TPN MCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | SDB GUEST ROOM DB PENTH HOUSE FLOOR described as above | [8 empty] | No. | 1 | 76732.26 | 0 | 76732.26 | 5757.2215 | 0 | 82489.4815 | 7596 | 938.8656 | 0 | 8534.8656 | 82489.4815 | 8534.8656 | 91024 | 10 | 1 | 7673.226 | 0 | 7673.226 | 575.7221 | 0 | 8248.9481 | 759.6 | 93.8866 | 0 | 853.4866 | 9102.4347
29 | 303000000 | SDB POWER FOR BOH AREA | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Incoming | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 160 amps TPN MCCB (25KA) with following accessories: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
i. | 303000000 | 0-500 volts digital volt meter with selector switch be protected by 2 amps TP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | 0- 100 Amps digital electronic ammeter with selector switch and 3 nos 100/5 amps 15 VA, CL 1 CTs . | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
iii. | 303000000 | Phase indicating light protected by 2 amps SP MCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Bus Bars | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 160 amps TPN aluminium bus bars with heat shrinkable insulation sleeve. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Outgoing | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 amps TPN MCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Spare MCCBs of the following: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 63 amps TPN MCB | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | All MCCBs shall be of 25 KA(Ics) breaking capacity. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | SDB AHU & VENTILATION BASEMENT-1 described as above | [8 empty] | No. | 1 | 62134.225 | 0 | 62134.225 | 4661.9309 | 0 | 66796.1559 | 7596 | 938.8656 | 0 | 8534.8656 | 66796.1559 | 8534.8656 | 75331 | 10 | 1 | 6213.4225 | 0 | 6213.4225 | 466.1931 | 0 | 6679.6156 | 759.6 | 93.8866 | 0 | 853.4866 | 7533.1022
30 | 303000000 | supply, installation, testing and commissioning of following rating ACB panel fabricated out of 2 mm thick CRCA sheet steel in cubical formation, compartmentalized in Form 3b Construction, floor mounted, free standing and shall be dust and vermin proof. 3 mm thick cable gland plate, shall be provided at the bottom of the panel suitable for 415 V, 3 phase, 50 Hz, 4 wire power supply system. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30.1 | 303000000 | 1600 amps 4 pole Manually operated fully drawout type air circuit breaker with built in microprocessor based release unit for protection (LSIG only) and indication as per specification and with following accessories : | [8 empty] | Nos. | 2 | 339624.545 | 0 | 339624.545 | 25482.0296 | 0 | 365106.5746 | 13926 | 1721.2536 | 0 | 15647.2536 | 730213.1492 | 31294.5072 | 761508 | 10 | 2 | 67924.909 | 0 | 67924.909 | 5096.4059 | 0 | 73021.3149 | 2785.2 | 344.2507 | 0 | 3129.4507 | 76150.7656
i. | 303000000 | Phase indicating light protected by 2 amps MCBs. 3 Sets | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ii. | 303000000 | Breaker ON / OFF / TRIP indicating lights with control MCBs. 1 Set | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | 303000000 | Rising Mains (In sandwich Construction) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Design, manufacture, supply, installation, testing and commissioning of 630 amps rating ( 25 KA for 1 Sec) 4 pole rising mains in sandwich construction of aluminium bus bar with tap-off connection points at every 1000 mm intervals, expansion joints, fire barriers including necessary support and louvers for ventilation, fabricated out of GI sheet painted with approved paint shade including 2 Nos. of 50 x 6 mm mm external GI earthing conductor through out the length of the rising mains (Phase sequence shall match the sequence of the incoming breaker provided at the LT Panel). Thrust pad shall be provided for each rising main for necessary support to rising main and to prevent the bus bar expansion in downward direction. Also provide end cover to close the end of rising main and to provide extra end supports to the bus bars. (IP 55 required). | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Rising Mains in sandwich construction described as above | [8 empty] | RM | 40 | 10478.26 | 0 | 10478.26 | 786.1838 | 0 | 11264.4438 | 1012.8 | 125.1821 | 0 | 1137.9821 | 450577.7539 | 45519.2832 | 496097 | 10 | 40 | 41913.04 | 0 | 41913.04 | 3144.7354 | 0 | 45057.7754 | 4051.2 | 500.7283 | 0 | 4551.9283 | 49609.7037
32 | 303000000 | Supply, installation, testing and commissioning of tap off of following rating with boxes made out of 14 gauge GI sheet duly painted and mounted on the rising mains including providing of following MCCBs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32.1 | 303000000 | 100 amps TPN MCCB of 25 KA (Ics). | [8 empty] | No. | 11 | 10447.665 | 0 | 10447.665 | 783.8883 | 0 | 11231.5533 | 1899 | 234.7164 | 0 | 2133.7164 | 123547.0864 | 23470.8804 | 147018 | 10 | 11 | 11492.4315 | 0 | 11492.4315 | 862.2771 | 0 | 12354.7086 | 2088.9 | 258.188 | 0 | 2347.088 | 14701.7967
32.2 | 303000000 | 63 amps TPN MCCB of 25 KA (Ics). | [8 empty] | No. | 1 | 10435.005 | 0 | 10435.005 | 782.9384 | 0 | 11217.9434 | 1266 | 156.4776 | 0 | 1422.4776 | 11217.9434 | 1422.4776 | 12640 | 10 | 1 | 1043.5005 | 0 | 1043.5005 | 78.2938 | 0 | 1121.7943 | 126.6 | 15.6478 | 0 | 142.2478 | 1264.0421
33 | 303000000 | Supply, installation, testing and commissioning of 630 Amps 4 pole Isolator MCCB with castle key , operating handle and with Aluminium busbar arragement suitable for termination of 3 nos 240 sqmm Al. Armoured cable on the incoming side and suitable for busduct termination on the outgoing in enclosure fabricated out of 14 gauge GI sheet duly painted with approved paint shade and with 2 nos of earth terminal suitable for 32 x 6mm GI earth strip. | [8 empty] | Nos. | 2 | 57203.155 | 0 | 57203.155 | 4291.9527 | 0 | 61495.1077 | 6330 | 782.388 | 0 | 7112.388 | 122990.2154 | 14224.776 | 137215 | 10 | 2 | 11440.631 | 0 | 11440.631 | 858.3905 | 0 | 12299.0215 | 1266 | 156.4776 | 0 | 1422.4776 | 13721.4991
34 | 303000000 | Supply, installation, testing and commissioning of 630 Amps 4 pole MCCB (25 KA Ics) with castle key , operating handle and suitable for busduct termination on the Incoming/outgoing in enclosure fabricated out of 14 gauge GI sheet duly painted with approved paint shade and with 2 nos of earth terminal suitable for 32 x 6mm GI earth strip. | [8 empty] | Nos. | 1 | 57203.155 | 0 | 57203.155 | 4291.9527 | 0 | 61495.1077 | 6330 | 782.388 | 0 | 7112.388 | 61495.1077 | 7112.388 | 68607 | 10 | 1 | 5720.3155 | 0 | 5720.3155 | 429.1953 | 0 | 6149.5108 | 633 | 78.2388 | 0 | 711.2388 | 6860.7496
35 | 303000000 | FINAL DISTRIBUTION BOARDS | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Supply, installation, testing and commissioning of the following FDBs fabricated out of 1.2 mm & 1.6 mm thick CRCA sheet steel for SPN & TPN db respectively , double door construction, powder coated with approved shade and partitions to segregate phases. Approved lockable covers with padlocking arrangement for each phase, recessed in wall or surface mounted final distribution boards of the following description: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35.1 | 303000000 | Type A (LDB) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 12 way TPN DB, 12 Nos. 10 amps SP MCBs per phase with 3 Nos. 63 amps DP RCCBs of 30 mA leakage current and 1 no. 63 amps 4 pole MCB isolator as incomer with separate neutral link for each phase. | [8 empty] | Nos. | 1 | 14541.065 | 0 | 14541.065 | 1091.0161 | 0 | 15632.0811 | 2532 | 312.9552 | 0 | 2844.9552 | 15632.0811 | 2844.9552 | 18477 | 10 | 1 | 1454.1065 | 0 | 1454.1065 | 109.1016 | 0 | 1563.2081 | 253.2 | 31.2955 | 0 | 284.4955 | 1847.7036
35.2 | 303000000 | Type B (LDB) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 10 way TPN DB, 10 Nos. 10 amps SP MCBs per phase with 3 Nos. 40 amps DP RCCBs of 30 mA leakage current and 1 no. 40 amps 4 pole MCB isolator as incomer with separate neutral link for each phase. | [8 empty] | Nos. | 2 | 12896.32 | 0 | 12896.32 | 967.6109 | 0 | 13863.9309 | 2532 | 312.9552 | 0 | 2844.9552 | 27727.8618 | 5689.9104 | 33418 | 10 | 2 | 2579.264 | 0 | 2579.264 | 193.5222 | 0 | 2772.7862 | 506.4 | 62.591 | 0 | 568.991 | 3341.7772
35.3 | 303000000 | Type C (LDB) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 8 way TPN DB, 8 Nos. 10 amps SP MCBs per phase with 3 Nos. 40 amps DP RCCBs of 30 mA leakage current and 1 No. 40 amps 4 pole MCB isolator as incomer with separate neutral link for each phase. | [8 empty] | Nos. | 1 | 11841.32 | 0 | 11841.32 | 888.4542 | 0 | 12729.7742 | 2532 | 312.9552 | 0 | 2844.9552 | 12729.7742 | 2844.9552 | 15575 | 10 | 1 | 1184.132 | 0 | 1184.132 | 88.8454 | 0 | 1272.9774 | 253.2 | 31.2955 | 0 | 284.4955 | 1557.4729
35.4 | 303000000 | Type D (LDB) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 6 way TPN DB, 6 Nos. 10 amps SP MCBs per phase with 3 Nos. 40 amps DP RCCBs of 30 mA leakage current and 1 No. 40 amps 4 pole MCB isolator as incomer with separate neutral link for each phase. | [8 empty] | Nos. | 8 | 10605.915 | 0 | 10605.915 | 795.7618 | 0 | 11401.6768 | 2532 | 312.9552 | 0 | 2844.9552 | 91213.4144 | 22759.6416 | 113973 | 10 | 8 | 8484.732 | 0 | 8484.732 | 636.6094 | 0 | 9121.3414 | 2025.6 | 250.3642 | 0 | 2275.9642 | 11397.3056
35.5 | 303000000 | Type E (LDB) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 4 way TPN DB, 4 Nos. 10 amps SP MCBs per phase with 3 Nos. 40 amps DP RCCBs of 30 mA leakage current and 1 No. 40 amps 4 pole MCB isolator as incomer separate neutral link for each phase. | [8 empty] | Nos. | 1 | 10033.05 | 0 | 10033.05 | 752.7797 | 0 | 10785.8297 | 2532 | 312.9552 | 0 | 2844.9552 | 10785.8297 | 2844.9552 | 13631 | 10 | 1 | 1003.305 | 0 | 1003.305 | 75.278 | 0 | 1078.583 | 253.2 | 31.2955 | 0 | 284.4955 | 1363.0785
35.6 | 303000000 | Type F (PDB) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 12 way TPN DB, 12 Nos. 16/20 amps SP MCB per phase with 3 Nos. 63 amps DP RCCBs of 30 mA leakage current and 1 No. 63 amps 4 pole MCB isolator as incomer with separate neutral link for each phase. | [8 empty] | Nos. | 1 | 14690.875 | 0 | 14690.875 | 1102.2564 | 0 | 15793.1314 | 2532 | 312.9552 | 0 | 2844.9552 | 15793.1314 | 2844.9552 | 18638 | 10 | 1 | 1469.0875 | 0 | 1469.0875 | 110.2256 | 0 | 1579.3131 | 253.2 | 31.2955 | 0 | 284.4955 | 1863.8087
35.7 | 303000000 | Type F (PDB, L+PDB) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 10 way TPN DB, 10 Nos. 16/20 amps SP MCB per phase with 3 Nos. 63 amps DP RCCBs of 30 mA leakage current and 1 No. 63 amps 4 pole MCB isolator as incomer with separate neutral link for each phase. | [8 empty] | Nos. | 0 | 13901.735 | 0 | 13901.735 | 1043.0472 | 0 | 14944.7822 | 2532 | 312.9552 | 0 | 2844.9552 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35.8 | 303000000 | Type (L+PDB for Penth house floor) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 10 way TPN DB, 10 Nos. 16/20 amps SP MCB per phase with 3 Nos. 63 amps DP RCCBs of 30 mA leakage current with 1 nos 63 amp DP contactor controlled through 0-24 hr timer in R phase and 1 No. 63 amps 4 pole MCB isolator as incomer with separate neutral link for each phase. | [8 empty] | Nos. | 1 | 19135.59 | 0 | 19135.59 | 1435.7433 | 0 | 20571.3333 | 2532 | 312.9552 | 0 | 2844.9552 | 20571.3333 | 2844.9552 | 23416 | 10 | 1 | 1913.559 | 0 | 1913.559 | 143.5743 | 0 | 2057.1333 | 253.2 | 31.2955 | 0 | 284.4955 | 2341.6289
35.9 | 303000000 | Type F ( L+PDB for 3rd to 12th Guest floor) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 8 way TPN DB, 8 Nos. 16/20 amps SP MCBs per phase with 3 Nos. 63 amps DP RCCBs of 30 mA leakage current with 1 nos 63 amp DP contactor controlled through 0-24 hr timer in R phase and 1 No.63 amps 4 pole MCB isolator as incomer with separate neutral link for each phase. | [8 empty] | Nos. | 11 | 17691.295 | 0 | 17691.295 | 1327.3779 | 0 | 19018.6729 | 2532 | 312.9552 | 0 | 2844.9552 | 209205.4015 | 31294.5072 | 240500 | 10 | 11 | 19460.4245 | 0 | 19460.4245 | 1460.1157 | 0 | 20920.5402 | 2785.2 | 344.2507 | 0 | 3129.4507 | 24049.9909
35.1 | 303000000 | Type F (PDB) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 8 way TPN DB, 8 Nos. 16/20 amps SP MCBs per phase with 3 Nos. 63 amps DP RCCBs of 30 mA leakage current and 1 No.63 amps 4 pole MCB isolator as incomer with separate neutral link for each phase. | [8 empty] | Nos. | 6 | 12191.58 | 0 | 12191.58 | 914.7342 | 0 | 13106.3142 | 2532 | 312.9552 | 0 | 2844.9552 | 78637.8855 | 17069.7312 | 95708 | 10 | 6 | 7314.948 | 0 | 7314.948 | 548.8405 | 0 | 7863.7885 | 1519.2 | 187.7731 | 0 | 1706.9731 | 9570.7617
35.11 | 303000000 | Type G (PDB) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 6 way TPN DB, 6 Nos. 16/20 amps SP MCBs per phase with 3 Nos. 63 amps DP RCCBs of 30 mA leakage current and 1 No. 63 amps 4 Pole MCB isolator as incomer with separate neutral link for each phase. | [8 empty] | Nos. | 3 | 11402.44 | 0 | 11402.44 | 855.5251 | 0 | 12257.9651 | 2532 | 312.9552 | 0 | 2844.9552 | 36773.8952 | 8534.8656 | 45309 | 10 | 3 | 3420.732 | 0 | 3420.732 | 256.6575 | 0 | 3677.3895 | 759.6 | 93.8866 | 0 | 853.4866 | 4530.8761
35.12 | 303000000 | Type H (L+PDB for Transfer Floor & Substation) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 4 way TPN DB, 4 Nos. 16/20 amps SP MCBs per phase with 3 Nos. 40 amps DP RCCBs of 30 mA leakage current and 1 No. 40 amps 4 Pole MCB isolator as incomer with separate neutral link for each phase. | [8 empty] | Nos. | 2 | 11552.25 | 0 | 11552.25 | 866.7653 | 0 | 12419.0153 | 2532 | 312.9552 | 0 | 2844.9552 | 24838.0306 | 5689.9104 | 30528 | 10 | 2 | 2310.45 | 0 | 2310.45 | 173.3531 | 0 | 2483.8031 | 506.4 | 62.591 | 0 | 568.991 | 3052.7941
35.13 | 303000000 | Type J ( ELDB ) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Incomer : 1no. 25A DP RCBO | [8 empty] | Nos. | 0 | 7323.81 | 0 | 7323.81 | 549.5055 | 0 | 7873.3155 | 1519.2 | 187.7731 | 0 | 1706.9731 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Out Going: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Set 1 having 6 nos 6 amps SP MCB with 25 amps DP insulated copper busbars. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Set 2 having 6 nos 6 amps SP MCB with 240 Volts, 50 Hz voltage sensing relay & 230Volts, 10 Amps DP contactor, 230 Volts No volt coil and with 25 amps DP insulated copper busbars. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35.14 | 303000000 | Type J ( ELDB + elevator lift shaft ltg DB ) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 6 way SPN DB, 6 Nos. 6 amps SP MCBs with 1 No. 25 amps DP RCBO of 30 mA leakage current as incomer including cu. Busbars | [8 empty] | Nos. | 10 | 3254.675 | 0 | 3254.675 | 244.1983 | 0 | 3498.8733 | 1519.2 | 187.7731 | 0 | 1706.9731 | 34988.7327 | 17069.7312 | 52058 | 10 | 10 | 3254.675 | 0 | 3254.675 | 244.1983 | 0 | 3498.8733 | 1519.2 | 187.7731 | 0 | 1706.9731 | 5205.8464
35.15 | 303000000 | Type K ( STAIRCASE DB WITH TIMER ) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 6 way SPN DB, 4 Nos. 6 amps SP MCBs with 1 No. 25 amps DP RCBO of 30 mA leakage current as incomer including cu. Busbars and with 25 amps DP contactor controlled through 0-24 hr timer | [8 empty] | Nos. | 4 | 7680.4 | 0 | 7680.4 | 576.2604 | 0 | 8256.6604 | 1519.2 | 187.7731 | 0 | 1706.9731 | 33026.6416 | 6827.8925 | 39855 | 10 | 4 | 3072.16 | 0 | 3072.16 | 230.5042 | 0 | 3302.6642 | 607.68 | 75.1092 | 0 | 682.7892 | 3985.4534
35.16 | 303000000 | Type L ( ELDB for Guest floor) ) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 4 way SPN DB, 4 Nos. 6 amps SP MCBs with 1 No. 25 amps DP RCBO of 30 mA leakage current as incomer including cu. Busbars | [8 empty] | Nos. | 10 | 2990.925 | 0 | 2990.925 | 224.4091 | 0 | 3215.3341 | 1519.2 | 187.7731 | 0 | 1706.9731 | 32153.341 | 17069.7312 | 49223 | 10 | 10 | 2990.925 | 0 | 2990.925 | 224.4091 | 0 | 3215.3341 | 1519.2 | 187.7731 | 0 | 1706.9731 | 4922.3072
35.17 | 303000000 | Type M (For Kitchen/Laundry/Gym) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 6 way TPN DB, 6 Nos. 20 amps DP MCB and 25 amps RCCBs of 30 mA leakage current per phase as outgoing with 3 Nos. 63 amps DP MCBs and 1 No. 63 amps 4 pole MCB isolator as incomer including cu bus bars | [8 empty] | Nos. | 15 | 20420.58 | 0 | 20420.58 | 1532.1561 | 0 | 21952.7361 | 2532 | 312.9552 | 0 | 2844.9552 | 329291.0418 | 42674.328 | 371965 | 10 | 15 | 30630.87 | 0 | 30630.87 | 2298.2342 | 0 | 32929.1042 | 3798 | 469.4328 | 0 | 4267.4328 | 37196.537
35.18 | 303000000 | Type R (For Kitchen/Laundry/spa/sump pump DB/stack park DB) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | TPN DB, 6 Nos. 20 / 32 amps 4 Pole MCB and 40 amps 4 pole RCCBs of 30 mA leakage current as outgoing and 1 No. 63 amps 4 pole MCB isolator as incomer including cu.bus bars. | [8 empty] | Nos. | 17 | 19762.26 | 0 | 19762.26 | 1482.7624 | 0 | 21245.0224 | 2532 | 312.9552 | 0 | 2844.9552 | 361165.3803 | 48364.2384 | 409530 | 10 | 17 | 33595.842 | 0 | 33595.842 | 2520.696 | 0 | 36116.538 | 4304.4 | 532.0238 | 0 | 4836.4238 | 40952.9619
35.19 | 303000000 | Type R (For Elevator ltg db) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | TPN DB, 6 Nos. 20 / 32 amps 4 Pole MCB as outgoing and 1 No. 63 amps 4 pole MCB isolator as incomer including cu.bus bars. | [8 empty] | Nos. | 2 | 8918.97 | 0 | 8918.97 | 669.1903 | 0 | 9588.1603 | 2532 | 312.9552 | 0 | 2844.9552 | 19176.3206 | 5689.9104 | 24866 | 10 | 2 | 1783.794 | 0 | 1783.794 | 133.8381 | 0 | 1917.6321 | 506.4 | 62.591 | 0 | 568.991 | 2486.6231
35.2 | 303000000 | Type-S (for external lighting with IP-55) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 6 way TPN DB, 6 Nos. 10 amps SP MCBs per phase as outgoing with 3 Nos. 40 amps DP RCCBs of 30 mA leakage current with 3 nos 40 amp DP contactor controlled through 0-24 hr timer and 1 no. 40 amps 4 pole MCB isolator as incomer with separate neutral link for each phase. | [8 empty] | Nos. | 2 | 23924.235 | 0 | 23924.235 | 1795.0354 | 0 | 25719.2704 | 2785.2 | 344.2507 | 0 | 3129.4507 | 51438.5407 | 6258.9014 | 57697 | 10 | 2 | 4784.847 | 0 | 4784.847 | 359.0071 | 0 | 5143.8541 | 557.04 | 68.8501 | 0 | 625.8901 | 5769.7442
35.21 | 303000000 | Type-S (for Façade lighting with IP-55) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 6 way TPN DB 6 Nos. 10 amps SP MCB per phase as outgoing with 3 nos. 40 amps DP RCCB of 30 mA leakage current plus 1 No. 40 amps TP Contactor controlled through 0-24 hour timer and 1 No. 40 amps 4 pole isolator as incomer. | [8 empty] | Nos. | 1 | 15082.28 | 0 | 15082.28 | 1131.6235 | 0 | 16213.9035 | 2785.2 | 344.2507 | 0 | 3129.4507 | 16213.9035 | 3129.4507 | 19343 | 10 | 1 | 1508.228 | 0 | 1508.228 | 113.1623 | 0 | 1621.3903 | 278.52 | 34.4251 | 0 | 312.9451 | 1934.3354
35.22 | 303000000 | Type T (DB for work station fed by UPS) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | 6 way TPN DB, 6 Nos. 16/20 amps SP MCBs per phase with 3 Nos. SI TYPE 63 amps DP RCCBs of 30 mA leakage current and 1 No. 63 amps 4 Pole MCB isolator as incomer with separate neutral link for each phase. | [8 empty] | Nos. | 8 | 14401.805 | 0 | 14401.805 | 1080.5674 | 0 | 15482.3724 | 2785.2 | 344.2507 | 0 | 3129.4507 | 123858.9794 | 25035.6058 | 148895 | 10 | 8 | 11521.444 | 0 | 11521.444 | 864.4539 | 0 | 12385.8979 | 2228.16 | 275.4006 | 0 | 2503.5606 | 14889.4585
36 | 303000000 | Distribution Board for Hotel Guest Room | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36.1 | 303000000 | Supply, installation, testing and commissioning of 4 way SPN, MCB, DB with 4 Nos. 20 amps SPMCB through energy saving unit and 1 No. 25 DP MCB as incomer. | [8 empty] | Nos. | 200 | 1809.325 | 0 | 1809.325 | 135.7537 | 0 | 1945.0787 | 1519.2 | 187.7731 | 0 | 1706.9731 | 389015.731 | 341394.624 | 730410 | 10 | 200 | 36186.5 | 0 | 36186.5 | 2715.0731 | 0 | 38901.5731 | 30384 | 3755.4624 | 0 | 34139.4624 | 73041.0355
36.2 | 303000000 | Supply, installation, testing and commissioning of 4 way SPN, MCB, DB with 6 Nos. 20 amps SPMCB through energy saving unit and 1 No. 32 DP MCB as incomer. | [8 empty] | Nos. | 22 | 2073.075 | 0 | 2073.075 | 155.5428 | 0 | 2228.6178 | 1519.2 | 187.7731 | 0 | 1706.9731 | 49029.592 | 37553.4086 | 86583 | 10 | 22 | 4560.765 | 0 | 4560.765 | 342.1942 | 0 | 4902.9592 | 3342.24 | 413.1009 | 0 | 3755.3409 | 8658.3001
37 | 303000000 | Supply, installation, testing and commissioning of 3 nos. 100 amps 4 pole MCCB with operating handle (25 KA Ics) breaking capacity in 1.6 mm thick CRCA sheet steel enclosure of approved make design and painted with approved paint shade (for UPS & bypass system.) | [8 empty] | Nos. | 3 | 8392.525 | 0 | 8392.525 | 629.6912 | 0 | 9022.2162 | 633 | 78.2388 | 0 | 711.2388 | 27066.6485 | 2133.7164 | 29200 | 10 | 3 | 2517.7575 | 0 | 2517.7575 | 188.9073 | 0 | 2706.6648 | 189.9 | 23.4716 | 0 | 213.3716 | 2920.0365
38 | 303000000 | Supply, installation, testing and commissioning of 63 amps 4 pole MCB in 1..6 mm thick MS enclosure of approved make design and painted with approved paint shade. (for gym ups) | [8 empty] | Nos. | 2 | 1497.045 | 0 | 1497.045 | 112.3233 | 0 | 1609.3683 | 189.9 | 23.4716 | 0 | 213.3716 | 3218.7366 | 426.7433 | 3645 | 10 | 2 | 299.409 | 0 | 299.409 | 22.4647 | 0 | 321.8737 | 37.98 | 4.6943 | 0 | 42.6743 | 364.548
39 | 303000000 | Supply, installation, testing and commissioning of 63 amps 4 pole MCB in 1..6 mm thick MS enclosure of approved make design and painted with approved paint shade. (for Inverter) | [8 empty] | Nos. | 2 | 1497.045 | 0 | 1497.045 | 112.3233 | 0 | 1609.3683 | 189.9 | 23.4716 | 0 | 213.3716 | 3218.7366 | 426.7433 | 3645 | 10 | 2 | 299.409 | 0 | 299.409 | 22.4647 | 0 | 321.8737 | 37.98 | 4.6943 | 0 | 42.6743 | 364.548
40 | 303000000 | Supply, installation, testing and commissioning of 63 amps 4P ELMCB of 300 mA leakage current suitable for AC3VF elevator drive in 1.6 mm thick CRCA sheet steel enclosure of approved make design and painted with approved paint shade. ( FOR SERVICE & GUEST ELEVATOR) | [8 empty] | Nos. | 6 | 2545.715 | 0 | 2545.715 | 191.005 | 0 | 2736.72 | 189.9 | 23.4716 | 0 | 213.3716 | 16420.32 | 1280.2298 | 17701 | 10 | 6 | 1527.429 | 0 | 1527.429 | 114.603 | 0 | 1642.032 | 113.94 | 14.083 | 0 | 128.023 | 1770.055
41 | 303000000 | Supply, installation, testing and commissioning of 63 amps 4 pole MCB in 1.6 mm thick CRCA sheet steel enclosure of approved make design and painted with approved paint shade. ( FOR DIMMER DB) | [8 empty] | Nos. | 10 | 1497.045 | 0 | 1497.045 | 112.3233 | 0 | 1609.3683 | 189.9 | 23.4716 | 0 | 213.3716 | 16093.6829 | 2133.7164 | 18227 | 10 | 10 | 1497.045 | 0 | 1497.045 | 112.3233 | 0 | 1609.3683 | 189.9 | 23.4716 | 0 | 213.3716 | 1822.7399
42 | 303000000 | Supply, installation, testing and commissioning of 40 amps DP MCB in 1.6 mm thick CRCA sheet steel enclosure of approved make design and painted with approved paint shade. ( FOR DIMMER DB) | [8 empty] | Nos. | 2 | 891.475 | 0 | 891.475 | 66.8874 | 0 | 958.3624 | 189.9 | 23.4716 | 0 | 213.3716 | 1916.7247 | 426.7433 | 2343 | 10 | 2 | 178.295 | 0 | 178.295 | 13.3775 | 0 | 191.6725 | 37.98 | 4.6943 | 0 | 42.6743 | 234.3468
42 | 303000000 | Supply, installation, testing and commissioning of 63 amps 4 pole Isolator MCB in IP 65 polycarbonate enclosure of approved make design. ( FOR Kitchen power equipment) | [8 empty] | Nos. | 6 | 1824.095 | 0 | 1824.095 | 136.8618 | 0 | 1960.9568 | 189.9 | 23.4716 | 0 | 213.3716 | 11765.7411 | 1280.2298 | 13046 | 10 | 6 | 1094.457 | 0 | 1094.457 | 82.1171 | 0 | 1176.5741 | 113.94 | 14.083 | 0 | 128.023 | 1304.5971
43 | 303000000 | Supply, installation, testing and commissioning of following dry type step down transformer having safety isolating transformer confirming to BS 3535 in 1.6 mm thick MS enclosure of approved make and design. Input voltage 240 volts + 10% and multiple output voltage of 12/14/16 volts (for external & swimming pool lighting) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
43.1 | 303000000 | 250 VA | [8 empty] | Nos. | 5 | 1953.86 | 0 | 1953.86 | 146.5981 | 0 | 2100.4581 | 316.5 | 39.1194 | 0 | 355.6194 | 10502.2906 | 1778.097 | 12280 | 10 | 5 | 976.93 | 0 | 976.93 | 73.2991 | 0 | 1050.2291 | 158.25 | 19.5597 | 0 | 177.8097 | 1228.0388
43.2 | 303000000 | 500 VA | [8 empty] | Nos. | 4 | 3252.565 | 0 | 3252.565 | 244.04 | 0 | 3496.605 | 316.5 | 39.1194 | 0 | 355.6194 | 13986.4198 | 1422.4776 | 15409 | 10 | 4 | 1301.026 | 0 | 1301.026 | 97.616 | 0 | 1398.642 | 126.6 | 15.6478 | 0 | 142.2478 | 1540.8897
43.3 | 303000000 | 750 VA | [8 empty] | Nos. | 3 | 5201.15 | 0 | 5201.15 | 390.2423 | 0 | 5591.3923 | 316.5 | 39.1194 | 0 | 355.6194 | 16774.1769 | 1066.8582 | 17841 | 10 | 3 | 1560.345 | 0 | 1560.345 | 117.0727 | 0 | 1677.4177 | 94.95 | 11.7358 | 0 | 106.6858 | 1784.1035
43.4 | 303000000 | 1000 VA | [8 empty] | Nos. | 2 | 6499.855 | 0 | 6499.855 | 487.6841 | 0 | 6987.5391 | 316.5 | 39.1194 | 0 | 355.6194 | 13975.0782 | 711.2388 | 14686 | 10 | 2 | 1299.971 | 0 | 1299.971 | 97.5368 | 0 | 1397.5078 | 63.3 | 7.8239 | 0 | 71.1239 | 1468.6317
44 | 303000000 | Supply and fixing in position 1000 mm wide rubber matting of 1100 volts grade as per IS-15652:2006 (exact length of rubber mat to be worked out as per site requirement). | [8 empty] | RM | 110 | 1820 | 0 | 1820 | 136.5546 | 0 | 1956.5546 | 76 | 9.3936 | 0 | 85.3936 | 215221.006 | 9393.296 | 224614 | 10 | 110 | 20020 | 0 | 20020 | 1502.1006 | 0 | 21522.1006 | 836 | 103.3296 | 0 | 939.3296 | 22461.4302
E. | 303000000 | CAPACITOR BANKS WITH DETUNED FILTER IN AUTOMATIC CONTROL UNITS | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Design, fabrication, assembling, wiring, supply, installation, testing and commissioning of Automatic control panels with MPP type capacitors, fabricated out of 14 gauge CRCA sheet steel in cubicle compartmentised, free standing, floor mounted, dust and vermin proof with reinforcement of suitable size, angle iron, channel, T sections and / or flats wherever necessary. Cable gland plates shall be provided on top as well as at the bottom of the panels. Panels shall be treated with all anticorrosive process before powder coating as per specifications and final approved shade. 2 Nos. earthing terminals shall be provided for all distrtibution panels. Panels shall be suitable for 415V, 3 phase, 4 wire, 50 HZ supply system. Lifting hooks shall also be provided in case of large panels. Approval shall be taken for each panel in the form of shop drawings before fabrication. Galvanised hardwares with zinc passivation shall be used in fabrication of panels. The system shall be provided with | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | [9 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | It shall provide rated 300 KVAR in suitable nos. of steps & of suitable rating of capacitors (minimum 8 steps up to 250 kVAR and 12 steps for above 250 kVAR bank), as per specification. The panel shall also comply with following : | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 303000000 | 630 Amps TPN MCCB incomer with 25 KA breaking capacity to be provided : | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 303000000 | Microprocessor APFC controller shall continuously monitor all three phases and displays various Electrical Parameters like voltage, input current, capacitive current, KVA demand,KW, Power Factor, self diagnostic error code indication with printout facility of the above with RS 232C/485 port. Controller should mounted on the front side of the panel. It shall have data logging for minimum 2 months, it shall provide thyristor output for maximum 16 stages. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 303000000 | Fast response time of ON capacitors 20-60 miliseconds. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 303000000 | Super fast electronic fuse and links of the proper rating to be used for grouping the capacitor banks. Capacitor shall be connected with fast discharge resistances. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 303000000 | Thyristor having suitable capacity to carry expected current continuosly. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 303000000 | Necessary control and firing card with proper wiring and lugs of the required rating to be provided. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 303000000 | Heavy duty exhaust fans to be provided for cooling Thyristors. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 303000000 | LED indication for number of capacitor banks ON. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 303000000 | LED indication of Power Factor lagging or leading. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 303000000 | Auto/manual selector switch with necessary wiring to operate APFC panel in manual mode bypassing APFC relay. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 303000000 | The APFC system shall be provided with following : | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Protections : | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
a. | 303000000 | Over voltage. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
b. | 303000000 | Voltage imbalance. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
c. | 303000000 | Over temperature-system should be in standby mode and automatically restart after above condition restored. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
d. | 303000000 | Total Harmonic Distortion | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 303000000 | 7% value series reactor with iron core | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 303000000 | Capacitor Units shall have 525 V and rating shall be suitably increased considering reactors into account. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Capacitor automatic control panel ( 300 KVAR) as described above. | [8 empty] | Sets | 2 | 711034.13 | 0 | 711034.13 | 53348.8908 | 0 | 764383.0208 | 31650 | 3911.94 | 0 | 35561.94 | 1528766.0415 | 71123.88 | 1599890 | 10 | 2 | 142206.826 | 0 | 142206.826 | 10669.7782 | 0 | 152876.6042 | 6330 | 782.388 | 0 | 7112.388 | 159988.9922
| 303000000 | Note: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Total watt-losses excluding discharge resistors shall be lessthan or equal to 0.45 W / kVAr for MPP capacitors. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Test certificate shall be provided confirming the watt-loss/KVAR | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
F. | 303000000 | EARTHING INSTALLATION (FOR POWER DISTRIBUTION SYSTEMS, UPS SYSTEM, DG SETS & EPABX | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 303000000 | Supply and fixing of following bare copper /GI tapes / wires including all necessary fixing accessories and effecting connections as per specifications. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.1 | 303000000 | 50 x 6 mm thick GI tape. | [8 empty] | RM | 850 | 182.515 | 0 | 182.515 | 13.6941 | 0 | 196.2091 | 69.63 | 8.6063 | 0 | 78.2363 | 166777.7354 | 66500.8278 | 233279 | 10 | 850 | 15513.775 | 0 | 15513.775 | 1163.9985 | 0 | 16677.7735 | 5918.55 | 731.5328 | 0 | 6650.0828 | 23327.8563
1.2 | 303000000 | 32 x 6 mm thick GI tape. | [8 empty] | RM | 80 | 129.765 | 0 | 129.765 | 9.7363 | 0 | 139.5013 | 56.97 | 7.0415 | 0 | 64.0115 | 11160.1014 | 5120.9194 | 16281 | 10 | 80 | 1038.12 | 0 | 1038.12 | 77.8901 | 0 | 1116.0101 | 455.76 | 56.3319 | 0 | 512.0919 | 1628.1021
1.3 | 303000000 | 25 x 6 mm thick GI tape. | [8 empty] | RM | 300 | 90.73 | 0 | 90.73 | 6.8075 | 0 | 97.5375 | 40.09 | 4.9551 | 0 | 45.0451 | 29261.2416 | 13513.5372 | 42775 | 10 | 300 | 2721.9 | 0 | 2721.9 | 204.2242 | 0 | 2926.1242 | 1202.7 | 148.6537 | 0 | 1351.3537 | 4277.4779
1.3 | 303000000 | 25 x 6 mm thick copper tape. | [8 empty] | RM | 25 | 947.39 | 0 | 947.39 | 71.0827 | 0 | 1018.4727 | 37.98 | 4.6943 | 0 | 42.6743 | 25461.8168 | 1066.8582 | 26529 | 10 | 25 | 2368.475 | 0 | 2368.475 | 177.7067 | 0 | 2546.1817 | 94.95 | 11.7358 | 0 | 106.6858 | 2652.8675
1.4 | 303000000 | 25 x 3 mm thick GI tape. | [8 empty] | RM | 100 | 51.695 | 0 | 51.695 | 3.8787 | 0 | 55.5737 | 31.65 | 3.9119 | 0 | 35.5619 | 5557.3676 | 3556.194 | 9114 | 10 | 100 | 516.95 | 0 | 516.95 | 38.7868 | 0 | 555.7368 | 316.5 | 39.1194 | 0 | 355.6194 | 911.3562
1.4 | 303000000 | 15 x 3 mm thick GI tape. | [8 empty] | RM | 650 | 28.485 | 0 | 28.485 | 2.1372 | 0 | 30.6222 | 27.43 | 3.3903 | 0 | 30.8203 | 19904.4492 | 20033.2262 | 39938 | 10 | 650 | 1851.525 | 0 | 1851.525 | 138.9199 | 0 | 1990.4449 | 1782.95 | 220.3726 | 0 | 2003.3226 | 3993.7675
1.5 | 303000000 | 8 SWG GI wire | [8 empty] | RM | 300 | 10.55 | 0 | 10.55 | 0.79157 | 0 | 11.3416 | 4.22 | 0.52159 | 0 | 4.7416 | 3402.47 | 1422.4776 | 4825 | 10 | 300 | 316.5 | 0 | 316.5 | 23.747 | 0 | 340.247 | 126.6 | 15.6478 | 0 | 142.2478 | 482.4948
2 | 303000000 | Providing and laying of 600 x 600 x 3.15 mm thick tined copper plate electrode, with 2 Nos 50 x 6 mm copper strips from earth plate electrode to inspection chamber, 50 mm dia medium class GI pipe, CI funnel with 20 gauge GI wire mesh, masonry chamber 1000 x 500 mm with concrete base C I heavy duty / chequered plate manhole cover with frame painted with bitumastic paint and packing with mixture of charcoal and common salt around plate electrode including digging of pit upto permanent moisture level and as per soil condition but not less than 3 meters and back filling as required. (For ups& DG neutral earthing) | [8 empty] | No. | 6 | 26583.89 | 0 | 26583.89 | 1994.5893 | 0 | 28578.4793 | 3165 | 391.194 | 0 | 3556.194 | 171470.8756 | 21337.164 | 192808 | 10 | 6 | 15950.334 | 0 | 15950.334 | 1196.7536 | 0 | 17147.0876 | 1899 | 234.7164 | 0 | 2133.7164 | 19280.804
3 | 303000000 | Providing and laying of 600 x 600 x 6.3 mm thick GI plate electrode, with 2 nos. 50 X 6 mm GI strips from earth plate electrode to inspection chamber, 50 mm dia medium class GI pipe, CI funnel with 20 gauge GI wire mesh, masonry chamber 1000 X 500 mm with concrete base CI manhole cover with frame painted with bitumastic paint and packing with mixture of charcoal and common salt around plate electrode including digging of pit upto permanent moisture level but not less than 3 meters and back filling as required. | [8 empty] | No. | 16 | 9573.07 | 0 | 9573.07 | 718.2674 | 0 | 10291.3374 | 2658.6 | 328.603 | 0 | 2987.203 | 164661.3991 | 47795.2474 | 212457 | 10 | 16 | 15316.912 | 0 | 15316.912 | 1149.2279 | 0 | 16466.1399 | 4253.76 | 525.7647 | 0 | 4779.5247 | 21245.6646
4 | 303000000 | Supply and laying of following 1100 volts grade PVC insulated sheathed copper conductor unarmoured cable including copper thimbles, fixing hardware as required. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4.1 | 303000000 | Single core 35 sq.mm Green colour cable | [8 empty] | RM | 175 | 294.345 | 0 | 294.345 | 22.0847 | 0 | 316.4297 | 25.32 | 3.1296 | 0 | 28.4496 | 55375.1984 | 4978.6716 | 60354 | 10 | 175 | 5151.0375 | 0 | 5151.0375 | 386.4823 | 0 | 5537.5198 | 443.1 | 54.7672 | 0 | 497.8672 | 6035.387
5 | 303000000 | Supply and laying of GI pipe under road / paved area crossing etc. including excavation back filling ramming and making good. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.1 | 303000000 | 50 mm dia pipe. | [8 empty] | RM | 25 | 468.42 | 0 | 468.42 | 35.1456 | 0 | 503.5656 | 94.95 | 11.7358 | 0 | 106.6858 | 12589.1388 | 2667.1455 | 15256 | 10 | 25 | 1171.05 | 0 | 1171.05 | 87.8639 | 0 | 1258.9139 | 237.375 | 29.3395 | 0 | 266.7145 | 1525.6284
5.2 | 303000000 | 100 mm dia pipe. | [8 empty] | RM | 25 | 1113.025 | 0 | 1113.025 | 83.5103 | 0 | 1196.5353 | 120.27 | 14.8654 | 0 | 135.1354 | 29913.3816 | 3378.3843 | 33292 | 10 | 25 | 2782.5625 | 0 | 2782.5625 | 208.7757 | 0 | 2991.3382 | 300.675 | 37.1634 | 0 | 337.8384 | 3329.1766
6 | 303000000 | Supply and installation of 50 x 6 mm Cu busbar mounted on insulators and having 6 nos. holes for terminating single core 35 Sq.mm flexible cable with the entire assembly enclosed in 1.6 mm thick MS enclosure of approved make, design & painted with approved paint shade. (for UPS/low volt earthing and installed in electrical shaft). | [8 empty] | Nos. | 1 | 5207.48 | 0 | 5207.48 | 390.7172 | 0 | 5598.1972 | 633 | 78.2388 | 0 | 711.2388 | 5598.1972 | 711.2388 | 6309 | 10 | 1 | 520.748 | 0 | 520.748 | 39.0717 | 0 | 559.8197 | 63.3 | 7.8239 | 0 | 71.1239 | 630.9436
G. | 303000000 | LIGHTING PROTECTION SYSTEM | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | (Based on New Zealand Standards) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 303000000 | Supply and fixing of following Erico LPI or equivalent make enhanced air terminals as per specifications. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.1 | 303000000 | Dynasphere terminal – stainless steel for hostile environment with necessary accessories like FRP mast with base, inlinr coupler, grips, fixing materials etc. complete as per specification. | [8 empty] | sets | 1 | 129997.1 | 0 | 129997.1 | 9753.6824 | 0 | 139750.7824 | 6330 | 782.388 | 0 | 7112.388 | 139750.7824 | 7112.388 | 146863 | 10 | 1 | 12999.71 | 0 | 12999.71 | 975.3682 | 0 | 13975.0782 | 633 | 78.2388 | 0 | 711.2388 | 14686.317
1.2 | 303000000 | Supply and fixing of 25x3mm bare GI tapes down conductor including all necessary fixing accessories and effecting connections as per specifications. | [8 empty] | Mtrs. | 180 | 51.695 | 0 | 51.695 | 3.8787 | 0 | 55.5737 | 50.64 | 6.2591 | 0 | 56.8991 | 10003.2617 | 10241.8387 | 20245 | 10 | 180 | 930.51 | 0 | 930.51 | 69.8162 | 0 | 1000.3262 | 911.52 | 112.6639 | 0 | 1024.1839 | 2024.51
1.3 | 303000000 | Providing and laying of 600 x 600 x 6.3 mm thick GI electrode, with 2 nos. 50 X 6 mm GI strips from earth electrode to inspection chamber, 50 mm dia medium class GI pipe, CI funnel with 20 gauge GI wire mesh, masonry chamber 1000 X 500 mm with concrete base CI manhole cover with frame painted with bitumastic paint and packing with mixture of charocoal and common salt around plate electrode including digging of pit upto permanent moisture level but not less than 3 meters and back filling as required.. | [8 empty] | Nos. | 2 | 9080.385 | 0 | 9080.385 | 681.3013 | 0 | 9761.6863 | 2532 | 312.9552 | 0 | 2844.9552 | 19523.3726 | 5689.9104 | 25213 | 10 | 2 | 1816.077 | 0 | 1816.077 | 136.2603 | 0 | 1952.3373 | 506.4 | 62.591 | 0 | 568.991 | 2521.3283
1.4 | 303000000 | Supply and laying of medium class GI pipe under road / paved area crossing etc. including excavation back filling ramming and making good (depth of excavation shall be minimum 750 mm). | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.4.1 | 303000000 | 75 mm dia pipe | [8 empty] | RM | 25 | 781.755 | 0 | 781.755 | 58.6551 | 0 | 840.4101 | 113.94 | 14.083 | 0 | 128.023 | 21010.2519 | 3200.5746 | 24211 | 10 | 25 | 1954.3875 | 0 | 1954.3875 | 146.6377 | 0 | 2101.0252 | 284.85 | 35.2075 | 0 | 320.0575 | 2421.0827
1.5 | 303000000 | Providing and fixing of lightning event counter MK4 model No-LEC-IV as per specification | [8 empty] | Nos. | 1 | 15850.32 | 0 | 15850.32 | 1189.2495 | 0 | 17039.5695 | 316.5 | 39.1194 | 0 | 355.6194 | 17039.5695 | 355.6194 | 17395 | 10 | 1 | 1585.032 | 0 | 1585.032 | 118.925 | 0 | 1703.957 | 31.65 | 3.9119 | 0 | 35.5619 | 1739.5189
1.6 | 303000000 | Providing and fixing of test link in weather proof 1.6 mm thick MS box of approved make & design | [8 empty] | Nos. | 1 | 2343.155 | 0 | 2343.155 | 175.8069 | 0 | 2518.9619 | 316.5 | 39.1194 | 0 | 355.6194 | 2518.9619 | 355.6194 | 2875 | 10 | 1 | 234.3155 | 0 | 234.3155 | 17.5807 | 0 | 251.8962 | 31.65 | 3.9119 | 0 | 35.5619 | 287.4581
H. | 303000000 | SUPPLY & INSTALLATION OF LIGHTING FIXTURES | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Supply of the following lighting fixtures with all fixing accessories etc. as required. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 303000000 | Fluorescent lighting fixture Philips TCS 669/228 HF or approved equal in quality and design complete with T5 fluorescent lamp. (For office ltg) | [8 empty] | Nos. | 5 | 3511.04 | 0 | 3511.04 | 263.4333 | 0 | 3774.4733 | 0 | 0 | 0 | 0 | 18872.3667 | 0 | 18872 | 10 | 5 | 1755.52 | 0 | 1755.52 | 131.7167 | 0 | 1887.2367 | 0 | 0 | 0 | 0 | 1887.2367
2 | 303000000 | Fluorescent lighting fixture Philips TBS 669/414 D6 HF or approved equal in quality and design complete with T5 fluorescent lamp. (For office ltg) | [8 empty] | Nos. | 130 | 3718.875 | 0 | 3718.875 | 279.0272 | 0 | 3997.9022 | 0 | 0 | 0 | 0 | 519727.2849 | 0 | 519727 | 10 | 130 | 48345.375 | 0 | 48345.375 | 3627.3535 | 0 | 51972.7285 | 0 | 0 | 0 | 0 | 51972.7285
3 | 303000000 | Fluorescent lighting fixture Philips TBS 570/414 HF ODF-WH or approved equal in quality and design complete with T5 fluorescent lamp. (For office ltg) | [8 empty] | Nos. | 15 | 4192.57 | 0 | 4192.57 | 314.5685 | 0 | 4507.1385 | 0 | 0 | 0 | 0 | 67607.0779 | 0 | 67607 | 10 | 15 | 6288.855 | 0 | 6288.855 | 471.8528 | 0 | 6760.7078 | 0 | 0 | 0 | 0 | 6760.7078
4 | 303000000 | Fluorescent lighting fixture Philips TBS 520/228 MI HF or approved equal in quality and design complete with T5 fluorescent lamp. (For store areas) | [8 empty] | Nos. | 85 | 1718.595 | 0 | 1718.595 | 128.9462 | 0 | 1847.5412 | 0 | 0 | 0 | 0 | 157041.0005 | 0 | 157041 | 10 | 85 | 14608.0575 | 0 | 14608.0575 | 1096.0426 | 0 | 15704.1001 | 0 | 0 | 0 | 0 | 15704.1001
5 | 303000000 | T5 Fluorescent lighting fixture Philips TMS 122/128 HF or approved equal in quality and design complete with T5 fluorescent lamp. (For plant room, carpark , Electrical room, staircase) | [8 empty] | Nos. | 275 | 932.62 | 0 | 932.62 | 69.9745 | 0 | 1002.5945 | 0 | 0 | 0 | 0 | 275713.4816 | 0 | 275713 | 10 | 275 | 25647.05 | 0 | 25647.05 | 1924.2982 | 0 | 27571.3482 | 0 | 0 | 0 | 0 | 27571.3482
6 | 303000000 | T5 Fluorescent lighting fixture Philips TMS 122/228 HF or approved equal in quality and design complete with T5 fluorescent lamp. (For plant room, carpark , Electrical room, staircase) | [8 empty] | Nos. | 225 | 1251.23 | 0 | 1251.23 | 93.8798 | 0 | 1345.1098 | 0 | 0 | 0 | 0 | 302649.7021 | 0 | 302650 | 10 | 225 | 28152.675 | 0 | 28152.675 | 2112.2952 | 0 | 30264.9702 | 0 | 0 | 0 | 0 | 30264.9702
7 | 303000000 | Fluorescent lighting fixture Philips TBS 670 2X36 W TL-DEB BOCA or approved equal in quality and design complete with fluorescent lamp. (For Kitchen & Laundry) | [8 empty] | Nos. | 36 | 5674.845 | 0 | 5674.845 | 425.7836 | 0 | 6100.6286 | 0 | 0 | 0 | 0 | 219622.6303 | 0 | 219623 | 10 | 36 | 20429.442 | 0 | 20429.442 | 1532.821 | 0 | 21962.263 | 0 | 0 | 0 | 0 | 21962.263
8 | 303000000 | Fluorescent lighting fixture Philips FBS 650 2X36 W PL-EB BOCA HF or approved equal in quality and design complete with PL lamp. (For Kitchen ) | [8 empty] | Nos. | 125 | 5570.4 | 0 | 5570.4 | 417.9471 | 0 | 5988.3471 | 0 | 0 | 0 | 0 | 748543.389 | 0 | 748543 | 10 | 125 | 69630 | 0 | 69630 | 5224.3389 | 0 | 74854.3389 | 0 | 0 | 0 | 0 | 74854.3389
9 | 303000000 | Fluorescent lighting fixture Philips TCW 450 128 W HF or approved equal in quality and design complete with T5 lamp. (For service & terrace floor ) | [8 empty] | Nos. | 30 | 1983.4 | 0 | 1983.4 | 148.8145 | 0 | 2132.2145 | 0 | 0 | 0 | 0 | 63966.4351 | 0 | 63966 | 10 | 30 | 5950.2 | 0 | 5950.2 | 446.4435 | 0 | 6396.6435 | 0 | 0 | 0 | 0 | 6396.6435
10 | 303000000 | Fluorescent lighting fixture Philips TCW 450 228 W HF or approved equal in quality and design complete with T5 lamp. | [8 empty] | Nos. | 5 | 2446.545 | 0 | 2446.545 | 183.5643 | 0 | 2630.1093 | 0 | 0 | 0 | 0 | 13150.5464 | 0 | 13151 | 10 | 5 | 1223.2725 | 0 | 1223.2725 | 91.7821 | 0 | 1315.0546 | 0 | 0 | 0 | 0 | 1315.0546
11 | 303000000 | Recessed step light fixture Philips DBP 701/2xPLC 18 Watt CFL or approved equal in quality and design (Ramp Lighting) | [8 empty] | Nos. | 15 | 12460.605 | 0 | 12460.605 | 934.9192 | 0 | 13395.5242 | 0 | 0 | 0 | 0 | 200932.8629 | 0 | 200933 | 10 | 15 | 18690.9075 | 0 | 18690.9075 | 1402.3788 | 0 | 20093.2863 | 0 | 0 | 0 | 0 | 20093.2863
12 | 303000000 | Wall mounting luminaire complete with all accessories Philips Cat No. FMS 300 /111 HF with1x PL-S 11 watt or approved equal in quality and design complete with lamp. (Toilet Mirror ltg.) | [8 empty] | Nos. | 10 | 526.445 | 0 | 526.445 | 39.4992 | 0 | 565.9442 | 0 | 0 | 0 | 0 | 5659.4417 | 0 | 5659 | 10 | 10 | 526.445 | 0 | 526.445 | 39.4992 | 0 | 565.9442 | 0 | 0 | 0 | 0 | 565.9442
13 | 303000000 | Recessed compact fluorescent Philips Cat No. FBH 150 //218 T HF with 2 x PLC-18 watt CFL or approved equal in quality and design. | [8 empty] | Nos. | 345 | 1269.165 | 0 | 1269.165 | 95.2254 | 0 | 1364.3904 | 0 | 0 | 0 | 0 | 470714.7052 | 0 | 470715 | 10 | 345 | 43786.1925 | 0 | 43786.1925 | 3285.278 | 0 | 47071.4705 | 0 | 0 | 0 | 0 | 47071.4705
14 | 303000000 | Recessed compact fluorescent Philips Cat No. FBH 150 //118 T HF with 1 x PLC-18 watt CFL or approved equal in quality and design. | [8 empty] | Nos. | 45 | 853.495 | 0 | 853.495 | 64.0377 | 0 | 917.5327 | 0 | 0 | 0 | 0 | 41288.9728 | 0 | 41289 | 10 | 45 | 3840.7275 | 0 | 3840.7275 | 288.1698 | 0 | 4128.8973 | 0 | 0 | 0 | 0 | 4128.8973
16 | 303000000 | Recessed 14.6 watt LED light fixture Philips type no. BBS 175 or approved equal in quality and design. | [8 empty] | Nos. | 220 | 1870.515 | 0 | 1870.515 | 140.3447 | 0 | 2010.8597 | 0 | 0 | 0 | 0 | 442389.1429 | 0 | 442389 | 10 | 220 | 41151.33 | 0 | 41151.33 | 3087.5843 | 0 | 44238.9143 | 0 | 0 | 0 | 0 | 44238.9143
| 303000000 | BBS 175 1XDLED-5000 PSU WH PHILIPS MAKE CONSIDERED | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 303000000 | Recessed 7 watt LED light fixture Philips type no. GU10-230V or approved equal in quality and design. | [8 empty] | Nos. | 15 | 1490.715 | 0 | 1490.715 | 111.8483 | 0 | 1602.5633 | 0 | 0 | 0 | 0 | 24038.4502 | 0 | 24038 | 10 | 15 | 2236.0725 | 0 | 2236.0725 | 167.7725 | 0 | 2403.845 | 0 | 0 | 0 | 0 | 2403.845
| 303000000 | QBSO27 1XMAX50 W/12V GU5.3WH WITH 7W GU10CONSIDERD | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 303000000 | Bulk head lighting fixtures Philips make FXC-101 or approved equal in quality and design with 9 watt PL lamps. (Lift Shaft & guest room shaft Ltg.) | [8 empty] | Nos. | 375 | 680.475 | 0 | 680.475 | 51.056 | 0 | 731.531 | 0 | 0 | 0 | 0 | 274324.1397 | 0 | 274324 | 10 | 375 | 25517.8125 | 0 | 25517.8125 | 1914.6015 | 0 | 27432.414 | 0 | 0 | 0 | 0 | 27432.414
19 | 303000000 | Self contained single sided exit sign for wall / ceiling / pendant cantilever mounting with 9 W CFL tube for non maintained battery backup emergency lighting for 3 hours duration Thorn EXB3, Prolite make or approved equal in quality and design. | [8 empty] | Nos. | 35 | 4091.29 | 0 | 4091.29 | 306.9695 | 0 | 4398.2595 | 0 | 0 | 0 | 0 | 153939.0821 | 0 | 153939 | 10 | 35 | 14319.515 | 0 | 14319.515 | 1074.3932 | 0 | 15393.9082 | 0 | 0 | 0 | 0 | 15393.9082
20 | 303000000 | Self contained double sided exit single for wall / ceiling / pendant cantilever mounting with 9 watt CFL tube, non maintained battery backup 3 hours duration Thorn EXB3, Prolite make or approved equal in quality and design. | [8 empty] | Nos. | 40 | 4791.81 | 0 | 4791.81 | 359.5295 | 0 | 5151.3395 | 0 | 0 | 0 | 0 | 206053.5802 | 0 | 206054 | 10 | 40 | 19167.24 | 0 | 19167.24 | 1438.118 | 0 | 20605.358 | 0 | 0 | 0 | 0 | 20605.358
21 | 303000000 | Aviation obstruction light with Light Emitting Diods (LEDs) with photochromatic switch Complete with all accessories as approved. | [8 empty] | Nos. | 1 | 3883.455 | 0 | 3883.455 | 291.3756 | 0 | 4174.8306 | 0 | 0 | 0 | 0 | 4174.8306 | 0 | 4175 | 10 | 1 | 388.3455 | 0 | 388.3455 | 29.1376 | 0 | 417.4831 | 0 | 0 | 0 | 0 | 417.4831
| 303000000 | XGP400 1XLED-K2/RD PHILIPD CONSIDERED | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 303000000 | 48" dia sweep ceiling fan with step type fan regulator of approved make complete with all accessories. | [8 empty] | Nos. | 10 | 1947.53 | 0 | 1947.53 | 146.1232 | 0 | 2093.6532 | 0 | 0 | 0 | 0 | 20936.5318 | 0 | 20937 | 10 | 10 | 1947.53 | 0 | 1947.53 | 146.1232 | 0 | 2093.6532 | 0 | 0 | 0 | 0 | 2093.6532
23 | 303000000 | Supply & installation of ON/OFF type occupancy sensors wipro COP 11010 OR equivalent with 360 degree coverage , with built in switch/relay & foot print diameter of 6-8 metres for installation in toilet blocks. | [8 empty] | Nos. | 50 | 3588.055 | 0 | 3588.055 | 269.2118 | 0 | 3857.2668 | 0 | 0 | 0 | 0 | 192863.3383 | 0 | 192863 | 10 | 50 | 17940.275 | 0 | 17940.275 | 1346.0588 | 0 | 19286.3338 | 0 | 0 | 0 | 0 | 19286.3338
I. | 303000000 | INSTALLATION OF LIGHTING FIXTURES | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Installation of the following lighting fixtures with all fixing accessories etc. as required. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 303000000 | Fluorescent lighting fixture Philips TCS 669/228 HF or approved equal in quality and design complete with T5 fluorescent lamp. | [8 empty] | Nos. | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 103.39 | 12.779 | 0 | 116.169 | 0 | 1742.5351 | 1743 | 10 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 155.085 | 19.1685 | 0 | 174.2535 | 174.2535
2 | 303000000 | Fluorescent lighting fixture Philips TBS 669/414 D6 HF or approved equal in quality and design complete with T5 fluorescent lamp. | [8 empty] | Nos. | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 103.39 | 12.779 | 0 | 116.169 | 0 | 5111.4362 | 5111 | 10 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 454.916 | 56.2276 | 0 | 511.1436 | 511.1436
3 | 303000000 | T5 Fluorescent lighting fixture Philips TMS 122/128 HF or approved equal in quality and design complete with T5 fluorescent lamp. (For cove lighting) | [8 empty] | Nos. | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 103.39 | 12.779 | 0 | 116.169 | 0 | 2904.2251 | 2904 | 10 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 258.475 | 31.9475 | 0 | 290.4225 | 290.4225
4 | 303000000 | Recessed compact fluorescent Philips Cat No. FBH 150 //218 T HF with 2 x PLC-18 watt CFL or approved equal in quality and design. | [8 empty] | Nos. | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 128.71 | 15.9086 | 0 | 144.6186 | 0 | 2169.2783 | 2169 | 10 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 193.065 | 23.8628 | 0 | 216.9278 | 216.9278
5 | 303000000 | Recessed compact fluorescent Philips Cat No. FBH 150 //118 T HF with 1 x PLC-18 watt CFL or approved equal in quality and design. | [8 empty] | Nos. | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 128.71 | 15.9086 | 0 | 144.6186 | 0 | 2169.2783 | 2169 | 10 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 193.065 | 23.8628 | 0 | 216.9278 | 216.9278
6 | 303000000 | Recessed 15 watt LED light fixture Philips type no. BBS 181 or approved equal in quality and design. | [8 empty] | Nos. | 535 | 0 | 0 | 0 | 0 | 0 | 0 | 103.39 | 12.779 | 0 | 116.169 | 0 | 62150.4171 | 62150 | 10 | 535 | 0 | 0 | 0 | 0 | 0 | 0 | 5531.365 | 683.6767 | 0 | 6215.0417 | 6215.0417
7 | 303000000 | 50 watts 12 volts halogen down lighter with 220 /12 volts transformer and lamp Philips Cat No. DN-652 or approved equal in quality and design (Tentative) | [8 empty] | Nos. | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 194.12 | 23.9932 | 0 | 218.1132 | 0 | 10905.6616 | 10906 | 10 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 970.6 | 119.9662 | 0 | 1090.5662 | 1090.5662
8 | 303000000 | Recessed mounted metal Halide Philips Cat No. MBS 050 / 70 or approved equal in quality and design with CDM-TP 70W/ 1x MHN- TD 70W (Tentative) | [8 empty] | Nos. | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 194.12 | 23.9932 | 0 | 218.1132 | 0 | 3271.6985 | 3272 | 10 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 291.18 | 35.9898 | 0 | 327.1698 | 327.1698
9 | 303000000 | 1 meter low voltage track length for use with 12 V output Philips make or approved equal in quality and design | [8 empty] | Nos. | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 322.83 | 39.9018 | 0 | 362.7318 | 0 | 3627.3179 | 3627 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 322.83 | 39.9018 | 0 | 362.7318 | 362.7318
10 | 303000000 | LV track adaptor for connecting LV spots to the track unit Philips make or approved equal in quality and design | [8 empty] | Nos. | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 258.475 | 31.9475 | 0 | 290.4225 | 0 | 8712.6753 | 8713 | 10 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 775.425 | 95.8425 | 0 | 871.2675 | 871.2675
11 | 303000000 | 150 VA electronic transformer for LV track unit Philips make or approved equal in quality and design | [8 empty] | Nos. | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 258.475 | 31.9475 | 0 | 290.4225 | 0 | 2904.2251 | 2904 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 258.475 | 31.9475 | 0 | 290.4225 | 290.4225
12 | 303000000 | Current supply end assembly for LV track unit Philips make or approved equal in quality and design | [8 empty] | Nos. | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 258.475 | 31.9475 | 0 | 290.4225 | 0 | 2904.2251 | 2904 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 258.475 | 31.9475 | 0 | 290.4225 | 290.4225
13 | 303000000 | Chandelier of approved quality and design | [8 empty] | Nos. | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 645.66 | 79.8036 | 0 | 725.4636 | 0 | 6529.1722 | 6529 | 10 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 581.094 | 71.8232 | 0 | 652.9172 | 652.9172
14 | 303000000 | LED strip light for cove lighting | [8 empty] | RM. | 748 | 0 | 0 | 0 | 0 | 0 | 0 | 103.39 | 12.779 | 0 | 116.169 | 0 | 86894.415 | 86894 | 10 | 748 | 0 | 0 | 0 | 0 | 0 | 0 | 7733.572 | 955.8695 | 0 | 8689.4415 | 8689.4415
| 303000000 | (Guest Room Ltg Fixture) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | 303000000 | Recessed 10 W LED downlight (L1) | [8 empty] | No. | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 103.39 | 12.779 | 0 | 116.169 | 0 | 46467.6016 | 46468 | 10 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 4135.6 | 511.1602 | 0 | 4646.7602 | 4646.7602
16 | 303000000 | Recessed 5W adjustable down light (L2) | [8 empty] | No. | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 103.39 | 12.779 | 0 | 116.169 | 0 | 46467.6016 | 46468 | 10 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 4135.6 | 511.1602 | 0 | 4646.7602 | 4646.7602
17 | 303000000 | Recessed 5W LED downlight (L3) | [8 empty] | No. | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 103.39 | 12.779 | 0 | 116.169 | 0 | 69701.4024 | 69701 | 10 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 6203.4 | 766.7402 | 0 | 6970.1402 | 6970.1402
18 | 303000000 | Recessed 7W Low Voltage dimmable down light (L4) | [8 empty] | No. | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 103.39 | 12.779 | 0 | 116.169 | 0 | 46467.6016 | 46468 | 10 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 4135.6 | 511.1602 | 0 | 4646.7602 | 4646.7602
19 | 303000000 | Recessed 7W Low Voltage down light (L5 steam proof) | [8 empty] | No. | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 103.39 | 12.779 | 0 | 116.169 | 0 | 23233.8008 | 23234 | 10 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 2067.8 | 255.5801 | 0 | 2323.3801 | 2323.3801
20 | 303000000 | Fluorescent T5 light fixture (L6 & L10) | [8 empty] | No. | 800 | 0 | 0 | 0 | 0 | 0 | 0 | 103.39 | 12.779 | 0 | 116.169 | 0 | 92935.2032 | 92935 | 10 | 800 | 0 | 0 | 0 | 0 | 0 | 0 | 8271.2 | 1022.3203 | 0 | 9293.5203 | 9293.5203
21 | 303000000 | Under counter LED night light (L7) | [8 empty] | No. | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 103.39 | 12.779 | 0 | 116.169 | 0 | 46467.6016 | 46468 | 10 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 4135.6 | 511.1602 | 0 | 4646.7602 | 4646.7602
22 | 303000000 | Fluorescent T5 light fixture (L8) | [8 empty] | No. | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 103.39 | 12.779 | 0 | 116.169 | 0 | 23233.8008 | 23234 | 10 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 2067.8 | 255.5801 | 0 | 2323.3801 | 2323.3801
23 | 303000000 | Decorative bed side light fixture (L9) | [8 empty] | No. | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 103.39 | 12.779 | 0 | 116.169 | 0 | 46467.6016 | 46468 | 10 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 4135.6 | 511.1602 | 0 | 4646.7602 | 4646.7602
24 | 303000000 | Bed Head Wall light fixture (L11) | [8 empty] | No. | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 103.39 | 12.779 | 0 | 116.169 | 0 | 46467.6016 | 46468 | 10 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 4135.6 | 511.1602 | 0 | 4646.7602 | 4646.7602
25 | 303000000 | Recessed 3W LED down light (L13) | [8 empty] | No. | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 103.39 | 12.779 | 0 | 116.169 | 0 | 23233.8008 | 23234 | 10 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 2067.8 | 255.5801 | 0 | 2323.3801 | 2323.3801
26 | 303000000 | Low Voltage Desk light fixture (L14) | [8 empty] | No. | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 103.39 | 12.779 | 0 | 116.169 | 0 | 23233.8008 | 23234 | 10 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 2067.8 | 255.5801 | 0 | 2323.3801 | 2323.3801
27 | 303000000 | LED strip light 12w /mtr (L15) | [8 empty] | Mtr | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 103.39 | 12.779 | 0 | 116.169 | 0 | 69701.4024 | 69701 | 10 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 6203.4 | 766.7402 | 0 | 6970.1402 | 6970.1402
J. | 303000000 | INVERTER | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 303000000 | Inverter | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 303000000 | Supply & installation of 20 KVA inverter input 3 phase (415 V + 10%) output 3 phase (415 V + 10%) with sealed maintenance free batteries suitable for 15 minutes backup including providing suitable size of 14 gauge MS battery rack suitably painted.. | [8 empty] | Set | 1 | 370257.525 | 0 | 370257.525 | 27780.4221 | 0 | 398037.9471 | 6330 | 782.388 | 0 | 7112.388 | 398037.9471 | 7112.388 | 405150 | 10 | 1 | 37025.7525 | 0 | 37025.7525 | 2778.0422 | 0 | 39803.7947 | 633 | 78.2388 | 0 | 711.2388 | 40515.0335
K. | 303000000 | HV INSTALLATION | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
I | 303000000 | SUPPLY AND INSTALLATION OF SUB-STATION EQUIPMENT | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 303000000 | Supply, installation, testing and commissioning of 11 KV SF6 insulated compact HT panel consisting of 1 Nos. incoming isolator switch and 2 nos. outgoing 630 Amps 25 KA for 1 sec. motorized Vacuum circuit breaker as per feeder details given in the specification and single line diagram. | [8 empty] | Set | 1 | 948967.225 | 0 | 948967.225 | 71201.0109 | 0 | 1020168.2359 | 45576 | 5633.1936 | 0 | 51209.1936 | 1020168.2359 | 51209.1936 | 1071377 | 10 | 1 | 94896.7225 | 0 | 94896.7225 | 7120.1011 | 0 | 102016.8236 | 4557.6 | 563.3194 | 0 | 5120.9194 | 107137.7429
2 | 303000000 | Supply, installation, testing and commissioning of 1000 KVA capacity 11/ 0.433 KV, Z= 5 % step down oil cooled transformers with ON load tap changer(OLTC) on HV side, and with surge Arrestor and surge counter on HV side as per specification. | [8 empty] | No. | 2 | 1387025.38 | 0 | 1387025.38 | 104068.5143 | 0 | 1491093.8943 | 37980 | 4694.328 | 0 | 42674.328 | 2982187.7885 | 85348.656 | 3067536 | 10 | 2 | 277405.076 | 0 | 277405.076 | 20813.7029 | 0 | 298218.7789 | 7596 | 938.8656 | 0 | 8534.8656 | 306753.6445
3 | 303000000 | Supply, installation, testing and commissioning of 200 AH capacity 24 volts DC hermetically sealed maintenance free lead acid batteries duly charged. | [8 empty] | Set | 1 | 31181.58 | 0 | 31181.58 | 2339.5539 | 0 | 33521.1339 | 633 | 78.2388 | 0 | 711.2388 | 33521.1339 | 711.2388 | 34232 | 10 | 1 | 3118.158 | 0 | 3118.158 | 233.9554 | 0 | 3352.1134 | 63.3 | 7.8239 | 0 | 71.1239 | 3423.2373
4 | 303000000 | Supply, installation, testing and commissioning of battery charger unit with provisions of Boost Charing, and Float charging. Suitable for 240 V single phase + 10% AC, 50 Hz power supply as per specifications. | [8 empty] | Set | 1 | 51987.235 | 0 | 51987.235 | 3900.6022 | 0 | 55887.8372 | 1899 | 234.7164 | 0 | 2133.7164 | 55887.8372 | 2133.7164 | 58022 | 10 | 1 | 5198.7235 | 0 | 5198.7235 | 390.0602 | 0 | 5588.7837 | 189.9 | 23.4716 | 0 | 213.3716 | 5802.1554
5 | 303000000 | Supply and fixing in position the approved “Shock Treatment Charts” written in English and Local Language. These charts shall be framed in teak wood frame and covered with glass. | [8 empty] | No. | 1 | 974.82 | 0 | 974.82 | 73.1407 | 0 | 1047.9607 | 63.3 | 7.8239 | 0 | 71.1239 | 1047.9607 | 71.1239 | 1119 | 10 | 1 | 97.482 | 0 | 97.482 | 7.3141 | 0 | 104.7961 | 6.33 | 0.78239 | 0 | 7.1124 | 111.9085
6 | 303000000 | Supply and fixing in position the fire extinguishers carbon-di-odide type 2.5 Kgs capacity. | [8 empty] | No. | 2 | 3248.345 | 0 | 3248.345 | 243.7233 | 0 | 3492.0683 | 63.3 | 7.8239 | 0 | 71.1239 | 6984.1367 | 142.2478 | 7126 | 10 | 2 | 649.669 | 0 | 649.669 | 48.7447 | 0 | 698.4137 | 12.66 | 1.5648 | 0 | 14.2248 | 712.6384
7 | 303000000 | Supply and fixing in position the best quality Danger Boards of approved shape and size as specified by Local Electricity Authorities written in English & Local Languages. | [8 empty] | No. | 2 | 325.995 | 0 | 325.995 | 24.4594 | 0 | 350.4544 | 63.3 | 7.8239 | 0 | 71.1239 | 700.9088 | 142.2478 | 843 | 10 | 2 | 65.199 | 0 | 65.199 | 4.8919 | 0 | 70.0909 | 12.66 | 1.5648 | 0 | 14.2248 | 84.3157
8 | 303000000 | Supply and fixing in position 1000 mm wide rubber matting of 11 KV grade as per electricity rules. | [8 empty] | RM | 10 | 1948.585 | 0 | 1948.585 | 146.2023 | 0 | 2094.7873 | 63.3 | 7.8239 | 0 | 71.1239 | 20947.8733 | 711.2388 | 21659 | 10 | 10 | 1948.585 | 0 | 1948.585 | 146.2023 | 0 | 2094.7873 | 63.3 | 7.8239 | 0 | 71.1239 | 2165.9112
9 | 303000000 | Supply of fire buckets 5 nos. in each set duly filled with fine sand and fixed on an angle iron frame as per requirement of local authorities. Fire buckets shall be painted red from outside and white from inside with additional handle at the bottom. | [8 empty] | Sets | 1 | 6499.855 | 0 | 6499.855 | 487.6841 | 0 | 6987.5391 | 316.5 | 39.1194 | 0 | 355.6194 | 6987.5391 | 355.6194 | 7343 | 10 | 1 | 649.9855 | 0 | 649.9855 | 48.7684 | 0 | 698.7539 | 31.65 | 3.9119 | 0 | 35.5619 | 734.3159
10 | 303000000 | Supply and fixing in position the approved single line diagram framed in 1000 x 800 mm size glass frame in the sub station. | [8 empty] | No. | 2 | 1948.585 | 0 | 1948.585 | 146.2023 | 0 | 2094.7873 | 63.3 | 7.8239 | 0 | 71.1239 | 4189.5747 | 142.2478 | 4332 | 10 | 2 | 389.717 | 0 | 389.717 | 29.2405 | 0 | 418.9575 | 12.66 | 1.5648 | 0 | 14.2248 | 433.1822
11 | 303000000 | Supply of first aid box of approved make as per specification. | [8 empty] | No. | 1 | 1948.585 | 0 | 1948.585 | 146.2023 | 0 | 2094.7873 | 63.3 | 7.8239 | 0 | 71.1239 | 2094.7873 | 71.1239 | 2166 | 10 | 1 | 194.8585 | 0 | 194.8585 | 14.6202 | 0 | 209.4787 | 6.33 | 0.78239 | 0 | 7.1124 | 216.5911
12 | 303000000 | Supply of tool kit with 1 pair 12 KV rubber hand gloves of approved make. | [8 empty] | No. | 2 | 974.82 | 0 | 974.82 | 73.1407 | 0 | 1047.9607 | 63.3 | 7.8239 | 0 | 71.1239 | 2095.9215 | 142.2478 | 2238 | 10 | 2 | 194.964 | 0 | 194.964 | 14.6281 | 0 | 209.5921 | 12.66 | 1.5648 | 0 | 14.2248 | 223.8169
| 303000000 | TOTAL CARRIED TO SUMMARY | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
II | 303000000 | HT CABLES & LT CONTROL CABLES | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 303000000 | Supplying and laying following size 11 KV grade XLPE (E) aluminium conductor armoured cables laid over MS supports in existing trenches. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.1 | 303000000 | 3 C x 240 sq.mm 11 KV XLPE cable (between metering panel room to HT panel and HT panel to transformers). | [8 empty] | RM | 100 | 1116.19 | 0 | 1116.19 | 83.7477 | 0 | 1199.9377 | 126.6 | 15.6478 | 0 | 142.2478 | 119993.7736 | 14224.776 | 134219 | 10 | 100 | 11161.9 | 0 | 11161.9 | 837.4774 | 0 | 11999.3774 | 1266 | 156.4776 | 0 | 1422.4776 | 13421.855
2 | 303000000 | Supplying and making cable end terminations for the following size of 11 KV grade, XLPE aluminium conductor armoured cable including termination kit complete heat shrinkable sleeve etc. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.1 | 303000000 | 3 C x 240 sq.mm 11 KV XLPE cable (indoor) | [8 empty] | Nos. | 4 | 5041.845 | 0 | 5041.845 | 378.2896 | 0 | 5420.1346 | 2532 | 312.9552 | 0 | 2844.9552 | 21680.5385 | 11379.8208 | 33060 | 10 | 4 | 2016.738 | 0 | 2016.738 | 151.3159 | 0 | 2168.0539 | 1012.8 | 125.1821 | 0 | 1137.9821 | 3306.0359
2.2 | 303000000 | 3 C x 240 sq.mm 11 KV XLPE cable (outdoor) | [8 empty] | Nos. | 2 | 7827.045 | 0 | 7827.045 | 587.2632 | 0 | 8414.3082 | 2785.2 | 344.2507 | 0 | 3129.4507 | 16828.6164 | 6258.9014 | 23088 | 10 | 2 | 1565.409 | 0 | 1565.409 | 117.4526 | 0 | 1682.8616 | 557.04 | 68.8501 | 0 | 625.8901 | 2308.7518
3 | 303000000 | Supplying, laying GI sleeves of following sizes: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.1 | 303000000 | 150 mm dia | [8 empty] | RM | 0 | 1749.19 | 0 | 1749.19 | 131.2417 | 0 | 1880.4317 | 151.92 | 18.7773 | 0 | 170.6973 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.2 | 303000000 | 200 mm dia | [8 empty] | RM | 15 | 2216.555 | 0 | 2216.555 | 166.3081 | 0 | 2382.8631 | 189.9 | 23.4716 | 0 | 213.3716 | 35742.9468 | 3200.5746 | 38944 | 10 | 15 | 3324.8325 | 0 | 3324.8325 | 249.4622 | 0 | 3574.2947 | 284.85 | 35.2075 | 0 | 320.0575 | 3894.3521
4 | 303000000 | Supplying and laying of following 1100 volts grade PVC insulated sheathed copper conductor armoured control cables in existing trenches cables trays, clamped on wall with suitable saddles, fixing bolts, including testing and commissioning. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4.1 | 303000000 | 12 Core 2.5 sq mm PVC insulated copper conductor armoured control cables | [8 empty] | RM | 50 | 281.685 | 0 | 281.685 | 21.1348 | 0 | 302.8198 | 31.65 | 3.9119 | 0 | 35.5619 | 15140.9913 | 1778.097 | 16919 | 10 | 50 | 1408.425 | 0 | 1408.425 | 105.6741 | 0 | 1514.0991 | 158.25 | 19.5597 | 0 | 177.8097 | 1691.9088
5 | 303000000 | Cable end termination of the following PVC insulated sheathed aluminium conductor armoured cables of 1100 volt grade including supplying and fixing of crimping lugs. Double compression glands with earthing provision and cable sockets | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.1 | 303000000 | 12 Core 2.5 sq.mm Control cable | [8 empty] | Nos. | 4 | 294.345 | 0 | 294.345 | 22.0847 | 0 | 316.4297 | 189.9 | 23.4716 | 0 | 213.3716 | 1265.7188 | 853.4866 | 2119 | 10 | 4 | 117.738 | 0 | 117.738 | 8.8339 | 0 | 126.5719 | 75.96 | 9.3887 | 0 | 85.3487 | 211.9205
III | 303000000 | EARTHING FOR SUB-STATION EQUIPMENT | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 303000000 | Supplying and fixing of following bare copper / GI tapes including all necessary fixing accessories and effecting connections. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.1 | 303000000 | 50 x 8 mm thick GI tape. (For Transformer body earthing & LT breaker panel on Ground floor) | [8 empty] | RM | 250 | 251.09 | 0 | 251.09 | 18.8393 | 0 | 269.9293 | 88.62 | 10.9534 | 0 | 99.5734 | 67482.3207 | 24893.358 | 92376 | 10 | 250 | 6277.25 | 0 | 6277.25 | 470.9821 | 0 | 6748.2321 | 2215.5 | 273.8358 | 0 | 2489.3358 | 9237.5679
1.2 | 303000000 | 50 x 6 mm thick copper tape. (For Neutral earthing of Transformer & DG) | [8 empty] | RM | 300 | 1895.835 | 0 | 1895.835 | 142.2445 | 0 | 2038.0795 | 82.29 | 10.171 | 0 | 92.461 | 611423.85 | 27738.3132 | 639162 | 10 | 300 | 56875.05 | 0 | 56875.05 | 4267.335 | 0 | 61142.385 | 2468.7 | 305.1313 | 0 | 2773.8313 | 63916.2163
1.3 | 303000000 | 25 mm x 6 mm thick copper tape. | [8 empty] | RM | 25 | 948.445 | 0 | 948.445 | 71.1618 | 0 | 1019.6068 | 50.64 | 6.2591 | 0 | 56.8991 | 25490.1707 | 1422.4776 | 26913 | 10 | 25 | 2371.1125 | 0 | 2371.1125 | 177.9046 | 0 | 2549.0171 | 126.6 | 15.6478 | 0 | 142.2478 | 2691.2648
2 | 303000000 | Providing earthing stations at locations as called for including providing and laying 600 x 600 x 3.15 mm thick tinned copper electrode with 2 Nos 50 x 6 mm thick copper strip, from earth electrode to inspection chamber,50 mm dia medium class G I pipe CI / chequered plate funnel with 20 gauge G I wire mesh, masonry chamber 1000 x 500 mm with concrete base, CI chequered plate manhole cover with frame and bitumastic paint and packing of mixture of charcoal and common salt around plate electrode complete with digging of pit upto permanent misture level but not less than 3 metres and back filling as required. (For transformer Neutral Earthing) | [8 empty] | Nos. | 4 | 26583.89 | 0 | 26583.89 | 1994.5893 | 0 | 28578.4793 | 3165 | 391.194 | 0 | 3556.194 | 114313.9171 | 14224.776 | 128539 | 10 | 4 | 10633.556 | 0 | 10633.556 | 797.8357 | 0 | 11431.3917 | 1266 | 156.4776 | 0 | 1422.4776 | 12853.8693
3 | 303000000 | Providing earthing stations at locations as called for including providing and laying 600 x 600 x 6.3 mm GI electrode with 2 Nos. 50 x 6 mm thick GI stripe, from earth electrode to inspection chamber,50 mm dia medium class G I pipe CI / chequered plate funnel with 20 gauge G I wire mesh, masonry chamber 1000 x 500 mm with concrete base, CI chequered plate manhole cover with frame and bitumastic paint and packing of mixture of charcoal and common salt around plate electrode complete with digging of pit upto permanent misture level but not less than 3 metres and back filling as required. (For HT panel client & supply company, Transformer body earthing) | [8 empty] | No. | 8 | 9573.07 | 0 | 9573.07 | 718.2674 | 0 | 10291.3374 | 2658.6 | 328.603 | 0 | 2987.203 | 82330.6995 | 23897.6237 | 106228 | 10 | 8 | 7658.456 | 0 | 7658.456 | 574.614 | 0 | 8233.07 | 2126.88 | 262.8824 | 0 | 2389.7624 | 10622.8323
4 | 303000000 | Supply and laying medium class GI pipe under road/paved areas/wall crossing etc. including earth excavations refilling, ramming and making good as approved. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4.1 | 303000000 | 150 mm dia GI pipe | [8 empty] | RM | 25 | 1750.245 | 0 | 1750.245 | 131.3209 | 0 | 1881.5659 | 189.9 | 23.4716 | 0 | 213.3716 | 47039.1471 | 5334.291 | 52373 | 10 | 25 | 4375.6125 | 0 | 4375.6125 | 328.3022 | 0 | 4703.9147 | 474.75 | 58.6791 | 0 | 533.4291 | 5237.3438
L. | 303000000 | CABLING AND INSTALLATION OF LIGHTING FIXTURE FOR EXTERNAL / LANDSCAPE LIGHTING | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 303000000 | Receiving, storing handling, installing, testing and commissioning of the following lighting fixtures and poles including excavation and back filling, foundation of pole, base plate as required. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.1 | 303000000 | Recessed uplight fixture | [8 empty] | No. | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 194.12 | 23.9932 | 0 | 218.1132 | 0 | 5452.8308 | 5453 | 10 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 485.3 | 59.9831 | 0 | 545.2831 | 545.2831
1.2 | 303000000 | Recessed underwater light | [8 empty] | No. | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 194.12 | 23.9932 | 0 | 218.1132 | 0 | 2181.1323 | 2181 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 194.12 | 23.9932 | 0 | 218.1132 | 218.1132
1.3 | 303000000 | Bollard | [8 empty] | No. | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 103.39 | 12.779 | 0 | 116.169 | 0 | 580.845 | 581 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 51.695 | 6.3895 | 0 | 58.0845 | 58.0845
1.4 | 303000000 | Post top lantern | [8 empty] | No | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 103.39 | 12.779 | 0 | 116.169 | 0 | 697.014 | 697 | 10 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.034 | 7.6674 | 0 | 69.7014 | 69.7014
1.5 | 303000000 | 1 x 50 W in ground low voltage tree uplight | [8 empty] | No. | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 103.39 | 12.779 | 0 | 116.169 | 0 | 1742.5351 | 1743 | 10 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 155.085 | 19.1685 | 0 | 174.2535 | 174.2535
1.6 | 303000000 | 70 W wallmounted up down light fixtures | [8 empty] | No. | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 103.39 | 12.779 | 0 | 116.169 | 0 | 580.845 | 581 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 51.695 | 6.3895 | 0 | 58.0845 | 58.0845
1.7 | 303000000 | 150 / 250 W compact general purpose flood light with high pressure lamp | [8 empty] | No. | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 194.12 | 23.9932 | 0 | 218.1132 | 0 | 1090.5662 | 1091 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 97.06 | 11.9966 | 0 | 109.0566 | 109.0566
2 | 303000000 | Supply, laying, testing and commissioning of following size PVC insulated sheathed copper conductor 1100 V grade armoured cable as per specification including excavation of earth, 300 mm thick and all around the cable, brick protection refilling, watering and ramming or providing to earth etc. complete. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.1 | 303000000 | 3 x 4 sq.mm (Red, Black & Green) | [8 empty] | RM | 350 | 141.37 | 0 | 141.37 | 10.607 | 0 | 151.977 | 75.96 | 9.3887 | 0 | 85.3487 | 53191.9469 | 29872.0296 | 83064 | 10 | 350 | 4947.95 | 0 | 4947.95 | 371.2447 | 0 | 5319.1947 | 2658.6 | 328.603 | 0 | 2987.203 | 8306.3976
2.2 | 303000000 | 3 x 4 sq.mm (Yellow, Black & Green) | [8 empty] | RM | 350 | 141.37 | 0 | 141.37 | 10.607 | 0 | 151.977 | 75.96 | 9.3887 | 0 | 85.3487 | 53191.9469 | 29872.0296 | 83064 | 10 | 350 | 4947.95 | 0 | 4947.95 | 371.2447 | 0 | 5319.1947 | 2658.6 | 328.603 | 0 | 2987.203 | 8306.3976
2.3 | 303000000 | 3 x 4 sq.mm (Blue, Black & Green) | [8 empty] | RM | 350 | 141.37 | 0 | 141.37 | 10.607 | 0 | 151.977 | 75.96 | 9.3887 | 0 | 85.3487 | 53191.9469 | 29872.0296 | 83064 | 10 | 350 | 4947.95 | 0 | 4947.95 | 371.2447 | 0 | 5319.1947 | 2658.6 | 328.603 | 0 | 2987.203 | 8306.3976
3 | 303000000 | Making end termination of following size PVC insulated sheathed copper conductor 1100 V grade armoured cable including cost of crimping lugs, sockets, double compression glands with earthing facility etc. complete. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.1 | 303000000 | 3C x 4 Sq. mm. | [8 empty] | No. | 10 | 281.685 | 0 | 281.685 | 21.1348 | 0 | 302.8198 | 94.95 | 11.7358 | 0 | 106.6858 | 3028.1983 | 1066.8582 | 4095 | 10 | 10 | 281.685 | 0 | 281.685 | 21.1348 | 0 | 302.8198 | 94.95 | 11.7358 | 0 | 106.6858 | 409.5056
4 | 303000000 | Providing and fixing of following PVC insulated copper conductor 1100 volts grade stranded flexible wire in GI conduit including providing and fixing of conduit concealed or surface mounted as indicated PVC insulated green colour copper stranded flexible wire for earthing and making connection complete. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4.1 | 303000000 | 3 x 2.5 sq.mm wire in 25 mm dia 16 gauge conduit. | [8 empty] | RM | 175 | 202.56 | 0 | 202.56 | 15.1981 | 0 | 217.7581 | 37.98 | 4.6943 | 0 | 42.6743 | 38107.6634 | 7468.0074 | 45576 | 10 | 175 | 3544.8 | 0 | 3544.8 | 265.9663 | 0 | 3810.7663 | 664.65 | 82.1507 | 0 | 746.8007 | 4557.5671
5 | 303000000 | Supply and installation of following hume pipe (NP-2 class) under paved areas, including providing 75 mm thick cement concrete cover all around pipe 1:3:6 (1 cement, 3 coarse sand and 6 crushed stone aggregate). | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.1 | 303000000 | 50 mm dia ID | [8 empty] | RM | 15 | 132.93 | 0 | 132.93 | 9.9737 | 0 | 142.9037 | 158.25 | 19.5597 | 0 | 177.8097 | 2143.5561 | 2667.1455 | 4811 | 10 | 15 | 199.395 | 0 | 199.395 | 14.9606 | 0 | 214.3556 | 237.375 | 29.3395 | 0 | 266.7145 | 481.0702
5.2 | 303000000 | 100 mm dia ID | [8 empty] | RM | 25 | 231.045 | 0 | 231.045 | 17.3353 | 0 | 248.3803 | 189.9 | 23.4716 | 0 | 213.3716 | 6209.5077 | 5334.291 | 11544 | 10 | 25 | 577.6125 | 0 | 577.6125 | 43.3383 | 0 | 620.9508 | 474.75 | 58.6791 | 0 | 533.4291 | 1154.3799
6 | 303000000 | Providing, installation, testing and commissining of 200 x 150 x 125 mm polycarbonate weather proof (IP-55) junction box recessed in wall or surface mounted as required for housing of 1 no. 10 amps SPN MCBs suitable size of terminal blocks complete. Suitable length of GI pipe upto junction box shall also be provided for laying of cables. | [8 empty] | Nos. | 5 | 1055 | 0 | 1055 | 79.1566 | 0 | 1134.1566 | 126.6 | 15.6478 | 0 | 142.2478 | 5670.7832 | 711.2388 | 6382 | 10 | 5 | 527.5 | 0 | 527.5 | 39.5783 | 0 | 567.0783 | 63.3 | 7.8239 | 0 | 71.1239 | 638.2022
7 | 303000000 | Supply, installation, testing and commissioning of following polycarbonate weather proof (IP-55) junction box suitable for pole mounting / underground complete as rerequired. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7.1 | 303000000 | One way | [8 empty] | Nos. | 5 | 781.755 | 0 | 781.755 | 58.6551 | 0 | 840.4101 | 126.6 | 15.6478 | 0 | 142.2478 | 4202.0504 | 711.2388 | 4913 | 10 | 5 | 390.8775 | 0 | 390.8775 | 29.3275 | 0 | 420.205 | 63.3 | 7.8239 | 0 | 71.1239 | 491.3289
7.2 | 303000000 | Two way | [8 empty] | Nos. | 5 | 781.755 | 0 | 781.755 | 58.6551 | 0 | 840.4101 | 126.6 | 15.6478 | 0 | 142.2478 | 4202.0504 | 711.2388 | 4913 | 10 | 5 | 390.8775 | 0 | 390.8775 | 29.3275 | 0 | 420.205 | 63.3 | 7.8239 | 0 | 71.1239 | 491.3289
7.3 | 303000000 | Three Way | [8 empty] | Nos. | 61 | 911.52 | 0 | 911.52 | 68.3913 | 0 | 979.9113 | 126.6 | 15.6478 | 0 | 142.2478 | 59774.5921 | 8677.1134 | 68452 | 10 | 61 | 5560.272 | 0 | 5560.272 | 417.1872 | 0 | 5977.4592 | 772.26 | 95.4513 | 0 | 867.7113 | 6845.1705
8 | 303000000 | Installation, testing & commissioning of 4.0 M high poles GI decorative poles (3.0 M above & 1 M below ground). | [8 empty] | Nos. | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 2582.64 | 319.2143 | 0 | 2901.8543 | 0 | 14509.2715 | 14509 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 1291.32 | 159.6072 | 0 | 1450.9272 | 1450.9272
9 | 303000000 | Making end termination of following size PVC insulated sheathed copper conductor 1100 V grade armoured cable including cost of crimping lugs, sockets, PVC glands etc. complete ( for polycarbonate boxes only). | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.1 | 303000000 | 3C x 4 Sq. mm. | [8 empty] | No. | 142 | 281.685 | 0 | 281.685 | 21.1348 | 0 | 302.8198 | 94.95 | 11.7358 | 0 | 106.6858 | 43000.4152 | 15149.3864 | 58150 | 10 | 142 | 3999.927 | 0 | 3999.927 | 300.1145 | 0 | 4300.0415 | 1348.29 | 166.6486 | 0 | 1514.9386 | 5814.9802
M. | 303000000 | CONDUITING AND CABLING FOR TELEPHONE SYSTEM | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 303000000 | Supply, installation, testing and commissioning of Krone make Protector panel with swivel input stub and splice chamber as required, for the incoming P & T lines. The panel shall have provision for both top and bottom cable feeding. The conductors in the swivel stub and splice chamber shall have 24 AWG conductors and satisfy the fuse link requirement. 5 Nos. test cards shall also be provided. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.1 | 303000000 | 150 pair protector panel | [8 empty] | Nos. | 1 | 16959.125 | 0 | 16959.125 | 1272.4431 | 0 | 18231.5681 | 3798 | 469.4328 | 0 | 4267.4328 | 18231.5681 | 4267.4328 | 22499 | 10 | 1 | 1695.9125 | 0 | 1695.9125 | 127.2443 | 0 | 1823.1568 | 379.8 | 46.9433 | 0 | 426.7433 | 2249.9001
2 | 303000000 | Supply, installation, testing and commissioning of Category 5 Riser cable consisting of multiple core or solid copper conductors of 24 AWG size insulated with expanded polyethylene covered by a PVC skin and inner shielding for grounding. The core shall be covered by a layer of plastic tape and overlaid with a corrugated PVC plastic. The cable shall be as per the specifications laid down in the tender | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.1 | 303000000 | 25 pair unarmoured riser cable | [8 empty] | RM | 3000 | 162.47 | 0 | 162.47 | 12.1901 | 0 | 174.6601 | 14.77 | 1.8256 | 0 | 16.5956 | 523980.3723 | 49786.716 | 573767 | 10 | 3000 | 48741 | 0 | 48741 | 3657.0372 | 0 | 52398.0372 | 4431 | 547.6716 | 0 | 4978.6716 | 57376.7088
3 | 303000000 | Supply, installation, testing and commissioning of following Category 6, IDC patch panel prepackaged with wiring block with legs with legs insert labels, label holders, jumper troughs, metal back panel, duct assembly, screws, washers and an instruction sheet for termination of incoming pairs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.1 | 303000000 | 24 port jack panel | [8 empty] | Nos. | 60 | 6251.93 | 0 | 6251.93 | 469.0823 | 0 | 6721.0123 | 886.2 | 109.5343 | 0 | 995.7343 | 403260.7385 | 59744.0592 | 463005 | 10 | 60 | 37511.58 | 0 | 37511.58 | 2814.4938 | 0 | 40326.0738 | 5317.2 | 657.2059 | 0 | 5974.4059 | 46300.4798
4 | 303000000 | Supply, installation, testing and commissioning of 4 pair Category 6 UTP cable consisting of 23 AWG solid copper conductors and as per the specification. The cable should have flexible jacket and ripcord for easy stripability. | [8 empty] | RM | 26500 | 23.21 | 0 | 23.21 | 1.7414 | 0 | 24.9514 | 5.275 | 0.65199 | 0 | 5.927 | 661213.327 | 157065.235 | 818279 | 10 | 26500 | 61506.5 | 0 | 61506.5 | 4614.8327 | 0 | 66121.3327 | 13978.75 | 1727.7735 | 0 | 15706.5235 | 81827.8562
5 | 303000000 | Providing and fixing in position the following 2mm thick embeded , concealed and or surface mounted, heavy duty FRLS PVC conduit as called for including all acessories i.e. bends, junction boxes, outlet boxes with cover plates of approved make and design. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.1 | 303000000 | 25 mm dia conduit | [8 empty] | RM | 10000 | 28.485 | 0 | 28.485 | 2.1372 | 0 | 30.6222 | 25.32 | 3.1296 | 0 | 28.4496 | 306222.2955 | 284495.52 | 590718 | 10 | 10000 | 28485 | 0 | 28485 | 2137.2296 | 0 | 30622.2296 | 25320 | 3129.552 | 0 | 28449.552 | 59071.7815
6 | 303000000 | Supply, installation, testing and commissioning of Category 6 IDC patch panle prepackaged with wiring block with legs, insert labels, label holders, jumper troughs, metal back panel duct assembly, screws washers and an instruction sheet for termination of incoming pairs. Rate shall include suitable size of lockable 1.6mm thick CRCA sheet steel enclosure duly powder coated. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6.1 | 303000000 | 300 pair wiring block | [8 empty] | Nos. | 4 | 13309.88 | 0 | 13309.88 | 998.6403 | 0 | 14308.5203 | 3162 | 390.8232 | 0 | 3552.8232 | 57234.0812 | 14211.2928 | 71445 | 10 | 4 | 5323.952 | 0 | 5323.952 | 399.4561 | 0 | 5723.4081 | 1264.8 | 156.3293 | 0 | 1421.1293 | 7144.5374
6.2 | 303000000 | 100 pair wiring block | [8 empty] | Nos. | 2 | 4440.495 | 0 | 4440.495 | 333.1703 | 0 | 4773.6653 | 1266 | 156.4776 | 0 | 1422.4776 | 9547.3307 | 2844.9552 | 12392 | 10 | 2 | 888.099 | 0 | 888.099 | 66.6341 | 0 | 954.7331 | 253.2 | 31.2955 | 0 | 284.4955 | 1239.2286
7 | 303000000 | Supply and installation, testing and commissioning following size KRONE make telephone tag block in lockable 16 gauge sheet steel enclosure complete as required. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7.1 | 303000000 | 20 pair Krone type tag block | [8 empty] | No. | 210 | 627.725 | 0 | 627.725 | 47.0982 | 0 | 674.8232 | 253.2 | 31.2955 | 0 | 284.4955 | 141712.8734 | 59744.0592 | 201457 | 10 | 210 | 13182.225 | 0 | 13182.225 | 989.0623 | 0 | 14171.2873 | 5317.2 | 657.2059 | 0 | 5974.4059 | 20145.6933
8 | 303000000 | Supply and installation of flush mounted Category 6 T 568 A or B outlet. The plastic shall be high impact, flame-retardant UL rated thermoplastic. Dust cover / Blank shall be provided to protect unused face plate openings. Termination cap and plastic cover shall be provided to protect jack wiring. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8.1 | 303000000 | Single outlet face plate with RJ-11 jack | [8 empty] | Nos. | 600 | 163.525 | 0 | 163.525 | 12.2693 | 0 | 175.7943 | 50.64 | 6.2591 | 0 | 56.8991 | 105476.5685 | 34139.4624 | 139616 | 10 | 600 | 9811.5 | 0 | 9811.5 | 736.1568 | 0 | 10547.6568 | 3038.4 | 375.5462 | 0 | 3413.9462 | 13961.6031
8.2 | 303000000 | Double outlet face plate with RJ-11 jack | [8 empty] | Nos. | 15 | 231.045 | 0 | 231.045 | 17.3353 | 0 | 248.3803 | 50.64 | 6.2591 | 0 | 56.8991 | 3725.7046 | 853.4866 | 4579 | 10 | 15 | 346.5675 | 0 | 346.5675 | 26.003 | 0 | 372.5705 | 75.96 | 9.3887 | 0 | 85.3487 | 457.9191
9 | 303000000 | Supply and fixing perforated GI cable tray with Cover of the following size including fixing hardware supports etc as required (From communication room to LV shaft and vertical in LV shaft: | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.1 | 303000000 | a. 450mm x 40 x 40 x 2 mm thick | [8 empty] | RM | 100 | 1499.155 | 0 | 1499.155 | 112.4816 | 0 | 1611.6366 | 202.56 | 25.0364 | 0 | 227.5964 | 161163.66 | 22759.6416 | 183923 | 10 | 100 | 14991.55 | 0 | 14991.55 | 1124.816 | 0 | 16116.366 | 2025.6 | 250.3642 | 0 | 2275.9642 | 18392.3302
10 | 303000000 | Providing and laying the following HDPE pipe of 6 Kg/ Cm2 working pressure laid in ground including cost of digging, 150 mm sand all around the pipe, brick protection and back filling including all accessories i.e. bends, reducers, flanges of approved make and design complete as required. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10.1 | 303000000 | a. 50 mm OD with 2.9 mm wall thickness | [8 empty] | RM | 15 | 79.125 | 0 | 79.125 | 5.9367 | 0 | 85.0617 | 63.3 | 7.8239 | 0 | 71.1239 | 1275.9262 | 1066.8582 | 2343 | 10 | 15 | 118.6875 | 0 | 118.6875 | 8.9051 | 0 | 127.5926 | 94.95 | 11.7358 | 0 | 106.6858 | 234.2784
11 | 303000000 | Supply, installation, testing and commisioning of the following incoming telephone cables. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11.1 | 303000000 | a. 150 pair 0.61 mm dia tinned copper armoured cable | [8 empty] | RM | 100 | 1637.36 | 0 | 1637.36 | 122.8511 | 0 | 1760.2111 | 50.64 | 6.2591 | 0 | 56.8991 | 176021.1121 | 5689.9104 | 181711 | 10 | 100 | 16373.6 | 0 | 16373.6 | 1228.5112 | 0 | 17602.1112 | 506.4 | 62.591 | 0 | 568.991 | 18171.1022
12 | 303000000 | Supply and installation of single pair 110 - 110 voice patch cord of 1meters length. | [8 empty] | Nos. | 450 | 169.855 | 0 | 169.855 | 12.7442 | 0 | 182.5992 | 25.32 | 3.1296 | 0 | 28.4496 | 82169.6493 | 12802.2984 | 94972 | 10 | 450 | 7643.475 | 0 | 7643.475 | 573.4899 | 0 | 8216.9649 | 1139.4 | 140.8298 | 0 | 1280.2298 | 9497.1948
13 | 303000000 | Supply and installation of following Enhanced Category 6 patch cord for item no 6 above. It shall have male RJ 45 connector on one end and male RJ45 connector at the other end. It shall be a 8 conductor. 4 pair cord with each conductor of 24 AWG stranded wire. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13.1 | 303000000 | 1 m long | [8 empty] | Nos. | 450 | 240.54 | 0 | 240.54 | 18.0477 | 0 | 258.5877 | 37.98 | 4.6943 | 0 | 42.6743 | 116364.4723 | 19203.4476 | 135568 | 10 | 450 | 10824.3 | 0 | 10824.3 | 812.1472 | 0 | 11636.4472 | 1709.1 | 211.2448 | 0 | 1920.3448 | 13556.792
N. | 303000000 | CONDUITING AND CABLING FOR DATA SYSTEM | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 303000000 | Supply and installation of following 19 inch rack for ethernet switches with A.C. distribution box, wire manager, fan tray, lockable front tinted glass door and two pair angle to support the switch installed in the rack. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.1 | 303000000 | 42 U Rack | [8 empty] | Nos. | 7 | 23407.285 | 0 | 23407.285 | 1756.2486 | 0 | 25163.5336 | 1519.2 | 187.7731 | 0 | 1706.9731 | 176144.7352 | 11948.8118 | 188094 | 10 | 7 | 16385.0995 | 0 | 16385.0995 | 1229.374 | 0 | 17614.4735 | 1063.44 | 131.4412 | 0 | 1194.8812 | 18809.3547
2 | 303000000 | Supply, installation, testing and commissioning of following Category 6, IDC patch panel prepackaged with wiring block with legs with legs insert labels, label holders, jumper troughs, metal back panel, duct assembly, screws, washers and an instruction sheet for termination of incoming pairs. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.1 | 303000000 | 24 port jack panel | [8 empty] | Nos. | 40 | 5861.58 | 0 | 5861.58 | 439.7943 | 0 | 6301.3743 | 886.2 | 109.5343 | 0 | 995.7343 | 252054.9739 | 39829.3728 | 291884 | 10 | 40 | 23446.32 | 0 | 23446.32 | 1759.1774 | 0 | 25205.4974 | 3544.8 | 438.1373 | 0 | 3982.9373 | 29188.4347
3 | 303000000 | Supply and installatlion of wire manager suitable for mounted on 19 inch rack. | [8 empty] | Nos. | 40 | 524.335 | 0 | 524.335 | 39.3409 | 0 | 563.6759 | 253.2 | 31.2955 | 0 | 284.4955 | 22547.0342 | 11379.8208 | 33927 | 10 | 40 | 2097.34 | 0 | 2097.34 | 157.3634 | 0 | 2254.7034 | 1012.8 | 125.1821 | 0 | 1137.9821 | 3392.6855
4 | 303000000 | Supply, installation, testing and commissioning of 4 pair Category 6 LAN cable consisting of 24 AWG solid copper conductors and as per the specification. The cable shall have flexible jacket and ripcord for easy Stripability | [8 empty] | RM | 26000 | 23.21 | 0 | 23.21 | 1.7414 | 0 | 24.9514 | 5.275 | 0.65199 | 0 | 5.927 | 648737.6038 | 154101.74 | 802839 | 10 | 26000 | 60346 | 0 | 60346 | 4527.7604 | 0 | 64873.7604 | 13715 | 1695.174 | 0 | 15410.174 | 80283.9344
5 | 303000000 | Supply and installation of flush mounted Enhanced Category 6 T 568 A or B) outlet. The plastic shall be high impact, flame-retardant, UL rate thermoplastic. Dust cover / blank shall be provided to protect unused faceplate openings. Termination caps and plastic cover shall be provided to protect jack wiring. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5.1 | 303000000 | Single outlet faceplate with RJ-45 jack with information outlet | [8 empty] | Nos. | 600 | 422 | 0 | 422 | 31.6627 | 0 | 453.6627 | 50.64 | 6.2591 | 0 | 56.8991 | 272197.596 | 34139.4624 | 306337 | 10 | 600 | 25320 | 0 | 25320 | 1899.7596 | 0 | 27219.7596 | 3038.4 | 375.5462 | 0 | 3413.9462 | 30633.7058
5.2 | 303000000 | Duplex outlet faceplate with 2 Nos. RJ-45 with information outlets | [8 empty] | Nos. | 15 | 762.765 | 0 | 762.765 | 57.2303 | 0 | 819.9953 | 50.64 | 6.2591 | 0 | 56.8991 | 12299.9289 | 853.4866 | 13153 | 10 | 15 | 1144.1475 | 0 | 1144.1475 | 85.8454 | 0 | 1229.9929 | 75.96 | 9.3887 | 0 | 85.3487 | 1315.3415
6 | 303000000 | Supply and installation of following Enhanced Category 6 mounting cord for connecting the outlets to the data station (computer/printer etc). It shall have male RJ 45 connector on one end and male RJ45 connector or open ended wire or a connector suitable for data outlet at the other end. It shall be a 8 conductor. 4 pair cord with each conductor of 24 AWG stranded wire. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6.1 | 303000000 | 1 m long (For patchong of jack panel & switch) | [8 empty] | Nos. | 600 | 168.8 | 0 | 168.8 | 12.6651 | 0 | 181.4651 | 12.66 | 1.5648 | 0 | 14.2248 | 108879.0384 | 8534.8656 | 117414 | 10 | 600 | 10128 | 0 | 10128 | 759.9038 | 0 | 10887.9038 | 759.6 | 93.8866 | 0 | 853.4866 | 11741.3904
6.2 | 303000000 | 2 m long (For outlet) | [8 empty] | Nos. | 600 | 259.53 | 0 | 259.53 | 19.4725 | 0 | 279.0025 | 12.66 | 1.5648 | 0 | 14.2248 | 167401.5215 | 8534.8656 | 175936 | 10 | 600 | 15571.8 | 0 | 15571.8 | 1168.3522 | 0 | 16740.1522 | 759.6 | 93.8866 | 0 | 853.4866 | 17593.6387
7 | 303000000 | Supply and fixing in position the following 2mm thick embeded heavy duty FRLS PVC conduit and or surface mounted 16 gauge GI conduits concealed or exposed as called for including cost of junction boxes, bends, elbows, sockets, tees etc. laying in slab cutting chasis and making good or surface mounted including all fixing hardware. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7.1 | 303000000 | 25 mm dia | [8 empty] | RM | 8500 | 39.035 | 0 | 39.035 | 2.9288 | 0 | 41.9638 | 25.32 | 3.1296 | 0 | 28.4496 | 356692.2664 | 241821.192 | 598513 | 10 | 8500 | 33179.75 | 0 | 33179.75 | 2489.4766 | 0 | 35669.2266 | 21522 | 2660.1192 | 0 | 24182.1192 | 59851.3458
8 | 303000000 | Supply and fixing perforated GI cable tray with Cover of the following size including fixing hardware supports etc as required (From communication room to LV shaft and vertical in LV shaft): | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8.1 | 303000000 | a. 450mm x 40 x 40 x 2 mm thick | [8 empty] | RM | 100 | 1499.155 | 0 | 1499.155 | 112.4816 | 0 | 1611.6366 | 202.56 | 25.0364 | 0 | 227.5964 | 161163.66 | 22759.6416 | 183923 | 10 | 100 | 14991.55 | 0 | 14991.55 | 1124.816 | 0 | 16116.366 | 2025.6 | 250.3642 | 0 | 2275.9642 | 18392.3302
9 | 303000000 | Providing and laying the following HDPE pipe of 6 Kg/ Cm2 working pressure laid in ground including cost of digging, 150 mm sand all around the pipe, brick protection and back filling including all accessories i.e. bends, reducers, flanges of approved make and design complete as required. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.1 | 303000000 | a. 50 mm OD with 2.9 mm wall thickness | [8 empty] | RM | 15 | 325.995 | 0 | 325.995 | 24.4594 | 0 | 350.4544 | 63.3 | 7.8239 | 0 | 71.1239 | 5256.8161 | 1066.8582 | 6324 | 10 | 15 | 488.9925 | 0 | 488.9925 | 36.6891 | 0 | 525.6816 | 94.95 | 11.7358 | 0 | 106.6858 | 632.3674
10 | 303000000 | Supply, installation and testing of 50/125 microm OM3 - 6 core multimode Fiber optics as per specification. | [8 empty] | RM | 50 | 182.515 | 0 | 182.515 | 13.6941 | 0 | 196.2091 | 23.21 | 2.8688 | 0 | 26.0788 | 9810.455 | 1303.9378 | 11114 | 10 | 50 | 912.575 | 0 | 912.575 | 68.4705 | 0 | 981.0455 | 116.05 | 14.3438 | 0 | 130.3938 | 1111.4393
11 | 303000000 | Supply, installation and testing of 50/125 microm OM3 - 12 core multimode Fiber optics as per specification. | [8 empty] | RM | 1625 | 207.835 | 0 | 207.835 | 15.5939 | 0 | 223.4289 | 25.32 | 3.1296 | 0 | 28.4496 | 363071.8976 | 46230.522 | 409302 | 10 | 1625 | 33773.1875 | 0 | 33773.1875 | 2534.0023 | 0 | 36307.1898 | 4114.5 | 508.5522 | 0 | 4623.0522 | 40930.242
12 | 303000000 | Supply , installation and testing of 12 port rack mount LIU | [8 empty] | Nos | 1 | 10397.025 | 0 | 10397.025 | 780.0888 | 0 | 11177.1138 | 379.8 | 46.9433 | 0 | 426.7433 | 11177.1138 | 426.7433 | 11604 | 10 | 1 | 1039.7025 | 0 | 1039.7025 | 78.0089 | 0 | 1117.7114 | 37.98 | 4.6943 | 0 | 42.6743 | 1160.3857
13 | 303000000 | Supply , installation and testing of 24 port rack mount LIU | [8 empty] | Nos | 5 | 18196.64 | 0 | 18196.64 | 1365.2939 | 0 | 19561.9339 | 759.6 | 93.8866 | 0 | 853.4866 | 97809.6695 | 4267.4328 | 102077 | 10 | 5 | 9098.32 | 0 | 9098.32 | 682.6469 | 0 | 9780.9669 | 379.8 | 46.9433 | 0 | 426.7433 | 10207.7102
14 | 303000000 | Termination of both sides of 6 core fiber optics cables in the LIU which includes adapter panel, adapter , SC type pigtail | [8 empty] | Nos | 4 | 1570.895 | 0 | 1570.895 | 117.8643 | 0 | 1688.7593 | 633 | 78.2388 | 0 | 711.2388 | 6755.037 | 2844.9552 | 9600 | 10 | 4 | 628.358 | 0 | 628.358 | 47.1457 | 0 | 675.5037 | 253.2 | 31.2955 | 0 | 284.4955 | 959.9992
15 | 303000000 | Termination of both sides of 12 core fiber optics cables in the LIU which includes adapter panel, adapter , SC type pigtail | [8 empty] | Nos | 20 | 3926.71 | 0 | 3926.71 | 294.6211 | 0 | 4221.3311 | 1519.2 | 187.7731 | 0 | 1706.9731 | 84426.621 | 34139.4624 | 118566 | 10 | 20 | 7853.42 | 0 | 7853.42 | 589.2421 | 0 | 8442.6621 | 3038.4 | 375.5462 | 0 | 3413.9462 | 11856.6083
O. | 303000000 | CONDUTING & CABLING FOR TV SYSTEM | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 303000000 | Providing and fixing in position the following 2mm thick conduits concealed, embeded or exposed as called for including all accessories i.e. bends, junction boxes, outlet boxes with cover plates of approved make and design | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1.1 | 303000000 | 25 mm dia conduit | [8 empty] | RM | 3350 | 39.035 | 0 | 39.035 | 2.9288 | 0 | 41.9638 | 25.32 | 3.1296 | 0 | 28.4496 | 140578.7168 | 95305.9992 | 235885 | 10 | 3350 | 13076.725 | 0 | 13076.725 | 981.1467 | 0 | 14057.8717 | 8482.2 | 1048.3999 | 0 | 9530.5999 | 23588.4716
1.2 | 303000000 | 32 mm dia conduit | [8 empty] | RM | 1350 | 63.3 | 0 | 63.3 | 4.7494 | 0 | 68.0494 | 31.65 | 3.9119 | 0 | 35.5619 | 91866.6886 | 48008.619 | 139875 | 10 | 1350 | 8545.5 | 0 | 8545.5 | 641.1689 | 0 | 9186.6689 | 4272.75 | 528.1119 | 0 | 4800.8619 | 13987.5308
1.2.1 | 303000000 | (For RG-11 Co-axial cable) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 303000000 | Supply and fixing following signal outlets with grid plate in 2 mm thick GI box complete including cutting, chases, fixing of GI boxes and making good. (Cover plate shall match the colour, size and make of wiring accessories to be used in the project.) | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.1 | 303000000 | TV Signals outlet | [8 empty] | Nos. | 295 | 162.47 | 0 | 162.47 | 12.1901 | 0 | 174.6601 | 50.64 | 6.2591 | 0 | 56.8991 | 51524.7366 | 16785.2357 | 68310 | 10 | 295 | 4792.865 | 0 | 4792.865 | 359.6087 | 0 | 5152.4737 | 1493.88 | 184.6436 | 0 | 1678.5236 | 6830.9972
3 | 303000000 | Supply, erection, testing and commissioning of following tap off with IP 55 boxes for CATV system. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.1 | 303000000 | One way (T-1) | [8 empty] | Nos. | 75 | 390.35 | 0 | 390.35 | 29.288 | 0 | 419.638 | 63.3 | 7.8239 | 0 | 71.1239 | 31472.847 | 5334.291 | 36807 | 10 | 75 | 2927.625 | 0 | 2927.625 | 219.6597 | 0 | 3147.2847 | 474.75 | 58.6791 | 0 | 533.4291 | 3680.7138
3.2 | 303000000 | Two way (T-2) | [8 empty] | Nos. | 102 | 455.76 | 0 | 455.76 | 34.1957 | 0 | 489.9557 | 75.96 | 9.3887 | 0 | 85.3487 | 49975.4786 | 8705.5629 | 58681 | 10 | 102 | 4648.752 | 0 | 4648.752 | 348.7959 | 0 | 4997.5479 | 774.792 | 95.7643 | 0 | 870.5563 | 5868.1042
3.3 | 303000000 | Four way (T-4) | [8 empty] | Nos. | 4 | 521.17 | 0 | 521.17 | 39.1034 | 0 | 560.2734 | 75.96 | 9.3887 | 0 | 85.3487 | 2241.0935 | 341.3946 | 2582 | 10 | 4 | 208.468 | 0 | 208.468 | 15.6414 | 0 | 224.1094 | 30.384 | 3.7555 | 0 | 34.1395 | 258.2488
4 | 303000000 | Supply, erection, testing and commissioning of spliter with IP 55 boxes. | [8 empty] | Nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4.1 | 303000000 | Two way (S 2) | [8 empty] | Nos. | 5 | 522.225 | 0 | 522.225 | 39.1825 | 0 | 561.4075 | 101.28 | 12.5182 | 0 | 113.7982 | 2807.0377 | 568.991 | 3376 | 10 | 5 | 261.1125 | 0 | 261.1125 | 19.5913 | 0 | 280.7038 | 50.64 | 6.2591 | 0 | 56.8991 | 337.6029
4.2 | 303000000 | Four way (S 4) | [8 empty] | Nos. | 5 | 650.935 | 0 | 650.935 | 48.8397 | 0 | 699.7747 | 101.28 | 12.5182 | 0 | 113.7982 | 3498.8733 | 568.991 | 4068 | 10 | 5 | 325.4675 | 0 | 325.4675 | 24.4198 | 0 | 349.8873 | 50.64 | 6.2591 | 0 | 56.8991 | 406.7864
5 | 303000000 | Supply, laying, connecting and commissioning of RG-11 co-axial cable of MATV as per specification in existing PVC conduit | [8 empty] | RM | 1350 | 36.925 | 0 | 36.925 | 2.7705 | 0 | 39.6955 | 5.275 | 0.65199 | 0 | 5.927 | 53588.9017 | 8001.4365 | 61590 | 10 | 1350 | 4984.875 | 0 | 4984.875 | 374.0152 | 0 | 5358.8902 | 712.125 | 88.0186 | 0 | 800.1436 | 6159.0338
6 | 303000000 | Supply, laying, connecting and commissioning of RG-6 co-axial cable of MATV as per specification in existing PVC conduit. | [8 empty] | RM | 3500 | 18.99 | 0 | 18.99 | 1.4248 | 0 | 20.4148 | 5.275 | 0.65199 | 0 | 5.927 | 71451.8689 | 20744.465 | 92196 | 10 | 3500 | 6646.5 | 0 | 6646.5 | 498.6869 | 0 | 7145.1869 | 1846.25 | 228.1965 | 0 | 2074.4465 | 9219.6334
7 | 303000000 | Supply and fixing of Line extender amplifier 110 DB as per specification housed in suitable size of 16 gauge CRCA sheet enclosed. | [8 empty] | Nos | 3 | 3901.39 | 0 | 3901.39 | 292.7213 | 0 | 4194.1113 | 253.2 | 31.2955 | 0 | 284.4955 | 12582.3339 | 853.4866 | 13436 | 10 | 3 | 1170.417 | 0 | 1170.417 | 87.8164 | 0 | 1258.2334 | 75.96 | 9.3887 | 0 | 85.3487 | 1343.582
8 | 303000000 | Supply, laying and connecting of single pair PVC insulated twisted copper conductor cable of 32/0.2 mm dia in conealed/surface mounted 2mm thick heavy duty FRLS pvc conduit including all fixing accessories as required. | [8 empty] | RM | 250 | 50.64 | 0 | 50.64 | 3.7995 | 0 | 54.4395 | 31.65 | 3.9119 | 0 | 35.5619 | 13609.8798 | 8890.485 | 22500 | 10 | 250 | 1266 | 0 | 1266 | 94.988 | 0 | 1360.988 | 791.25 | 97.7985 | 0 | 889.0485 | 2250.0365

## COP Facesheet
CHARTERED HOTELS PVT. LTD.
CERTIFICATE OF PAYMENT
COP No.:- HRL/COP/servotech/ |  |  |  |  | Date.:- 27/09/2014
Project Code:- |  | 006 |  |  | Not For Payment
Project:- |  | Proposed Five star hotel at lucknow
Work: | Supply, Installation, testing & commisioning of Electrical works |  |  | M/s Servotech electricals
Budget Code:- |  |  |  | 252-A Vijay Tower,Shahpur jat,Opp,Panchseel Commercial Complex,New Delhi-110049
W.O. / P.O. No. & Date:- |  |  | CHPL/002/WO/14-15/ Dated : 19.05.2010 | PAN No.:- AACCS9091E
Original W.O. Value:- |  |  | 63424804 | VAT No.:- CST NO- Service Tax No:- AACCS9091E
WO Amendment No.:- |  |  |  | Invoice No.
Amended WO/PO Value:-
Sr. No. | Description of Work |  |  | Previous Certified Amount INR | Current Certified Amount INR | Cumulative Certified Amount INR
| Certificate Type:- |  |  |  | I
| Certificate No.:- |  |  |  | COP-R001
A | Work Done Amount
1 | Net Supply Amount |  |  |  | 5118098.6605 | 5118098.6605
2 | Net Installation Amount |  |  |  | 747928.233 | 747928.233
3 | VAT |  |  |  | 384010.9425 | 384010.9425
4 | Service Tax. |  |  |  | 92443.9296 | 92443.9296
5 | Supply and Installation Others |  |  |  | 0 | 0
A | Gross Amount for Work Done As per this Bill |  |  | 0 | 6342481.7656 | 6342481.7656
B | Recoveries:- |  |  |  | 0
1 | Recovery of Advance (@13.333%) |  |  |  | 0
2 | Recovery of water Charges for Water Consumed |  |  |  | 0
3 | Recovery of Power ( For Electricity Consumed) |  |  |  | 0
4 | Recovery of Monthly Advance ( if any) |  |  |  | 0
5 | Recovery of unsecured Advance( Including Expired Bank Guarantee |  |  |  | 0
6 | Recovery of Insurance Premium |  |  |  | 0
7 | Debit for Non removing of debris |  |  |  | 0
8 | Retention Amount (as per Contract Conditions 5%) |  |  |  | 0
9 | Non Conformity of Concrete |  |  |  | 0
10 | Miscellaneous |  |  |  | 0
B | Total Gross Recoveries:- |  |  | 0 | 0 | 0
C | Other Payments |  |  |  | 0
1 | Mobilisation Advance |  |  |  | 0
2 | Ad-Hoc Certification |  |  |  | 0
3 | Secured Advance |  |  |  | 0
4 | Travel Reimbursement |  |  |  | 0
| Net Amount of Other Payments |  |  |  | 0
| Service Tax ON Other Payments, if any. |  |  |  | 0
C | Gross Amount for Other Payments |  |  | 0 | 0 | 0
| Gross Certified as Per This Bill A-B+C |  |  |  | 6342481.7656 | 6342481.7656
Rs. (In Words):
Mode of Payment:-
Remarks:-
Prepared By |  | Checked By |  | Approved By | Approved By
QS and Contracts |  | Asst.GM - Contracts |  | GM -Project | GM -Contracts
CHPL
CHPL
CHPL